## Equipment Tree
BPL131
BR4.SRV.CTRLSYS.PLC.BPL131 | BPL131 PLC
BR4.SRV.CTRLSYS.PLC.BPL131.Drop01 | BPL131 Drop 1 - BTY1502DX01
BR4.SRV.CTRLSYS.PLC.BPL131.Drop02 | BPL131 Drop 2 - BSR131DX01
BR4.SRV.CTRLSYS.PLC.BPL131.Drop03 | BPL131 Drop 3 - BTY1502DX03
BR4.SRV.CTRLSYS.PLC.BPL131.Drop04 | BPL131 Drop 4 - BTK2101DX04
BSR131
BR4.SRV.PWR.BSR131 | BSR131 Switchroom
BR4.SRV.PWR.BSR131.AC01 | BSR131 Switchroom - Air Conditioner 1
BR4.SRV.PWR.BSR131.AC01.CB01 | BSR131 Switchroom - Air Conditioner 1 Main Circuit Breaker
BR4.SRV.PWR.BSR131.AC02 | BSR131 Switchroom - Air Conditioner 2
BR4.SRV.PWR.BSR131.AC02.CB01 | BSR131 Switchroom - Air Conditioner 2 Main Circuit Breaker
BR4.SRV.PWR.BSR131.BC01 | BSR131 Switchroom - Battery Charger 1
BR4.SRV.PWR.BSR131.BC01.CB01 | BSR131 Switchroom - Battery Charger 1 Main Circuit Breaker
BR4.SRV.PWR.BSR131.BC02 | BSR131 Switchroom - Battery Charger 2
BR4.SRV.PWR.BSR131.BC02.BACS | BSR131 Switchroom - Battery Charger 2 Battery Management
BR4.SRV.PWR.BSR131.BC02.CB01 | BSR131 Switchroom - Battery Charger 2 Main Circuit Breaker
BR4.SRV.PWR.BSR131.BC02.Cordex | BSR131 Switchroom - Battery Charger 2 Controller
BR4.SRV.PWR.BSR131.BMC131 | BMC131 Motor Control Centre
BR4.SRV.PWR.BSR131.BMC131.INC01 | BMC131 Motor Control Centre - Incomer 1
BR4.SRV.PWR.BSR131.BMC131.INC01.MasterPact | BMC131 Motor Control Centre - Incomer 1 Masterpact
BR4.SRV.PWR.BSR131.BMC131.INC01.VAMP | BMC131 Motor Control Centre - Incomer 1 VAMP Arc Flash
BR4.SRV.PWR.BSR131.BMC131.INC02 | BMC131 Motor Control Centre - Incomer 2
BR4.SRV.PWR.BSR131.BMC131.INC02.MasterPact | BMC131 Motor Control Centre - Incomer 2 Masterpact
BR4.SRV.PWR.BSR131.BMC131.INC03 | BMC131 Motor Control Centre - Incomer 3
BR4.SRV.PWR.BSR131.BMC131.INC03.MasterPact | BMC131 Motor Control Centre - Incomer 3 Masterpact
BR4.SRV.PWR.BSR131.BMC1311 | BMC1311 HME Refuelling Feeder
BR4.SRV.PWR.BSR131.BMC1311.Sub | BMC1311 HME Refuelling Feeder
BR4.SRV.PWR.BSR131.BMC1311.Sub.CB01 | BMC1311 HME Refuelling Feeder Main Circuit Breaker
BR4.SRV.PWR.BSR131.DB01 | DB01 - Small Power & Lighting Distribution Board
BR4.SRV.PWR.BSR131.DB01.CB01 | DB01 - Small Power & Lighting Distribution Board Main Circuit Breaker
BR4.SRV.PWR.BSR131.DB02 | DB02 - Small Power & Lighting Distribution Board
BR4.SRV.PWR.BSR131.DB02.CB01 | DB02 - Small Power & Lighting Distribution Board Main Circuit Breaker
BR4.SRV.PWR.BSR131.DB03 | DB03 - Small Power & Lighting Distribution Board
BR4.SRV.PWR.BSR131.DB03.CB01 | DB03 - Small Power & Lighting Distribution Board Main Circuit Breaker
BR4.SRV.PWR.BSR131.DB04 | DB04 - Small Power & Lighting Distribution Board
BR4.SRV.PWR.BSR131.DB04.CB01 | DB04 - Small Power & Lighting Distribution Board Main Circuit Breaker
BR4.SRV.PWR.BSR131.NEP01 | NEP01 - BSR131 Network Equipment Panel 1
BR4.SRV.PWR.BSR131.UP01 | UP01 - BSR131 Uninterruptable Power Supply 1
BR4.SRV.PWR.BSR131.UP01.BACS | UP01 - BSR131 UPS Battery Management
BR4.SRV.PWR.BSR131.UP01.DB01 | UP01 - BSR131 UPS Distribution Board 1
BR4.SRV.PWR.BSR131.UP01.UPScale | UP01 - BSR131 UPS
Pumps
BR4.UTILITIES.WATER.BS1.RWD1.BPP1101 | BPP1101 - Raw Water Distribution Pump
BR4.UTILITIES.WATER.BS1.RWD1.BPP1101.FieldIO | BPP1101 - Field I/O
BR4.UTILITIES.WATER.BS1.RWD1.BPP1101.FieldIO.FT01 | BPP1101 - FT01 NPI Raw Water Flowmeter
BR4.UTILITIES.WATER.BS1.RWD1.BPP1101.FieldIO.FT03 | BPP1101 - FT03 NPI/PC3 Supply Flowmeter
BR4.UTILITIES.WATER.BS1.RWD1.BPP1101.FieldIO.PT03 | BPP1101 - PT03 Pump Discharge Pressure
BR4.UTILITIES.WATER.BS1.RWD1.BPP1101.FieldIO.PT10 | BPP1101 - PT10 BS1 Raw Water Distribution Pressure 1
BR4.UTILITIES.WATER.BS1.RWD1.BPP1101.FieldIO.PT11 | BPP1101 - PT11 BS1 Raw Water Distribution Pressure 2
BR4.UTILITIES.WATER.BS1.RWD1.BPP1101.Sub | BPP1101 - Feeder
BR4.UTILITIES.WATER.BS1.RWD1.BPP1101.Sub.CB01 | BPP1101 - Feeder Main Cicuit Breaker
BR4.UTILITIES.WATER.BS1.RWD1.BPP1101.VS01 | BPP1101 - Raw Water Distribution Pump VSD
BR4.UTILITIES.WATER.BS1.RWD1.BPP1102 | BPP1102 - Raw Water Distribution Pump
BR4.UTILITIES.WATER.BS1.RWD1.BPP1102.FieldIO | BPP1102 - Field I/O
BR4.UTILITIES.WATER.BS1.RWD1.BPP1102.FieldIO.PT04 | BPP1102 - PT04 Pump Discharge Pressure
BR4.UTILITIES.WATER.BS1.RWD1.BPP1102.Sub | BPP1102 - Feeder
BR4.UTILITIES.WATER.BS1.RWD1.BPP1102.Sub.CB01 | BPP1102 - Feeder Main Cicuit Breaker
BR4.UTILITIES.WATER.BS1.RWD1.BPP1102.VS01 | BPP1102 - Raw Water Distribution Pump VSD
BR4.UTILITIES.WATER.BS1.RWT.BPP1103 | BPP1103 - Raw Water Transfer Pump
BR4.UTILITIES.WATER.BS1.RWT.BPP1103.FieldIO | BPP1103 - Field I/O
BR4.UTILITIES.WATER.BS1.RWT.BPP1103.FieldIO.FT03 | BPP1103 - FT03 Pump Flowmeter
BR4.UTILITIES.WATER.BS1.RWT.BPP1103.FieldIO.FT06 | RWT - FT03 Transfer Pipeline Flowmeter
BR4.UTILITIES.WATER.BS1.RWT.BPP1103.FieldIO.PT05 | BPP1103 - PT05 Pump Discharge Pressure
BR4.UTILITIES.WATER.BS1.RWT.BPP1103.FieldIO.PT08 | BPP1103 - PT08 Transfer Header Pressure
BR4.UTILITIES.WATER.BS1.RWT.BPP1103.Sub | BPP1103 - Feeder
BR4.UTILITIES.WATER.BS1.RWT.BPP1103.Sub.CB01 | BPP1103 - Feeder Main Cicuit Breaker
BR4.UTILITIES.WATER.BS1.RWT.BPP1103.VS01 | BPP1103 - Raw Water Transfer Pump VSD
BR4.UTILITIES.WATER.BS1.RWT.BPP1104 | BPP1104 - Raw Water Transfer Pump
BR4.UTILITIES.WATER.BS1.RWT.BPP1104.FieldIO | BPP1104 - Field I/O
BR4.UTILITIES.WATER.BS1.RWT.BPP1104.FieldIO.FT04 | BPP1104 - FT04 Pump Flowmeter
BR4.UTILITIES.WATER.BS1.RWT.BPP1104.FieldIO.PT06 | BPP1104 - PT06 Pump Discharge Pressure
BR4.UTILITIES.WATER.BS1.RWT.BPP1104.Sub | BPP1104 - Feeder
BR4.UTILITIES.WATER.BS1.RWT.BPP1104.Sub.CB01 | BPP1104 - Feeder Main Cicuit Breaker
BR4.UTILITIES.WATER.BS1.RWT.BPP1104.VS01 | BPP1104 - Raw Water Transfer Pump VSD
BR4.UTILITIES.WATER.BS1.RWT.BPP1105 | BPP1105 - Raw Water Transfer Pump
BR4.UTILITIES.WATER.BS1.RWT.BPP1105.FieldIO | BPP1105 - Field I/O
BR4.UTILITIES.WATER.BS1.RWT.BPP1105.FieldIO.FT05 | BPP1105 - FT04 Pump Flowmeter
BR4.UTILITIES.WATER.BS1.RWT.BPP1105.FieldIO.PT07 | BPP1105 - PT06 Pump Discharge Pressure
BR4.UTILITIES.WATER.BS1.RWT.BPP1105.Sub | BPP1105 - Feeder
BR4.UTILITIES.WATER.BS1.RWT.BPP1105.Sub.CB01 | BPP1105 - Feeder Main Cicuit Breaker
BR4.UTILITIES.WATER.BS1.RWT.BPP1105.VS01 | BPP1105 - Raw Water Transfer Pump VSD
BR4.UTILITIES.WATER.BS1.STD1.BPP1106 | BPP1106 - Standpipe Pump
BR4.UTILITIES.WATER.BS1.STD1.BPP1106.FieldIO | BPP1106 - Field I/O
BR4.UTILITIES.WATER.BS1.STD1.BPP1106.FieldIO.PT01 | BPP1106 - PT01 Pump Discharge Pressure
BR4.UTILITIES.WATER.BS1.STD1.BPP1106.Sub | BPP1106 - Feeder
BR4.UTILITIES.WATER.BS1.STD1.BPP1106.Sub.CB01 | BPP1106 - Feeder Main Cicuit Breaker
BR4.UTILITIES.WATER.BS1.STD1.BPP1106.VS01 | BPP1106 - Raw Water Transfer Pump VSD
BR4.UTILITIES.WATER.BS1.STD1.BPP1107 | BPP1107 - Standpipe Pump
BR4.UTILITIES.WATER.BS1.STD1.BPP1107.FieldIO | BPP1107 - Field I/O
BR4.UTILITIES.WATER.BS1.STD1.BPP1107.FieldIO.PT02 | BPP1107 - PT01 Pump Discharge Pressure
BR4.UTILITIES.WATER.BS1.STD1.BPP1107.Sub | BPP1107 - Feeder
BR4.UTILITIES.WATER.BS1.STD1.BPP1107.Sub.CB01 | BPP1107 - Feeder Main Cicuit Breaker
BR4.UTILITIES.WATER.BS1.STD1.BPP1107.VS01 | BPP1107 - Raw Water Transfer Pump VSD
Standpipes
BR4.UTILITIES.WATER.BS1.STD1.BSTD1106 | BSTD1106 - LME Standpipe
BR4.UTILITIES.WATER.BS1.STD1.BSTD1106.FieldIO | BSTD1106 - Field I/O
BR4.UTILITIES.WATER.BS1.STD1.BSTD1106.FieldIO.FT03 | BSTD1106 - FT03 LME Standpipe Flowmeter
BR4.UTILITIES.WATER.BS1.STD1.BSTD1106.FV03 | BSTD1106 - FV03 LME Standpipe Flow Valve
BR4.UTILITIES.WATER.BS1.STD1.BSTD1106.FV03.FieldIO | BSTD1106 - FV03 LME Standpipe Flow Valve Field I/O
BR4.UTILITIES.WATER.BS1.STD1.BSTD1106.FV03.FieldIO.CB01 | BSTD1106 - FV03 Cicuit Breaker
BR4.UTILITIES.WATER.BS1.STD1.BSTD1106.FV03.FieldIO.ZC01 | BSTD1106 - FV03 Position Controller
BR4.UTILITIES.WATER.BS1.STD1.BSTD1106.FV03.FieldIO.ZT01 | BSTD1106 - FV03 Position
BR4.UTILITIES.WATER.BS1.STD1.BSTD1107 | BSTD1107 - HME Standpipe
BR4.UTILITIES.WATER.BS1.STD1.BSTD1107.FieldIO | BSTD1107 - Field I/O
BR4.UTILITIES.WATER.BS1.STD1.BSTD1107.FieldIO.FT02 | BSTD1107 - FT02 HME Standpipe Flowmeter
BR4.UTILITIES.WATER.BS1.STD1.BSTD1107.FV02 | BSTD1107 - FV02 HME Standpipe Flow Valve
BR4.UTILITIES.WATER.BS1.STD1.BSTD1107.FV02.FieldIO | BSTD1107 - FV02 HME Standpipe Flow Valve Field I/O
BR4.UTILITIES.WATER.BS1.STD1.BSTD1107.FV02.FieldIO.CB01 | BSTD1107 - FV02 Cicuit Breaker
BR4.UTILITIES.WATER.BS1.STD1.BSTD1107.FV02.FieldIO.ZC01 | BSTD1107 - FV02 Position Controller
BR4.UTILITIES.WATER.BS1.STD1.BSTD1107.FV02.FieldIO.ZT01 | BSTD1107 - FV02 Position
West Turkeys Nest
BR4.UTILITIES.WATER.BS1.BTY1502 | BTY1502 - West Turkeys Nest
BR4.UTILITIES.WATER.BS1.BTY1502.FieldIO | BTY1502 - West Turkeys Nest Field I/O
BR4.UTILITIES.WATER.BS1.BTY1502.FieldIO.FT01 | BTY1502 - FT01 WTN East Pit Flowmeter
BR4.UTILITIES.WATER.BS1.BTY1502.FieldIO.FT02 | BTY1502 - FT02 Recirculation Flowmeter
BR4.UTILITIES.WATER.BS1.BTY1502.FieldIO.FT03 | BTY1502 - FT03 WTN West Pit Flowmeter
BR4.UTILITIES.WATER.BS1.BTY1502.FieldIO.LT01 | BTY1502 - LT01 West Turkeys Nest Level 1
BR4.UTILITIES.WATER.BS1.BTY1502.FieldIO.LT02 | BTY1502 - LT02 West Turkeys Nest Level 2
BR4.UTILITIES.WATER.BS1.BTY1502.FieldIO.PT01 | BTY1502 - PT01 WTN East Pit Line Pressure
BR4.UTILITIES.WATER.BS1.BTY1502.FieldIO.PT03 | BTY1502 - PT03 WTN West Pit Line Pressure
BR4.UTILITIES.WATER.BS1.BTY1502.FV01 | BTY1502 - FV01 West Turkeys Nest Recirculation Valve
BR4.UTILITIES.WATER.BS1.BTY1502.FV01.FieldIO | BTY1502 - FV01 West Turkeys Nest Recirculation Valve Field IO
BR4.UTILITIES.WATER.BS1.BTY1502.FV01.FieldIO.CB01 | BTY1502 - FV01 West Turkeys Nest Recirculation Valve Circuit Breaker
BR4.UTILITIES.WATER.BS1.BTY1502.FV01.FieldIO.ZC01 | BTY1502 - FV01 West Turkeys Nest Recirculation Valve Position Controller
BR4.UTILITIES.WATER.BS1.BTY1502.FV01.FieldIO.ZT01 | BTY1502 - FV01 West Turkeys Nest Recirculation Valve Position
FireWater Tanks
BR4.UTILITIES.WATER.BS1.P3FIREWATER.BTK2101.FieldIO.LT01 | BTK2101 - LT01 BS1 NPI Firewater Tank 1 Level 1
BR4.UTILITIES.WATER.BS1.P3FIREWATER.BTK2101.FieldIO | BTK2101 - BS1 NPI Firewater Tank 1 Field I/O
BR4.UTILITIES.WATER.BS1.P3FIREWATER.BTK2101 | BTK2101 - BS1 NPI Firewater Tank 1
BR4.UTILITIES.WATER.BS1.P3FIREWATER.BTK2102.FieldIO.LT01 | BTK2102 - LT01 BS1 NPI Firewater Tank 2 Level 1
BR4.UTILITIES.WATER.BS1.P3FIREWATER.BTK2102.FieldIO | BTK2102 - BS1 NPI Firewater Tank 2 Field I/O
BR4.UTILITIES.WATER.BS1.P3FIREWATER.BTK2102 | BTK2102 - BS1 NPI Firewater Tank 2
BR4.UTILITIES.WATER.BS1.RWD1 | West Turkeys Nest Raw Water Distribution Pumps
BR4.UTILITIES.WATER.BS1.RWT | West Turkeys Nest Raw Water Transfer Pumps
BR4.UTILITIES.WATER.BS1.STD1 | West Turkeys Nest Standpipe Pumps

## Variables
BR4.SRV.CTRLSYS.PLC.BPL131.Drop02 |  | BTY1502DX02CB01_I | BR4_Cluster1 | BPL131 | DIGITAL | %M1000 | West Turkeys Nest DIO Box 2 240VAC BTY1502AX01 Control Supply Circuit Breaker (Q106) Closed |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.BMC1311.Sub.CB01 |  | BMC1311CB01_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M10000 | HME Refuelling MCC Main Circuit Breaker (Q103) Open Healthy |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.BMC1311.Sub.CB01 |  | BMC1311TRP01_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M10001 | HME Refuelling MCC Main Circuit Breaker Trip Healthy |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.BMC1311 |  | BMC1311VDC01_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M10002 | HME Refuelling MCC 24VDC Control Supply (Q155) Failure Healthy |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC01 |  | BMC131INC01CB02_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M10003 | BMC131 Process Bus Incomer Arc Flash Supply (Q204) Open Healthy |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC01 |  | BMC131INC01CB03_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M10004 | BMC131 Process Bus Incomer Incomer Circuit Breaker Spring Charge Supply (Q212) Open Healthy |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC01 |  | BMC131INC01CB04_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M10005 | BMC131 Process Bus Incomer Incomer Circuit Breaker Trip Supply (Q220) Open Healthy |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC01 |  | BMC131INC01CB05_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M10006 | BMC131 Process Bus Incomer Incomer Circuit Breaker 24VDC Cubicle Bus Supply (Q256) Open Healthy |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC01 |  | BMC131INC01CB06_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M10007 | BMC131 Process Bus Incomer 110VDC/24VDC Power Supply (Q215) Open Healthy |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC01 |  | BMC131INC01PR1_CB_PwrOK | BR4_Cluster1 | BPL131 | DIGITAL | %M10008 | BMC131 Process Bus Incomer Protection Relay Main Power to Drive Healthy |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC01 |  | BMC131INC01PR1_CBCls | BR4_Cluster1 | BPL131 | DIGITAL | %M10009 | BMC131 Process Bus Incomer Protection Relay Circuit Breaker Closed |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.BTY1502.FieldIO |  | BTY1502DX02VDC01_I | BR4_Cluster1 | BPL131 | DIGITAL | %M1001 | West Turkeys Nest DIO Box 2 24VDC Output Control Supply (Q143) Healthy |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC01 |  | BMC131INC01PR1_CBCls_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M10010 | BMC131 Process Bus Incomer Protection Relay Circuit Breaker Healthy |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC01 |  | BMC131INC01PR1_CBClsDatOK | BR4_Cluster1 | BPL131 | DIGITAL | %M10011 | BMC131 Process Bus Incomer Protection Relay Circuit Breaker Closed Data Valid |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC01 |  | BMC131INC01PR1_CBClsRdy | BR4_Cluster1 | BPL131 | DIGITAL | %M10012 | BMC131 Process Bus Incomer Protection Relay Circuit Breaker Ready to Close |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC01 |  | BMC131INC01PR1_CBClsRdyDatOK | BR4_Cluster1 | BPL131 | DIGITAL | %M10013 | BMC131 Process Bus Incomer Protection Relay Circuit Breaker Ready To Close Data Valid |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC01 |  | BMC131INC01PR1_CBFlt | BR4_Cluster1 | BPL131 | DIGITAL | %M10014 | BMC131 Process Bus Incomer Protection Relay Fault |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC01 |  | BMC131INC01PR1_CBFlt_A | BR4_Cluster1 | BPL131 | DIGITAL | %M10015 | BMC131 Process Bus Incomer Protection Relay Fault Alarm |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC01 |  | BMC131INC01PR1_CBFltDatOK | BR4_Cluster1 | BPL131 | DIGITAL | %M10016 | BMC131 Process Bus Incomer Protection Relay Fault Data Valid |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC01 |  | BMC131INC01PR1_CBSprChr | BR4_Cluster1 | BPL131 | DIGITAL | %M10017 | BMC131 Process Bus Incomer Protection Relay Spring Charged |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC01 |  | BMC131INC01PR1_CBSprChrDatOK | BR4_Cluster1 | BPL131 | DIGITAL | %M10018 | BMC131 Process Bus Incomer Protection Relay Spring Charged Data Valid |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC01 |  | BMC131INC01PR1_ComFlt | BR4_Cluster1 | BPL131 | DIGITAL | %M10019 | BMC131 Process Bus Incomer Protection Relay Communications Fault |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.BTY1502.FieldIO |  | BTY1502DX02VDC02_I | BR4_Cluster1 | BPL131 | DIGITAL | %M1002 | West Turkeys Nest DIO Box 2 24VDC GW1 Control Supply (Q157) Healthy |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC01 |  | BMC131INC01PR1_ComFlt_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M10020 | BMC131 Process Bus Incomer Protection Relay Communications Fault Healthy |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC01.MasterPact | DatOK | BMC131INC01PR1_DatOK | BR4_Cluster1 | BPL131 | DIGITAL | %M10021 | BMC131 Process Bus Incomer Protection Relay Data Valid |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC01 |  | BMC131INC01PR1_Flt | BR4_Cluster1 | BPL131 | DIGITAL | %M10022 | BMC131 Process Bus Incomer Protection Relay Fault |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC01 |  | BMC131INC01PR1_Flt_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M10023 | BMC131 Process Bus Incomer Protection Relay Fault Healthy |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC01 |  | BMC131INC01PR1_LnkOK | BR4_Cluster1 | BPL131 | DIGITAL | %M10024 | BMC131 Process Bus Incomer Protection Relay Communications Link Active |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC01 |  | BMC131INC01PR1_MntRqd | BR4_Cluster1 | BPL131 | DIGITAL | %M10025 | BMC131 Process Bus Incomer Protection Relay Contactor Replacement Required |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC01 |  | BMC131INC01PR1_MntRqd_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M10026 | BMC131 Process Bus Incomer Protection Relay Contactor Replacement Required Healthy |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC01 |  | BMC131INC01PR1_OK | BR4_Cluster1 | BPL131 | DIGITAL | %M10027 | BMC131 Process Bus Incomer Protection Relay Healthy |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC01 |  | BMC131INC01PR1_PwrUp | BR4_Cluster1 | BPL131 | DIGITAL | %M10028 | BMC131 Process Bus Incomer Protection Relay Power Up in Progress |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC01.VAMP |  | BMC131INC01TRP02_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M10029 | BMC131 Process Bus Incomer Arc Flash Trip Healthy |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.BTY1502.FieldIO |  | BTY1502DX02VDC03_I | BR4_Cluster1 | BPL131 | DIGITAL | %M1003 | West Turkeys Nest DIO Box 2 24VDC Instrument Control Supply (Q164) Healthy |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC01 |  | BMC131INC01VDC01_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M10034 | BMC131 Process Bus Incomer 24VDC Control Supply (Q267) Failure Healthy |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC01.VAMP |  | BMC131INC01XS02_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M10036 | BMC131 Process Bus Incomer Vamp Self Supervision Fault Healthy |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC01 |  | BMC131INC01XS03_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M10037 | BMC131 Process Bus Incomer Surge Protection Healthy |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC02 |  | BMC131INC02CB03_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M10038 | BMC131 Essential Bus Incomer Incomer Circuit Breaker Spring Charge Supply (Q212) Open Healthy |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC02 |  | BMC131INC02CB04_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M10039 | BMC131 Essential Bus Incomer Incomer Circuit Breaker Trip Supply (Q220) Open Healthy |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.BTY1502.FieldIO |  | BTY1502DX02VDC04_I | BR4_Cluster1 | BPL131 | DIGITAL | %M1004 | West Turkeys Nest DIO Box 2 24VDC Transmitter Control Supply (Q168) Healthy |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC02 |  | BMC131INC02CB05_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M10040 | BMC131 Essential Bus Incomer Incomer Circuit Breaker 24VDC Cubicle Bus Supply (Q256) Open Healthy |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC02 |  | BMC131INC02CB06_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M10041 | BMC131 Essential Bus Incomer 110VDC/24VDC Power Supply (Q215) Open Healthy |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC02 |  | BMC131INC02PR1_CB_PwrOK | BR4_Cluster1 | BPL131 | DIGITAL | %M10042 | BMC131 Essential Bus Incomer Protection Relay Main Power to Drive Healthy |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC02 |  | BMC131INC02PR1_CBCls | BR4_Cluster1 | BPL131 | DIGITAL | %M10043 | BMC131 Essential Bus Incomer Protection Relay Circuit Breaker Closed |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC02 |  | BMC131INC02PR1_CBCls_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M10044 | BMC131 Essential Bus Incomer Protection Relay Circuit Breaker Healthy |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC02 |  | BMC131INC02PR1_CBClsDatOK | BR4_Cluster1 | BPL131 | DIGITAL | %M10045 | BMC131 Essential Bus Incomer Protection Relay Circuit Breaker Closed Data Valid |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC02 |  | BMC131INC02PR1_CBClsRdy | BR4_Cluster1 | BPL131 | DIGITAL | %M10046 | BMC131 Essential Bus Incomer Protection Relay Circuit Breaker Ready to Close |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC02 |  | BMC131INC02PR1_CBClsRdyDatOK | BR4_Cluster1 | BPL131 | DIGITAL | %M10047 | BMC131 Essential Bus Incomer Protection Relay Circuit Breaker Ready To Close Data Valid |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC02 |  | BMC131INC02PR1_CBFlt | BR4_Cluster1 | BPL131 | DIGITAL | %M10048 | BMC131 Essential Bus Incomer Protection Relay Fault |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC02 |  | BMC131INC02PR1_CBFlt_A | BR4_Cluster1 | BPL131 | DIGITAL | %M10049 | BMC131 Essential Bus Incomer Protection Relay Fault Alarm |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.BTY1502.FieldIO |  | BTY1502DX02VDC05_I | BR4_Cluster1 | BPL131 | DIGITAL | %M1005 | West Turkeys Nest DIO Box 2 24VDC Process Water Control Supply (Q172) Healthy |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC02 |  | BMC131INC02PR1_CBFltDatOK | BR4_Cluster1 | BPL131 | DIGITAL | %M10050 | BMC131 Essential Bus Incomer Protection Relay Fault Data Valid |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC02 |  | BMC131INC02PR1_CBSprChr | BR4_Cluster1 | BPL131 | DIGITAL | %M10051 | BMC131 Essential Bus Incomer Protection Relay Spring Charged |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC02 |  | BMC131INC02PR1_CBSprChrDatOK | BR4_Cluster1 | BPL131 | DIGITAL | %M10052 | BMC131 Essential Bus Incomer Protection Relay Spring Charged Data Valid |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC02 |  | BMC131INC02PR1_ComFlt | BR4_Cluster1 | BPL131 | DIGITAL | %M10053 | BMC131 Essential Bus Incomer Protection Relay Communications Fault |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC02 |  | BMC131INC02PR1_ComFlt_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M10054 | BMC131 Essential Bus Incomer Protection Relay Communications Fault Healthy |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC02.MasterPact | DatOK | BMC131INC02PR1_DatOK | BR4_Cluster1 | BPL131 | DIGITAL | %M10055 | BMC131 INC02 Essential Bus Incomer Protection Relay Data Valid |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC02 |  | BMC131INC02PR1_Flt | BR4_Cluster1 | BPL131 | DIGITAL | %M10056 | BMC131 Essential Bus Incomer Protection Relay Fault |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC02 |  | BMC131INC02PR1_Flt_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M10057 | BMC131 Essential Bus Incomer Protection Relay Fault Healthy |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC02 |  | BMC131INC02PR1_LnkOK | BR4_Cluster1 | BPL131 | DIGITAL | %M10058 | BMC131 Essential Bus Incomer Protection Relay Communications Link Active |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC02 |  | BMC131INC02PR1_MntRqd | BR4_Cluster1 | BPL131 | DIGITAL | %M10059 | BMC131 Essential Bus Incomer Protection Relay Contactor Replacement Required |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1101.FieldIO |  | BTY1502DX02VDC06_I | BR4_Cluster1 | BPL131 | DIGITAL | %M1006 | West Turkeys Nest DIO Box 2 24VDC BPP1101 Control Supply (Q176) Healthy |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC02 |  | BMC131INC02PR1_MntRqd_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M10060 | BMC131 Essential Bus Incomer Protection Relay Contactor Replacement Required Healthy |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC02 |  | BMC131INC02PR1_OK | BR4_Cluster1 | BPL131 | DIGITAL | %M10061 | BMC131 Essential Bus Incomer Protection Relay Healthy |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC02 |  | BMC131INC02PR1_PwrUp | BR4_Cluster1 | BPL131 | DIGITAL | %M10062 | BMC131 Essential Bus Incomer Protection Relay Power Up in Progress |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC02 |  | BMC131INC02VDC01_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M10064 | BMC131 Essential Bus Incomer 24VDC Control Supply (Q267) Failure Healthy |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC02 |  | BMC131INC02XS03_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M10067 | BMC131 Essential Bus Incomer Surge Protection Healthy |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1102.FieldIO |  | BTY1502DX02VDC07_I | BR4_Cluster1 | BPL131 | DIGITAL | %M1007 | West Turkeys Nest DIO Box 2 24VDC BPP1102 Control Supply (Q180) Healthy |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC03 |  | BMC131INC03PR1_CB_PwrOK | BR4_Cluster1 | BPL131 | DIGITAL | %M10073 | BMC131 Generator Bus Incomer Protection Relay Main Power to Drive Healthy |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC03 |  | BMC131INC03PR1_CBCls | BR4_Cluster1 | BPL131 | DIGITAL | %M10074 | BMC131 Generator Bus Incomer Protection Relay Circuit Breaker Closed |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC03 |  | BMC131INC03PR1_CBCls_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M10075 | BMC131 Generator Bus Incomer Protection Relay Circuit Breaker Healthy |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC03 |  | BMC131INC03PR1_CBClsDatOK | BR4_Cluster1 | BPL131 | DIGITAL | %M10076 | BMC131 Generator Bus Incomer Protection Relay Circuit Breaker Closed Data Valid |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC03 |  | BMC131INC03PR1_CBClsRdy | BR4_Cluster1 | BPL131 | DIGITAL | %M10077 | BMC131 Generator Bus Incomer Protection Relay Circuit Breaker Ready to Close |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC03 |  | BMC131INC03PR1_CBClsRdyDatOK | BR4_Cluster1 | BPL131 | DIGITAL | %M10078 | BMC131 Generator Bus Incomer Protection Relay Circuit Breaker Ready To Close Data Valid |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC03 |  | BMC131INC03PR1_CBFlt | BR4_Cluster1 | BPL131 | DIGITAL | %M10079 | BMC131 Generator Bus Incomer Protection Relay Fault |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BPP1106.FieldIO |  | BTY1502DX02VDC08_I | BR4_Cluster1 | BPL131 | DIGITAL | %M1008 | West Turkeys Nest DIO Box 2 24VDC BPP1106 Control Supply (Q184) Healthy |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC03 |  | BMC131INC03PR1_CBFlt_A | BR4_Cluster1 | BPL131 | DIGITAL | %M10080 | BMC131 Generator Bus Incomer Protection Relay Fault Alarm |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC03 |  | BMC131INC03PR1_CBFltDatOK | BR4_Cluster1 | BPL131 | DIGITAL | %M10081 | BMC131 Generator Bus Incomer Protection Relay Fault Data Valid |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC03 |  | BMC131INC03PR1_CBSprChr | BR4_Cluster1 | BPL131 | DIGITAL | %M10082 | BMC131 Generator Bus Incomer Protection Relay Spring Charged |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC03 |  | BMC131INC03PR1_CBSprChrDatOK | BR4_Cluster1 | BPL131 | DIGITAL | %M10083 | BMC131 Generator Bus Incomer Protection Relay Spring Charged Data Valid |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC03 |  | BMC131INC03PR1_ComFlt | BR4_Cluster1 | BPL131 | DIGITAL | %M10084 | BMC131 Generator Bus Incomer Protection Relay Communications Fault |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC03 |  | BMC131INC03PR1_ComFlt_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M10085 | BMC131 Generator Bus Incomer Protection Relay Communications Fault Healthy |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC03.MasterPact | DatOK | BMC131INC03PR1_DatOK | BR4_Cluster1 | BPL131 | DIGITAL | %M10086 | BMC131 INC03 Generator Bus Incomer Protection Relay Data Valid |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC03 |  | BMC131INC03PR1_Flt | BR4_Cluster1 | BPL131 | DIGITAL | %M10087 | BMC131 Generator Bus Incomer Protection Relay Fault |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC03 |  | BMC131INC03PR1_Flt_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M10088 | BMC131 Generator Bus Incomer Protection Relay Fault Healthy |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC03 |  | BMC131INC03PR1_LnkOK | BR4_Cluster1 | BPL131 | DIGITAL | %M10089 | BMC131 Generator Bus Incomer Protection Relay Communications Link Active |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BPP1107.FieldIO |  | BTY1502DX02VDC09_I | BR4_Cluster1 | BPL131 | DIGITAL | %M1009 | West Turkeys Nest DIO Box 2 24VDC BPP1107 Control Supply (Q188) Healthy |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC03 |  | BMC131INC03PR1_MntRqd | BR4_Cluster1 | BPL131 | DIGITAL | %M10090 | BMC131 Generator Bus Incomer Protection Relay Contactor Replacement Required |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC03 |  | BMC131INC03PR1_MntRqd_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M10091 | BMC131 Generator Bus Incomer Protection Relay Contactor Replacement Required Healthy |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC03 |  | BMC131INC03PR1_OK | BR4_Cluster1 | BPL131 | DIGITAL | %M10092 | BMC131 Generator Bus Incomer Protection Relay Healthy |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC03 |  | BMC131INC03PR1_PwrUp | BR4_Cluster1 | BPL131 | DIGITAL | %M10093 | BMC131 Generator Bus Incomer Protection Relay Power Up in Progress |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC03 |  | BMC131INC03VDC01_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M10095 | BMC131 Generator Bus Incomer 24VDC Control Supply (Q267) Failure Healthy |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131 |  | BPL131_MemFlt_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M10096 | NPI Hub PLC CPU Memory Card Error Healthy |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131 |  | BPL131_SetTm_CmdHMI | BR4_Cluster1 | BPL131 | DIGITAL | %M10097 | NPI Hub PLC CPU Set Time Command from HMI |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131 |  | BPL131_Sys1Flt_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M10098 | NPI Hub PLC CPU Arithmetic Fault Healthy |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131 |  | BPL131_Sys2Flt_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M10099 | NPI Hub PLC CPU Index Overflow Fault Healthy |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BSTD1106.FieldIO |  | BTY1502DX02VDC10_I | BR4_Cluster1 | BPL131 | DIGITAL | %M1010 | West Turkeys Nest DIO Box 2 24VDC BSTD1106 Control Supply (Q192) Healthy |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131 |  | BPL131IPC2_Flt_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M10100 | BPL131 Communications From BPL130 Fault Healthy |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131 |  | BPL131IPC2_OK | BR4_Cluster1 | BPL131 | DIGITAL | %M10101 | BPL131 Communications From BPL130 Healthy |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131 |  | BPL131IPC2_PriFlt_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M10102 | BPL131 Communications From BPL130 Primary Path Fault Healthy |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131 |  | BPL131IPC2_PriLnkOK | BR4_Cluster1 | BPL131 | DIGITAL | %M10103 | BPL131 Communications From BPL130 Primary Link Healthy |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131 |  | BPL131IPC2_SecFlt_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M10104 | BPL131 Communications From BPL130 Secondary Path Fault Alarm Acknowledge |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131 |  | BPL131IPC2_SecLnkOK | BR4_Cluster1 | BPL131 | DIGITAL | %M10105 | BPL131 Communications From BPL130 Secondary Link Healthy |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131 |  | BPL131IPC3_Flt_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M10106 | BPL131 Communications From BPL132 Fault Healthy |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131 |  | BPL131IPC3_OK | BR4_Cluster1 | BPL131 | DIGITAL | %M10107 | BPL131 Communications From BPL132 Healthy |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131 |  | BPL131IPC3_PriFlt_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M10108 | BPL131 Communications From BPL132 Primary Path Fault Healthy |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131 |  | BPL131IPC3_PriLnkOK | BR4_Cluster1 | BPL131 | DIGITAL | %M10109 | BPL131 Communications From BPL132 Primary Link Healthy |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BSTD1107.FieldIO |  | BTY1502DX02VDC11_I | BR4_Cluster1 | BPL131 | DIGITAL | %M1011 | West Turkeys Nest DIO Box 2 24VDC BSTD1107 Control Supply (Q196) Healthy |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131 |  | BPL131IPC3_SecFlt_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M10110 | BPL131 Communications From BPL132 Secondary Path Fault Alarm Acknowledge |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131 |  | BPL131IPC3_SecLnkOK | BR4_Cluster1 | BPL131 | DIGITAL | %M10111 | BPL131 Communications From BPL132 Secondary Link Healthy |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131 |  | BPL131PLM0_Flt_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M10112 | NPI Hub PLC CPU RIO Network Fault Healthy |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131 |  | BPL131PLM0_OK | BR4_Cluster1 | BPL131 | DIGITAL | %M10113 | NPI Hub PLC CPU RIO Network Healthy |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131 |  | BPL131PLM3_Flt_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M10115 | NPI Hub PLC Ethernet Module Slot 3 Fault Healthy |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131 |  | BPL131PLM3_OK | BR4_Cluster1 | BPL131 | DIGITAL | %M10116 | NPI Hub PLC Ethernet Module Slot 3 Healthy |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131 |  | BPL131PLM4_Flt_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M10117 | NPI Hub PLC Ethernet Module Slot 4 Fault Healthy |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131 |  | BPL131PLM4_OK | BR4_Cluster1 | BPL131 | DIGITAL | %M10118 | NPI Hub PLC Ethernet Module Slot 4 Healthy |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131 |  | BPL131PLM5_Flt_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M10119 | NPI Hub PLC Ethernet Module Slot 5 Fault Healthy |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131 |  | BPL131PLM5_OK | BR4_Cluster1 | BPL131 | DIGITAL | %M10120 | NPI Hub PLC Ethernet Module Slot 5 Healthy |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1101 | Auto | BPP1101_Aut | BR4_Cluster1 | BPL131 | DIGITAL | %M10121 | Production Plant and NPI Water Supply Pump 1 Mode Auto |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1101 |  | BPP1101_AutRdy | BR4_Cluster1 | BPL131 | DIGITAL | %M10123 | Production Plant and NPI Water Supply Pump 1 Auto Ready |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1101 |  | BPP1101_AutRun | BR4_Cluster1 | BPL131 | DIGITAL | %M10124 | Production Plant and NPI Water Supply Pump 1 Auto Running |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1101 |  | BPP1101_AuxStt | BR4_Cluster1 | BPL131 | DIGITAL | %M10125 | Production Plant and NPI Water Supply Pump 1 Auxiliary Drive Run Request |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1101 |  | BPP1101_CIL | BR4_Cluster1 | BPL131 | DIGITAL | %M10126 | Production Plant and NPI Water Supply Pump 1 Critical Interlock Healthy |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1101 |  | BPP1101_ComOK | BR4_Cluster1 | BPL131 | DIGITAL | %M10127 | Production Plant and NPI Water Supply Pump 1 Overall Communications Healthy |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1101 |  | BPP1101_CTS | BR4_Cluster1 | BPL131 | DIGITAL | %M10128 | Production Plant and NPI Water Supply Pump 1 Clear and Trial Complete (HMI Tag) |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1101 |  | BPP1101_FltSL | BR4_Cluster1 | BPL131 | DIGITAL | %M10129 | Production Plant and NPI Water Supply Pump 1 Fault Seal |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1101 |  | BPP1101_GrpSttSL | BR4_Cluster1 | BPL131 | DIGITAL | %M10130 | Production Plant and NPI Water Supply Pump 1 Group Start Seal |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1101 | Local | BPP1101_Loc | BR4_Cluster1 | BPL131 | DIGITAL | %M10131 | Production Plant and NPI Water Supply Pump 1 Mode Local |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1101 |  | BPP1101_LocRunIL | BR4_Cluster1 | BPL131 | DIGITAL | %M10133 | Production Plant and NPI Water Supply Pump 1 Local Run Interlock |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1101 |  | BPP1101_LocSttIL | BR4_Cluster1 | BPL131 | DIGITAL | %M10134 | Production Plant and NPI Water Supply Pump 1 Local Start Interlock |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1101 |  | BPP1101_NCIL | BR4_Cluster1 | BPL131 | DIGITAL | %M10135 | Production Plant and NPI Water Supply Pump 1 Non-Critical Interlock Healthy |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1101 |  | BPP1101_Off | BR4_Cluster1 | BPL131 | DIGITAL | %M10136 | Production Plant and NPI Water Supply Pump 1 Stopped |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1101 |  | BPP1101_OOS | BR4_Cluster1 | BPL131 | DIGITAL | %M10137 | Production Plant and NPI Water Supply Pump 1 Mode Out of Service |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1101 |  | BPP1101_PwrOK | BR4_Cluster1 | BPL131 | DIGITAL | %M10138 | Production Plant and NPI Water Supply Pump 1 Overall Power Healthy |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1101 |  | BPP1101_ReSttRqd | BR4_Cluster1 | BPL131 | DIGITAL | %M10139 | Production Plant and NPI Water Supply Pump 1 Restart Required |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1101 |  | BPP1101_RstRqd | BR4_Cluster1 | BPL131 | DIGITAL | %M10140 | Production Plant and NPI Water Supply Pump 1 Reset Required |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1101 |  | BPP1101_Run | BR4_Cluster1 | BPL131 | DIGITAL | %M10141 | Production Plant and NPI Water Supply Pump 1 Running |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1101 |  | BPP1101_SeqReq | BR4_Cluster1 | BPL131 | DIGITAL | %M10144 | Production Plant and NPI Water Supply Pump 1 Requested by Pump Station Sequence |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1101 |  | BPP1101_SeqRunIL | BR4_Cluster1 | BPL131 | DIGITAL | %M10145 | Production Plant and NPI Water Supply Pump 1 Sequence Run Interlock |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1101 |  | BPP1101_SeqStpIL | BR4_Cluster1 | BPL131 | DIGITAL | %M10146 | Production Plant and NPI Water Supply Pump 1 Sequence Stop Interlock |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1101 |  | BPP1101_SeqSttIL | BR4_Cluster1 | BPL131 | DIGITAL | %M10147 | Production Plant and NPI Water Supply Pump 1 Sequence Start Interlock |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1101 |  | BPP1101_Stp | BR4_Cluster1 | BPL131 | DIGITAL | %M10148 | Production Plant and NPI Water Supply Pump 1 Stopping |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1101 |  | BPP1101_Stt | BR4_Cluster1 | BPL131 | DIGITAL | %M10149 | Production Plant and NPI Water Supply Pump 1 Starting |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1101.Sub.CB01 |  | BPP1101CB01_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M10150 | Production Plant and NPI Water Supply Pump 1 Main Circuit Breaker (Q103) Open Healthy |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1101.FieldIO.FT01 |  | BPP1101FT01_ChOK | BR4_Cluster1 | BPL131 | DIGITAL | %M10154 | Production Plant and NPI Water Supply Pump 1 Flow Rate (m3/h) Channel Healthy |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1101 |  | BPP1101PIC01_Aut | BR4_Cluster1 | BPL131 | DIGITAL | %M10157 | BPP1101 Pressure Controller Auto Mode |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1101 |  | BPP1101PIC01_AutEn | BR4_Cluster1 | BPL131 | DIGITAL | %M10158 | BPP1101 Pressure Controller Auto Enabled |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1101 |  | BPP1101PIC01_Man | BR4_Cluster1 | BPL131 | DIGITAL | %M10160 | BPP1101 Pressure Controller Manual Mode |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1101.FieldIO.PT03 |  | BPP1101PT03_ChOK | BR4_Cluster1 | BPL131 | DIGITAL | %M10161 | Production Plant and NPI Water Supply Pump 1 Discharge Pressure (kPa) Channel Healthy |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1101.FieldIO.PT10 |  | BPP1101PT10_ChOK | BR4_Cluster1 | BPL131 | DIGITAL | %M10162 | Production Plant and NPI Water Supply Pump 1 Discharge Pressure 1 (kPa) Channel Healthy |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1101.FieldIO.PT11 |  | BPP1101PT11_ChOK | BR4_Cluster1 | BPL131 | DIGITAL | %M10163 | Production Plant and NPI Water Supply Pump 1 Discharge Pressure 2 (kPa) Channel Healthy |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1101 |  | BPP1101STS1_Iso | BR4_Cluster1 | BPL131 | DIGITAL | %M10164 | Production Plant and NPI Water Supply Pump 1 Isolated |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1101 |  | BPP1101STS1_SysOK | BR4_Cluster1 | BPL131 | DIGITAL | %M10165 | Production Plant and NPI Water Supply Pump 1 Overall Control System Healthy |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1101 |  | BPP1101THR01_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M10171 | Production Plant and NPI Water Supply Pump 1 Production Plant & NPI Water Supply Pump 1 (Duty) (K190) Healthy |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1101 |  | BPP1101VDC01_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M10176 | Production Plant and NPI Water Supply Pump 1 24VDC Control Supply (Q155) Failure Healthy |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1101.VS01 |  | BPP1101VS01VDC01_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M10179 | BPP1101VS01 VVVF Drive BPP1101VS01 Control Supply (Q204) Failure Healthy |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1102 | Auto | BPP1102_Aut | BR4_Cluster1 | BPL131 | DIGITAL | %M10199 | Production Plant and NPI Water Supply Pump 2 Mode Auto |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1102 |  | BPP1102_AutRdy | BR4_Cluster1 | BPL131 | DIGITAL | %M10201 | Production Plant and NPI Water Supply Pump 2 Auto Ready |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1102 |  | BPP1102_AutRun | BR4_Cluster1 | BPL131 | DIGITAL | %M10202 | Production Plant and NPI Water Supply Pump 2 Auto Running |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1102 |  | BPP1102_AuxStt | BR4_Cluster1 | BPL131 | DIGITAL | %M10203 | Production Plant and NPI Water Supply Pump 2 Auxiliary Drive Run Request |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1102 |  | BPP1102_CIL | BR4_Cluster1 | BPL131 | DIGITAL | %M10204 | Production Plant and NPI Water Supply Pump 2 Critical Interlock Healthy |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1102 |  | BPP1102_ComOK | BR4_Cluster1 | BPL131 | DIGITAL | %M10205 | Production Plant and NPI Water Supply Pump 2 Overall Communications Healthy |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1102 |  | BPP1102_CTS | BR4_Cluster1 | BPL131 | DIGITAL | %M10206 | Production Plant and NPI Water Supply Pump 2 Clear and Trial Complete (HMI Tag) |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1102 |  | BPP1102_FltSL | BR4_Cluster1 | BPL131 | DIGITAL | %M10207 | Production Plant and NPI Water Supply Pump 2 Fault Seal |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1102 |  | BPP1102_GrpSttSL | BR4_Cluster1 | BPL131 | DIGITAL | %M10208 | Production Plant and NPI Water Supply Pump 2 Group Start Seal |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1102 | Local | BPP1102_Loc | BR4_Cluster1 | BPL131 | DIGITAL | %M10209 | Production Plant and NPI Water Supply Pump 2 Mode Local |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1102 |  | BPP1102_LocRunIL | BR4_Cluster1 | BPL131 | DIGITAL | %M10211 | Production Plant and NPI Water Supply Pump 2 Local Run Interlock |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1102 |  | BPP1102_LocSttIL | BR4_Cluster1 | BPL131 | DIGITAL | %M10212 | Production Plant and NPI Water Supply Pump 2 Local Start Interlock |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1102 |  | BPP1102_NCIL | BR4_Cluster1 | BPL131 | DIGITAL | %M10213 | Production Plant and NPI Water Supply Pump 2 Non-Critical Interlock Healthy |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1102 |  | BPP1102_Off | BR4_Cluster1 | BPL131 | DIGITAL | %M10214 | Production Plant and NPI Water Supply Pump 2 Stopped |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1102 |  | BPP1102_OOS | BR4_Cluster1 | BPL131 | DIGITAL | %M10215 | Production Plant and NPI Water Supply Pump 2 Mode Out of Service |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1102 |  | BPP1102_PwrOK | BR4_Cluster1 | BPL131 | DIGITAL | %M10217 | Production Plant and NPI Water Supply Pump 2 Overall Power Healthy |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1102 |  | BPP1102_ReSttRqd | BR4_Cluster1 | BPL131 | DIGITAL | %M10218 | Production Plant and NPI Water Supply Pump 2 Restart Required |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1102 |  | BPP1102_RstRqd | BR4_Cluster1 | BPL131 | DIGITAL | %M10219 | Production Plant and NPI Water Supply Pump 2 Reset Required |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1102 |  | BPP1102_Run | BR4_Cluster1 | BPL131 | DIGITAL | %M10220 | Production Plant and NPI Water Supply Pump 2 Running |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1102 |  | BPP1102_SeqReq | BR4_Cluster1 | BPL131 | DIGITAL | %M10223 | Production Plant and NPI Water Supply Pump 2 Requested by Pump Station Sequence |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1102 |  | BPP1102_SeqRunIL | BR4_Cluster1 | BPL131 | DIGITAL | %M10224 | Production Plant and NPI Water Supply Pump 2 Sequence Run Interlock |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1102 |  | BPP1102_SeqStpIL | BR4_Cluster1 | BPL131 | DIGITAL | %M10225 | Production Plant and NPI Water Supply Pump 2 Sequence Stop Interlock |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1102 |  | BPP1102_SeqSttIL | BR4_Cluster1 | BPL131 | DIGITAL | %M10226 | Production Plant and NPI Water Supply Pump 2 Sequence Start Interlock |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1102 |  | BPP1102_Stp | BR4_Cluster1 | BPL131 | DIGITAL | %M10227 | Production Plant and NPI Water Supply Pump 2 Stopping |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1102 |  | BPP1102_Stt | BR4_Cluster1 | BPL131 | DIGITAL | %M10228 | Production Plant and NPI Water Supply Pump 2 Starting |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1102.Sub.CB01 |  | BPP1102CB01_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M10229 | Production Plant and NPI Water Supply Pump 2 Main Circuit Breaker (Q103) Open Healthy |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1102.FieldIO.PT04 |  | BPP1102PT04_ChOK | BR4_Cluster1 | BPL131 | DIGITAL | %M10233 | Production Plant and NPI Water Supply Pump 2 Discharge Pressure (kPa) Channel Healthy |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1102 |  | BPP1102STS1_Iso | BR4_Cluster1 | BPL131 | DIGITAL | %M10234 | Production Plant and NPI Water Supply Pump 2 Isolated |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1102 |  | BPP1102STS1_SysOK | BR4_Cluster1 | BPL131 | DIGITAL | %M10235 | Production Plant and NPI Water Supply Pump 2 Overall Control System Healthy |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1102 |  | BPP1102THR01_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M10241 | Production Plant and NPI Water Supply Pump 2 Production Plant & NPI Water Supply Pump 2 (Standby) (K190) Healthy |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1102 |  | BPP1102VDC01_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M10242 | Production Plant and NPI Water Supply Pump 2 24VDC Control Supply (Q155) Failure Healthy |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1102.VS01 |  | BPP1102VS01VDC01_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M10245 | BPP1101VS01 VVVF Drive BPP1102VS01 Control Supply (Q207) Failure Healthy |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BPP1106 |  | BPP1106THR01_I | BR4_Cluster1 | BPL131 | DIGITAL | %M1026 | HME & LME Standpipe Pump 3 HME And LME Standpipe Pump 3 (Duty) (K190) Healthy |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1103 | Auto | BPP1103_Aut | BR4_Cluster1 | BPL131 | DIGITAL | %M10265 | Water Transfer Pump 1 Mode Auto |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1103 |  | BPP1103_AutRdy | BR4_Cluster1 | BPL131 | DIGITAL | %M10267 | Water Transfer Pump 1 Auto Ready |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1103 |  | BPP1103_AutRun | BR4_Cluster1 | BPL131 | DIGITAL | %M10268 | Water Transfer Pump 1 Auto Running |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1103 |  | BPP1103_AuxStt | BR4_Cluster1 | BPL131 | DIGITAL | %M10269 | Water Transfer Pump 1 Auxiliary Drive Run Request |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BPP1107.Sub.CB01 |  | BPP1107THR01_I | BR4_Cluster1 | BPL131 | DIGITAL | %M1027 | HME & LME Standpipe Pump 4 HME And LME Standpipe Pump 4 (Standby) (K190) Healthy |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1103 |  | BPP1103_CIL | BR4_Cluster1 | BPL131 | DIGITAL | %M10270 | Water Transfer Pump 1 Critical Interlock Healthy |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1103 |  | BPP1103_ComOK | BR4_Cluster1 | BPL131 | DIGITAL | %M10271 | Water Transfer Pump 1 Overall Communications Healthy |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1103 |  | BPP1103_CTS | BR4_Cluster1 | BPL131 | DIGITAL | %M10272 | Water Transfer Pump 1 Clear and Trial Complete (HMI Tag) |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1103 |  | BPP1103_FltSL | BR4_Cluster1 | BPL131 | DIGITAL | %M10273 | Water Transfer Pump 1 Fault Seal |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1103 |  | BPP1103_GrpSttSL | BR4_Cluster1 | BPL131 | DIGITAL | %M10274 | Water Transfer Pump 1 Group Start Seal |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1103 | Local | BPP1103_Loc | BR4_Cluster1 | BPL131 | DIGITAL | %M10275 | Water Transfer Pump 1 Mode Local |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1103 |  | BPP1103_LocRunIL | BR4_Cluster1 | BPL131 | DIGITAL | %M10277 | Water Transfer Pump 1 Local Run Interlock |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1103 |  | BPP1103_LocSttIL | BR4_Cluster1 | BPL131 | DIGITAL | %M10278 | Water Transfer Pump 1 Local Start Interlock |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1103 |  | BPP1103_NCIL | BR4_Cluster1 | BPL131 | DIGITAL | %M10279 | Water Transfer Pump 1 Non-Critical Interlock Healthy |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1101 |  | BPP1101THR01_I | BR4_Cluster1 | BPL131 | DIGITAL | %M1028 | Production Plant and NPI Water Supply Pump 1 Production Plant & NPI Water Supply Pump 1 (Duty) (K190) Healthy |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1103 |  | BPP1103_Off | BR4_Cluster1 | BPL131 | DIGITAL | %M10280 | Water Transfer Pump 1 Stopped |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1103 |  | BPP1103_OOS | BR4_Cluster1 | BPL131 | DIGITAL | %M10281 | Water Transfer Pump 1 Mode Out of Service |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1103 |  | BPP1103_PwrOK | BR4_Cluster1 | BPL131 | DIGITAL | %M10283 | Water Transfer Pump 1 Overall Power Healthy |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1103 |  | BPP1103_ReSttRqd | BR4_Cluster1 | BPL131 | DIGITAL | %M10284 | Water Transfer Pump 1 Restart Required |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1103 |  | BPP1103_RstRqd | BR4_Cluster1 | BPL131 | DIGITAL | %M10285 | Water Transfer Pump 1 Reset Required |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1103 |  | BPP1103_Run | BR4_Cluster1 | BPL131 | DIGITAL | %M10286 | Water Transfer Pump 1 Running |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1103 |  | BPP1103_SeqReq | BR4_Cluster1 | BPL131 | DIGITAL | %M10289 | Water Transfer Pump 1 Requested by Pump Station Sequence |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1102 |  | BPP1102THR01_I | BR4_Cluster1 | BPL131 | DIGITAL | %M1029 | Production Plant and NPI Water Supply Pump 2 Production Plant & NPI Water Supply Pump 2 (Standby) (K190) Healthy |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1103 |  | BPP1103_SeqRunIL | BR4_Cluster1 | BPL131 | DIGITAL | %M10290 | Water Transfer Pump 1 Sequence Run Interlock |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1103 |  | BPP1103_SeqStpIL | BR4_Cluster1 | BPL131 | DIGITAL | %M10291 | Water Transfer Pump 1 Sequence Stop Interlock |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1103 |  | BPP1103_SeqSttIL | BR4_Cluster1 | BPL131 | DIGITAL | %M10292 | Water Transfer Pump 1 Sequence Start Interlock |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1103 |  | BPP1103_Stp | BR4_Cluster1 | BPL131 | DIGITAL | %M10293 | Water Transfer Pump 1 Stopping |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1103 |  | BPP1103_Stt | BR4_Cluster1 | BPL131 | DIGITAL | %M10294 | Water Transfer Pump 1 Starting |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1103.Sub.CB01 |  | BPP1103CB01_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M10295 | Water Transfer Pump 1 Main Circuit Breaker (Q103) Open Healthy |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1103.FieldIO.FT03 |  | BPP1103FT03_ChOK | BR4_Cluster1 | BPL131 | DIGITAL | %M10299 | Water Transfer Pump 1 Flow Rate (m3/h) Channel Healthy |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BPP1106 |  | BPP1106FS07_I | BR4_Cluster1 | BPL131 | DIGITAL | %M1030 | HME & LME Standpipe Pump 3 HME And LME Standpipe Pump 3 Flow Low |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1103.FieldIO.FT06 |  | BPP1103FT06_ChOK | BR4_Cluster1 | BPL131 | DIGITAL | %M10300 | Water Transfer Pump 1 Flow Rate (m3/h) Channel Healthy |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1103 |  | BPP1103LIC01_Aut | BR4_Cluster1 | BPL131 | DIGITAL | %M10301 | West Turkeys Nest Level Controller Auto Mode |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1103 |  | BPP1103LIC01_AutEn | BR4_Cluster1 | BPL131 | DIGITAL | %M10302 | West Turkeys Nest Level Controller Auto Enabled |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1103 |  | BPP1103LIC01_Man | BR4_Cluster1 | BPL131 | DIGITAL | %M10304 | West Turkeys Nest Level Controller Manual Mode |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1103.FieldIO.PT05 |  | BPP1103PT05_ChOK | BR4_Cluster1 | BPL131 | DIGITAL | %M10305 | Water Transfer Pump 1 Discharge Pressure (kPa) Channel Healthy |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1103.FieldIO.PT08 |  | BPP1103PT08_ChOK | BR4_Cluster1 | BPL131 | DIGITAL | %M10306 | Water Transfer Pump 1 Discharge Pressure (kPa) Channel Healthy |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1103 |  | BPP1103STS1_Iso | BR4_Cluster1 | BPL131 | DIGITAL | %M10307 | Water Transfer Pump 1 Isolated |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1103 |  | BPP1103STS1_SysOK | BR4_Cluster1 | BPL131 | DIGITAL | %M10308 | Water Transfer Pump 1 Overall Control System Healthy |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BPP1107 |  | BPP1107FS08_I | BR4_Cluster1 | BPL131 | DIGITAL | %M1031 | HME & LME Standpipe Pump 4 HME And LME Standpipe Pump 4 Flow Low |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1103 |  | BPP1103THR01_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M10314 | Water Transfer Pump 1 Thermistor Relay (K190) Healthy |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1103 |  | BPP1103VDC01_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M10315 | Water Transfer Pump 1 24VDC Control Supply (Q155) Failure Healthy |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1103.VS01 |  | BPP1103VS01VDC01_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M10318 | BPP1101VS01 VVVF Drive BPP1103VS01 Control Supply (Q210) Failure Healthy |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BSTD1106.FieldIO.FT03 |  | BSTD1106FQ03_I | BR4_Cluster1 | BPL131 | DIGITAL | %M1032 | West Turkeys Nest LME Standpipe Flow Pulse |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BSTD1107 |  | BSTD1107FQ02_I | BR4_Cluster1 | BPL131 | DIGITAL | %M1033 | West Turkeys Nest HME Standpipe HME Standpipe Pulse |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1104 | Auto | BPP1104_Aut | BR4_Cluster1 | BPL131 | DIGITAL | %M10338 | Water Transfer Pump 2 Mode Auto |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.BTY1502.FieldIO.FT01 |  | BTY1502FQ01_I | BR4_Cluster1 | BPL131 | DIGITAL | %M1034 | West Turkeys Nest Raw Water From East Pit Pulse |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1104 |  | BPP1104_AutRdy | BR4_Cluster1 | BPL131 | DIGITAL | %M10340 | Water Transfer Pump 2 Auto Ready |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1104 |  | BPP1104_AutRun | BR4_Cluster1 | BPL131 | DIGITAL | %M10341 | Water Transfer Pump 2 Auto Running |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1104 |  | BPP1104_AuxStt | BR4_Cluster1 | BPL131 | DIGITAL | %M10342 | Water Transfer Pump 2 Auxiliary Drive Run Request |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1104 |  | BPP1104_CIL | BR4_Cluster1 | BPL131 | DIGITAL | %M10343 | Water Transfer Pump 2 Critical Interlock Healthy |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1104 |  | BPP1104_ComOK | BR4_Cluster1 | BPL131 | DIGITAL | %M10344 | Water Transfer Pump 2 Overall Communications Healthy |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1104 |  | BPP1104_CTS | BR4_Cluster1 | BPL131 | DIGITAL | %M10345 | Water Transfer Pump 2 Clear and Trial Complete (HMI Tag) |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1104 |  | BPP1104_FltSL | BR4_Cluster1 | BPL131 | DIGITAL | %M10346 | Water Transfer Pump 2 Fault Seal |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1104 |  | BPP1104_GrpSttSL | BR4_Cluster1 | BPL131 | DIGITAL | %M10347 | Water Transfer Pump 2 Group Start Seal |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1104 | Local | BPP1104_Loc | BR4_Cluster1 | BPL131 | DIGITAL | %M10348 | Water Transfer Pump 2 Mode Local |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.BTY1502.FieldIO.FT03 |  | BTY1502FQ03_I | BR4_Cluster1 | BPL131 | DIGITAL | %M1035 | West Turkeys Nest Raw Water From West Pit Pulse |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1104 |  | BPP1104_LocRunIL | BR4_Cluster1 | BPL131 | DIGITAL | %M10350 | Water Transfer Pump 2 Local Run Interlock |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1104 |  | BPP1104_LocSttIL | BR4_Cluster1 | BPL131 | DIGITAL | %M10351 | Water Transfer Pump 2 Local Start Interlock |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1104 |  | BPP1104_NCIL | BR4_Cluster1 | BPL131 | DIGITAL | %M10352 | Water Transfer Pump 2 Non-Critical Interlock Healthy |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1104 |  | BPP1104_Off | BR4_Cluster1 | BPL131 | DIGITAL | %M10353 | Water Transfer Pump 2 Stopped |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1104 |  | BPP1104_OOS | BR4_Cluster1 | BPL131 | DIGITAL | %M10354 | Water Transfer Pump 2 Mode Out of Service |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1104 |  | BPP1104_PwrOK | BR4_Cluster1 | BPL131 | DIGITAL | %M10356 | Water Transfer Pump 2 Overall Power Healthy |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1104 |  | BPP1104_ReSttRqd | BR4_Cluster1 | BPL131 | DIGITAL | %M10357 | Water Transfer Pump 2 Restart Required |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1104 |  | BPP1104_RstRqd | BR4_Cluster1 | BPL131 | DIGITAL | %M10358 | Water Transfer Pump 2 Reset Required |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1104 |  | BPP1104_Run | BR4_Cluster1 | BPL131 | DIGITAL | %M10359 | Water Transfer Pump 2 Running |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.BTY1502 |  | BTY1502LS01_I | BR4_Cluster1 | BPL131 | DIGITAL | %M1036 | West Turkeys Nest West Turkeys Nest Healthy |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1104 |  | BPP1104_SeqReq | BR4_Cluster1 | BPL131 | DIGITAL | %M10362 | Water Transfer Pump 2 Requested by Pump Station Sequence |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1104 |  | BPP1104_SeqRunIL | BR4_Cluster1 | BPL131 | DIGITAL | %M10363 | Water Transfer Pump 2 Sequence Run Interlock |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1104 |  | BPP1104_SeqStpIL | BR4_Cluster1 | BPL131 | DIGITAL | %M10364 | Water Transfer Pump 2 Sequence Stop Interlock |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1104 |  | BPP1104_SeqSttIL | BR4_Cluster1 | BPL131 | DIGITAL | %M10365 | Water Transfer Pump 2 Sequence Start Interlock |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1104 |  | BPP1104_Stp | BR4_Cluster1 | BPL131 | DIGITAL | %M10366 | Water Transfer Pump 2 Stopping |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1104 |  | BPP1104_Stt | BR4_Cluster1 | BPL131 | DIGITAL | %M10367 | Water Transfer Pump 2 Starting |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1104.Sub.CB01 |  | BPP1104CB01_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M10368 | Water Transfer Pump 2 Main Circuit Breaker (Q103) Open Healthy |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1101 |  | BPP1101FS09_I | BR4_Cluster1 | BPL131 | DIGITAL | %M1037 | Production Plant and NPI Water Supply Pump 1 Production Plant & NPI Water Supply Pump 1 (Duty) Flow Low |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1104.FieldIO.FT04 |  | BPP1104FT04_ChOK | BR4_Cluster1 | BPL131 | DIGITAL | %M10372 | Water Transfer Pump 2 Flow Rate (m3/h) Channel Healthy |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1104.FieldIO.PT06 |  | BPP1104PT06_ChOK | BR4_Cluster1 | BPL131 | DIGITAL | %M10373 | Water Transfer Pump 2 Discharge Pressure (kPa) Channel Healthy |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1104 |  | BPP1104STS1_Iso | BR4_Cluster1 | BPL131 | DIGITAL | %M10374 | Water Transfer Pump 2 Isolated |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1104 |  | BPP1104STS1_SysOK | BR4_Cluster1 | BPL131 | DIGITAL | %M10375 | Water Transfer Pump 2 Overall Control System Healthy |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1102 |  | BPP1102FS10_I | BR4_Cluster1 | BPL131 | DIGITAL | %M1038 | Production Plant and NPI Water Supply Pump 2 Production Plant & NPI Water Supply Pump 2 (Standby) Flow Low |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1104 |  | BPP1104THR01_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M10381 | Water Transfer Pump 2 Thermistor Relay (K190) Healthy |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1104 |  | BPP1104VDC01_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M10382 | Water Transfer Pump 2 24VDC Control Supply (Q155) Failure Healthy |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1104.VS01 |  | BPP1104VS01VDC01_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M10385 | BPP1101VS01 VVVF Drive BPP1104VS01 Control Supply (Q213) Failure Healthy |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1101 |  | BPP1101FQ03_I | BR4_Cluster1 | BPL131 | DIGITAL | %M1039 | Production Plant and NPI Water Supply Pump 1 Production Plant & NPI Water Supply Pulse |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.BTY1502.FieldIO.FT02 |  | BTY1502FQ02_I | BR4_Cluster1 | BPL131 | DIGITAL | %M1040 | West Turkeys Nest West Turkeys Nest Pulse |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1105 | Auto | BPP1105_Aut | BR4_Cluster1 | BPL131 | DIGITAL | %M10405 | Water Transfer Pump 3 Mode Auto |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1105 |  | BPP1105_AutRdy | BR4_Cluster1 | BPL131 | DIGITAL | %M10407 | Water Transfer Pump 3 Auto Ready |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1105 |  | BPP1105_AutRun | BR4_Cluster1 | BPL131 | DIGITAL | %M10408 | Water Transfer Pump 3 Auto Running |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1105 |  | BPP1105_AuxStt | BR4_Cluster1 | BPL131 | DIGITAL | %M10409 | Water Transfer Pump 3 Auxiliary Drive Run Request |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BSTD1106.FV03 |  | BSTD1106FV03ZS01_I | BR4_Cluster1 | BPL131 | DIGITAL | %M1041 | West Turkeys Nest LME Standpipe Flow Valve Open |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1105 |  | BPP1105_CIL | BR4_Cluster1 | BPL131 | DIGITAL | %M10410 | Water Transfer Pump 3 Critical Interlock Healthy |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1105 |  | BPP1105_ComOK | BR4_Cluster1 | BPL131 | DIGITAL | %M10411 | Water Transfer Pump 3 Overall Communications Healthy |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1105 |  | BPP1105_CTS | BR4_Cluster1 | BPL131 | DIGITAL | %M10412 | Water Transfer Pump 3 Clear and Trial Complete (HMI Tag) |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1105 |  | BPP1105_FltSL | BR4_Cluster1 | BPL131 | DIGITAL | %M10413 | Water Transfer Pump 3 Fault Seal |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1105 |  | BPP1105_GrpSttSL | BR4_Cluster1 | BPL131 | DIGITAL | %M10414 | Water Transfer Pump 3 Group Start Seal |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1105 | Local | BPP1105_Loc | BR4_Cluster1 | BPL131 | DIGITAL | %M10415 | Water Transfer Pump 3 Mode Local |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1105 |  | BPP1105_LocRunIL | BR4_Cluster1 | BPL131 | DIGITAL | %M10417 | Water Transfer Pump 3 Local Run Interlock |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1105 |  | BPP1105_LocSttIL | BR4_Cluster1 | BPL131 | DIGITAL | %M10418 | Water Transfer Pump 3 Local Start Interlock |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1105 |  | BPP1105_NCIL | BR4_Cluster1 | BPL131 | DIGITAL | %M10419 | Water Transfer Pump 3 Non-Critical Interlock Healthy |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BSTD1106.FV03 |  | BSTD1106FV03ZS02_I | BR4_Cluster1 | BPL131 | DIGITAL | %M1042 | West Turkeys Nest LME Standpipe Flow Valve Closed |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1105 |  | BPP1105_Off | BR4_Cluster1 | BPL131 | DIGITAL | %M10420 | Water Transfer Pump 3 Stopped |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1105 |  | BPP1105_OOS | BR4_Cluster1 | BPL131 | DIGITAL | %M10421 | Water Transfer Pump 3 Mode Out of Service |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1105 |  | BPP1105_PwrOK | BR4_Cluster1 | BPL131 | DIGITAL | %M10423 | Water Transfer Pump 3 Overall Power Healthy |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1105 |  | BPP1105_ReSttRqd | BR4_Cluster1 | BPL131 | DIGITAL | %M10424 | Water Transfer Pump 3 Restart Required |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1105 |  | BPP1105_RstRqd | BR4_Cluster1 | BPL131 | DIGITAL | %M10425 | Water Transfer Pump 3 Reset Required |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1105 |  | BPP1105_Run | BR4_Cluster1 | BPL131 | DIGITAL | %M10426 | Water Transfer Pump 3 Running |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1105 |  | BPP1105_SeqReq | BR4_Cluster1 | BPL131 | DIGITAL | %M10429 | Water Transfer Pump 3 Requested by Pump Station Sequence |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BSTD1106.FV03 |  | BSTD1106FV03SW01_I | BR4_Cluster1 | BPL131 | DIGITAL | %M1043 | West Turkeys Nest LME Standpipe Flow Valve Local Mode Selected |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1105 |  | BPP1105_SeqRunIL | BR4_Cluster1 | BPL131 | DIGITAL | %M10430 | Water Transfer Pump 3 Sequence Run Interlock |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1105 |  | BPP1105_SeqStpIL | BR4_Cluster1 | BPL131 | DIGITAL | %M10431 | Water Transfer Pump 3 Sequence Stop Interlock |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1105 |  | BPP1105_SeqSttIL | BR4_Cluster1 | BPL131 | DIGITAL | %M10432 | Water Transfer Pump 3 Sequence Start Interlock |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1105 |  | BPP1105_Stp | BR4_Cluster1 | BPL131 | DIGITAL | %M10433 | Water Transfer Pump 3 Stopping |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1105 |  | BPP1105_Stt | BR4_Cluster1 | BPL131 | DIGITAL | %M10434 | Water Transfer Pump 3 Starting |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1105.Sub.CB01 |  | BPP1105CB01_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M10435 | Water Transfer Pump 3 Main Circuit Breaker (Q103) Open Healthy |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1105.FieldIO.FT05 |  | BPP1105FT05_ChOK | BR4_Cluster1 | BPL131 | DIGITAL | %M10439 | Water Transfer Pump 3 Flow Rate (m3/h) Channel Healthy |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BSTD1106.FV03 |  | BSTD1106FV03XS01_I | BR4_Cluster1 | BPL131 | DIGITAL | %M1044 | West Turkeys Nest LME Standpipe Flow Valve Fault |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1105.FieldIO.PT07 |  | BPP1105PT07_ChOK | BR4_Cluster1 | BPL131 | DIGITAL | %M10440 | Water Transfer Pump 3 Discharge Pressure (kPa) Channel Healthy |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1105 |  | BPP1105STS1_Iso | BR4_Cluster1 | BPL131 | DIGITAL | %M10441 | Water Transfer Pump 3 Isolated |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1105 |  | BPP1105STS1_SysOK | BR4_Cluster1 | BPL131 | DIGITAL | %M10442 | Water Transfer Pump 3 Overall Control System Healthy |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1105 |  | BPP1105THR01_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M10448 | Water Transfer Pump 3 Thermistor Relay (K190) Healthy |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1105 |  | BPP1105VDC01_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M10449 | Water Transfer Pump 3 24VDC Control Supply (Q155) Failure Healthy |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BSTD1106.FV03.FieldIO.CB01 |  | BSTD1106FV03CB01_I | BR4_Cluster1 | BPL131 | DIGITAL | %M1045 | West Turkeys Nest LME Standpipe 240VAC Flow Valve Power Circuit Breaker Closed |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1105.VS01 |  | BPP1105VS01VDC01_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M10452 | BPP1101VS01 VVVF Drive BPP1105VS01 Control Supply (Q216) Failure Healthy |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BSTD1107.FV02 |  | BSTD1107FV02ZS01_I | BR4_Cluster1 | BPL131 | DIGITAL | %M1046 | West Turkeys Nest HME Standpipe Flow Valve Open |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BSTD1107.FV02 |  | BSTD1107FV02ZS02_I | BR4_Cluster1 | BPL131 | DIGITAL | %M1047 | West Turkeys Nest HME Standpipe Flow Valve Closed |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BPP1106 | Auto | BPP1106_Aut | BR4_Cluster1 | BPL131 | DIGITAL | %M10472 | HME & LME Standpipe Pump 3 Mode Auto |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BPP1106 |  | BPP1106_AutRdy | BR4_Cluster1 | BPL131 | DIGITAL | %M10474 | HME & LME Standpipe Pump 3 Auto Ready |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BPP1106 |  | BPP1106_AutRun | BR4_Cluster1 | BPL131 | DIGITAL | %M10475 | HME & LME Standpipe Pump 3 Auto Running |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BPP1106 |  | BPP1106_AuxStt | BR4_Cluster1 | BPL131 | DIGITAL | %M10476 | HME & LME Standpipe Pump 3 Auxiliary Drive Run Request |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BPP1106 |  | BPP1106_CIL | BR4_Cluster1 | BPL131 | DIGITAL | %M10477 | HME & LME Standpipe Pump 3 Critical Interlock Healthy |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BPP1106 |  | BPP1106_ComOK | BR4_Cluster1 | BPL131 | DIGITAL | %M10478 | HME & LME Standpipe Pump 3 Overall Communications Healthy |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BPP1106 |  | BPP1106_CTS | BR4_Cluster1 | BPL131 | DIGITAL | %M10479 | HME & LME Standpipe Pump 3 Clear and Trial Complete (HMI Tag) |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BSTD1107.FV02 |  | BSTD1107FV02SW01_I | BR4_Cluster1 | BPL131 | DIGITAL | %M1048 | West Turkeys Nest HME Standpipe Flow Valve Local Mode Selected |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BPP1106 |  | BPP1106_FltSL | BR4_Cluster1 | BPL131 | DIGITAL | %M10480 | HME & LME Standpipe Pump 3 Fault Seal |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BPP1106 |  | BPP1106_GrpSttSL | BR4_Cluster1 | BPL131 | DIGITAL | %M10481 | HME & LME Standpipe Pump 3 Group Start Seal |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BPP1106 | Local | BPP1106_Loc | BR4_Cluster1 | BPL131 | DIGITAL | %M10482 | HME & LME Standpipe Pump 3 Mode Local |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BPP1106 |  | BPP1106_LocRunIL | BR4_Cluster1 | BPL131 | DIGITAL | %M10484 | HME & LME Standpipe Pump 3 Local Run Interlock |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BPP1106 |  | BPP1106_LocSttIL | BR4_Cluster1 | BPL131 | DIGITAL | %M10485 | HME & LME Standpipe Pump 3 Local Start Interlock |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BPP1106 |  | BPP1106_NCIL | BR4_Cluster1 | BPL131 | DIGITAL | %M10486 | HME & LME Standpipe Pump 3 Non-Critical Interlock Healthy |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BPP1106 |  | BPP1106_Off | BR4_Cluster1 | BPL131 | DIGITAL | %M10487 | HME & LME Standpipe Pump 3 Stopped |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BPP1106 |  | BPP1106_OOS | BR4_Cluster1 | BPL131 | DIGITAL | %M10488 | HME & LME Standpipe Pump 3 Mode Out of Service |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BSTD1107.FV02 |  | BSTD1107FV02XS01_I | BR4_Cluster1 | BPL131 | DIGITAL | %M1049 | West Turkeys Nest HME Standpipe Flow Valve Fault |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BPP1106 |  | BPP1106_PwrOK | BR4_Cluster1 | BPL131 | DIGITAL | %M10490 | HME & LME Standpipe Pump 3 Overall Power Healthy |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BPP1106 |  | BPP1106_ReSttRqd | BR4_Cluster1 | BPL131 | DIGITAL | %M10491 | HME & LME Standpipe Pump 3 Restart Required |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BPP1106 |  | BPP1106_RstRqd | BR4_Cluster1 | BPL131 | DIGITAL | %M10492 | HME & LME Standpipe Pump 3 Reset Required |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BPP1106 |  | BPP1106_Run | BR4_Cluster1 | BPL131 | DIGITAL | %M10493 | HME & LME Standpipe Pump 3 Running |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BPP1106 |  | BPP1106_SeqReq | BR4_Cluster1 | BPL131 | DIGITAL | %M10496 | HME & LME Standpipe Pump 3 Requested by Pump Station Sequence |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BPP1106 |  | BPP1106_SeqRunIL | BR4_Cluster1 | BPL131 | DIGITAL | %M10497 | HME & LME Standpipe Pump 3 Sequence Run Interlock |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BPP1106 |  | BPP1106_SeqStpIL | BR4_Cluster1 | BPL131 | DIGITAL | %M10498 | HME & LME Standpipe Pump 3 Sequence Stop Interlock |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BPP1106 |  | BPP1106_SeqSttIL | BR4_Cluster1 | BPL131 | DIGITAL | %M10499 | HME & LME Standpipe Pump 3 Sequence Start Interlock |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BSTD1107.FV02.FieldIO.CB01 |  | BSTD1107FV02CB01_I | BR4_Cluster1 | BPL131 | DIGITAL | %M1050 | West Turkeys Nest HME Standpipe 240VAC Flow Valve Power Circuit Breaker Closed |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BPP1106 |  | BPP1106_Stp | BR4_Cluster1 | BPL131 | DIGITAL | %M10500 | HME & LME Standpipe Pump 3 Stopping |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BPP1106 |  | BPP1106_Stt | BR4_Cluster1 | BPL131 | DIGITAL | %M10501 | HME & LME Standpipe Pump 3 Starting |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BPP1106.Sub.CB01 |  | BPP1106CB01_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M10502 | HME & LME Standpipe Pump 3 Main Circuit Breaker (Q103) Open Healthy |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BPP1106.FieldIO.PT01 |  | BPP1106PT01_ChOK | BR4_Cluster1 | BPL131 | DIGITAL | %M10506 | HME & LME Standpipe Pump 3 Pressure (kPa) Channel Healthy |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BPP1106 |  | BPP1106STS1_Iso | BR4_Cluster1 | BPL131 | DIGITAL | %M10507 | HME & LME Standpipe Pump 3 Isolated |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BPP1106 |  | BPP1106STS1_SysOK | BR4_Cluster1 | BPL131 | DIGITAL | %M10508 | HME & LME Standpipe Pump 3 Overall Control System Healthy |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.BTY1502.FV01 |  | BTY1502FV01ZS01_I | BR4_Cluster1 | BPL131 | DIGITAL | %M1051 | West Turkeys Nest Flow Valve Open |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BPP1106 |  | BPP1106THR01_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M10514 | HME & LME Standpipe Pump 3 HME And LME Standpipe Pump 3 (Duty) (K190) Healthy |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BPP1106 |  | BPP1106VDC01_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M10515 | HME & LME Standpipe Pump 3 24VDC Control Supply (Q155) Failure Healthy |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BPP1106.VS01 |  | BPP1106VS01VDC01_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M10518 | BPP1101VS01 VVVF Drive BPP1106VS01 Control Supply (Q219) Failure Healthy |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.BTY1502.FV01 |  | BTY1502FV01ZS02_I | BR4_Cluster1 | BPL131 | DIGITAL | %M1052 | West Turkeys Nest Flow Valve Closed |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.BTY1502.FV01 |  | BTY1502FV01SW01_I | BR4_Cluster1 | BPL131 | DIGITAL | %M1053 | West Turkeys Nest Flow Valve Local Mode Selected |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BPP1107 | Auto | BPP1107_Aut | BR4_Cluster1 | BPL131 | DIGITAL | %M10538 | HME & LME Standpipe Pump 4 Mode Auto |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.BTY1502.FV01 |  | BTY1502FV01XS01_I | BR4_Cluster1 | BPL131 | DIGITAL | %M1054 | West Turkeys Nest Flow Valve Fault |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BPP1107 |  | BPP1107_AutRdy | BR4_Cluster1 | BPL131 | DIGITAL | %M10540 | HME & LME Standpipe Pump 4 Auto Ready |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BPP1107 |  | BPP1107_AutRun | BR4_Cluster1 | BPL131 | DIGITAL | %M10541 | HME & LME Standpipe Pump 4 Auto Running |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BPP1107 |  | BPP1107_AuxStt | BR4_Cluster1 | BPL131 | DIGITAL | %M10542 | HME & LME Standpipe Pump 4 Auxiliary Drive Run Request |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BPP1107 |  | BPP1107_CIL | BR4_Cluster1 | BPL131 | DIGITAL | %M10543 | HME & LME Standpipe Pump 4 Critical Interlock Healthy |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BPP1107 |  | BPP1107_ComOK | BR4_Cluster1 | BPL131 | DIGITAL | %M10544 | HME & LME Standpipe Pump 4 Overall Communications Healthy |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BPP1107 |  | BPP1107_CTS | BR4_Cluster1 | BPL131 | DIGITAL | %M10545 | HME & LME Standpipe Pump 4 Clear and Trial Complete (HMI Tag) |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BPP1107 |  | BPP1107_FltSL | BR4_Cluster1 | BPL131 | DIGITAL | %M10546 | HME & LME Standpipe Pump 4 Fault Seal |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BPP1107 |  | BPP1107_GrpSttSL | BR4_Cluster1 | BPL131 | DIGITAL | %M10547 | HME & LME Standpipe Pump 4 Group Start Seal |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BPP1107 | Local | BPP1107_Loc | BR4_Cluster1 | BPL131 | DIGITAL | %M10548 | HME & LME Standpipe Pump 4 Mode Local |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.BTY1502.FV01.FieldIO.CB01 |  | BTY1502FV01CB01_I | BR4_Cluster1 | BPL131 | DIGITAL | %M1055 | West Turkeys Nest 240VAC Flow Valve Power Circuit Breaker Closed |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BPP1107 |  | BPP1107_LocRunIL | BR4_Cluster1 | BPL131 | DIGITAL | %M10550 | HME & LME Standpipe Pump 4 Local Run Interlock |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BPP1107 |  | BPP1107_LocSttIL | BR4_Cluster1 | BPL131 | DIGITAL | %M10551 | HME & LME Standpipe Pump 4 Local Start Interlock |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BPP1107 |  | BPP1107_NCIL | BR4_Cluster1 | BPL131 | DIGITAL | %M10552 | HME & LME Standpipe Pump 4 Non-Critical Interlock Healthy |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BPP1107 |  | BPP1107_Off | BR4_Cluster1 | BPL131 | DIGITAL | %M10553 | HME & LME Standpipe Pump 4 Stopped |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BPP1107 |  | BPP1107_OOS | BR4_Cluster1 | BPL131 | DIGITAL | %M10554 | HME & LME Standpipe Pump 4 Mode Out of Service |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BPP1107 |  | BPP1107_PwrOK | BR4_Cluster1 | BPL131 | DIGITAL | %M10556 | HME & LME Standpipe Pump 4 Overall Power Healthy |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BPP1107 |  | BPP1107_ReSttRqd | BR4_Cluster1 | BPL131 | DIGITAL | %M10557 | HME & LME Standpipe Pump 4 Restart Required |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BPP1107 |  | BPP1107_RstRqd | BR4_Cluster1 | BPL131 | DIGITAL | %M10558 | HME & LME Standpipe Pump 4 Reset Required |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BPP1107 |  | BPP1107_Run | BR4_Cluster1 | BPL131 | DIGITAL | %M10559 | HME & LME Standpipe Pump 4 Running |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop03 |  | BTY1502DX03CB01_I | BR4_Cluster1 | BPL131 | DIGITAL | %M1056 | West Turkeys Nest DIO Box 3 240VAC Circuit Breaker (Q106) Closed |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BPP1107 |  | BPP1107_SeqReq | BR4_Cluster1 | BPL131 | DIGITAL | %M10562 | HME & LME Standpipe Pump 4 Requested by Pump Station Sequence |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BPP1107 |  | BPP1107_SeqRunIL | BR4_Cluster1 | BPL131 | DIGITAL | %M10563 | HME & LME Standpipe Pump 4 Sequence Run Interlock |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BPP1107 |  | BPP1107_SeqStpIL | BR4_Cluster1 | BPL131 | DIGITAL | %M10564 | HME & LME Standpipe Pump 4 Sequence Stop Interlock |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BPP1107 |  | BPP1107_SeqSttIL | BR4_Cluster1 | BPL131 | DIGITAL | %M10565 | HME & LME Standpipe Pump 4 Sequence Start Interlock |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BPP1107 |  | BPP1107_Stp | BR4_Cluster1 | BPL131 | DIGITAL | %M10566 | HME & LME Standpipe Pump 4 Stopping |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BPP1107 |  | BPP1107_Stt | BR4_Cluster1 | BPL131 | DIGITAL | %M10567 | HME & LME Standpipe Pump 4 Starting |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BPP1107.Sub.CB01 |  | BPP1107CB01_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M10568 | HME & LME Standpipe Pump 4 Main Circuit Breaker (Q103) Open Healthy |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop03 |  | BTY1502DX03VDC01_I | BR4_Cluster1 | BPL131 | DIGITAL | %M1057 | West Turkeys Nest DIO Box 3 24VDC Output Control Supply (Q143) Healthy |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BPP1107.FieldIO.PT02 |  | BPP1107PT02_ChOK | BR4_Cluster1 | BPL131 | DIGITAL | %M10572 | HME & LME Standpipe Pump 4 Pressure (kPa) Channel Healthy |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BPP1107 |  | BPP1107STS1_Iso | BR4_Cluster1 | BPL131 | DIGITAL | %M10573 | HME & LME Standpipe Pump 4 Isolated |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BPP1107 |  | BPP1107STS1_SysOK | BR4_Cluster1 | BPL131 | DIGITAL | %M10574 | HME & LME Standpipe Pump 4 Overall Control System Healthy |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop03 |  | BTY1502DX03VDC02_I | BR4_Cluster1 | BPL131 | DIGITAL | %M1058 | West Turkeys Nest DIO Box 3 24VDC GW1 Control Supply (Q157) Healthy |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BPP1107 |  | BPP1107THR01_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M10580 | HME & LME Standpipe Pump 4 HME And LME Standpipe Pump 4 (Standby) (K190) Healthy |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BPP1107 |  | BPP1107VDC01_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M10581 | HME & LME Standpipe Pump 4 24VDC Control Supply (Q155) Failure Healthy |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BPP1107.VS01 |  | BPP1107VS01VDC01_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M10584 | BPP1101VS01 VVVF Drive BPP1107VS01 Control Supply (Q222) Failure Healthy |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop03 |  | BTY1502DX03VDC03_I | BR4_Cluster1 | BPL131 | DIGITAL | %M1059 | West Turkeys Nest DIO Box 3 24VDC Instrument Control Supply (Q164) Healthy |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop03 |  | BTY1502DX03VDC04_I | BR4_Cluster1 | BPL131 | DIGITAL | %M1060 | West Turkeys Nest DIO Box 3 24VDC Transmitter Control Supply (Q168) Healthy |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.P3FIREWATER.BPQE2101.Sub.DB01.CB01 |  | BPQE2101DB01CB01_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M10604 | NPI & Primary Crusher Fire Water Pump Dist Board Main Circuit Breaker (Q103) Open Healthy |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.P3FIREWATER.BPQE2101.Sub.DB01.CB01 |  | BPQE2101DB01TRP01_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M10605 | NPI & Primary Crusher Fire Water Pump Dist Board Main Circuit Breaker Trip Healthy |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.P3FIREWATER.BPQE2101.Sub.DB01 |  | BPQE2101DB01VDC01_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M10606 | NPI & Primary Crusher Fire Water Pump Dist Board 24VDC Control Supply (Q155) Failure Healthy |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.P3FIREWATER.BPQE2101.Sub.PN01 |  | BPQE2101PN01VDC01_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M10609 | NPI & Primary Crushing Fire Water Container Panel 24VDC Control Supply (Q155) Failure Healthy |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop03 |  | BTY1502DX03VDC05_I | BR4_Cluster1 | BPL131 | DIGITAL | %M1061 | West Turkeys Nest DIO Box 3 24VDC BTY1502DX03 Field Control Supply (Q172) Healthy |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.P3POTWATER.BPQE2115.Sub.DB01 |  | BPQE2115MC01VDC01_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M10612 | Potable Water MCC 24VDC Control Supply (PWTP) (Q155) Failure Healthy |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.AC01.CB01 |  | BSR131AC01CB01_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M10613 | BSR131 Aircon 1 Main Circuit Breaker (Q103) Open Healthy |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.AC01.CB01 |  | BSR131AC01TRP01_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M10614 | BSR131 Aircon 1 Main Circuit Breaker Trip Healthy |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.AC01 |  | BSR131AC01VDC01_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M10615 | BSR131 Aircon 1 24VDC Control Supply (Q155) Failure Healthy |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.AC02.CB01 |  | BSR131AC02CB01_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M10617 | BSR131 Aircon 2 Main Circuit Breaker (Q103) Open Healthy |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.AC02.CB01 |  | BSR131AC02TRP01_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M10618 | BSR131 Aircon 2 Main Circuit Breaker Trip Healthy |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.AC02 |  | BSR131AC02VDC01_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M10619 | BSR131 Aircon 2 24VDC Control Supply (Q155) Failure Healthy |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop03 |  | BTY1502DX03VDC06_I | BR4_Cluster1 | BPL131 | DIGITAL | %M1062 | West Turkeys Nest DIO Box 3 24VDC BPP1103 Field Control Supply (Q176) Healthy |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.BC01.CB01 |  | BSR131BC01TRP01_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M10627 | BSR131 Battery Charger 1 Main Circuit Breaker Trip Healthy |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop03 |  | BTY1502DX03VDC07_I | BR4_Cluster1 | BPL131 | DIGITAL | %M1063 | West Turkeys Nest DIO Box 3 24VDC BPP1104 Field Control Supply (Q180) Healthy |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.BC01.CB01 |  | BSR131BC01CB01_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M10636 | BSR131 Battery Charger 1 Main Circuit Breaker (Q103) Open Healthy |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.BC01 |  | BSR131BC01VDC01_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M10638 | BSR131 Battery Charger 1 24VDC Control Supply (Q155) Failure Healthy |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.BC02.BACS |  | BSR131BC02_BACS_LnkOK | BR4_Cluster1 | BPL131 | DIGITAL | %M10639 | BSR131 Battery Charger 2 BACS Link Ok |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop03 |  | BTY1502DX03VDC08_I | BR4_Cluster1 | BPL131 | DIGITAL | %M1064 | West Turkeys Nest DIO Box 3 24VDC BPP1105 Field Control Supply (Q184) Healthy |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.BC02.BACS |  | BSR131BC02_BACSComFlt | BR4_Cluster1 | BPL131 | DIGITAL | %M10640 | BSR131 Battery Charger 2 BACS Comms Fault |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.BC02.BACS |  | BSR131BC02_BACSFlt | BR4_Cluster1 | BPL131 | DIGITAL | %M10641 | BSR131 Battery Charger 2 BACS Fault |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.BC02.BACS |  | BSR131BC02_BACSOK | BR4_Cluster1 | BPL131 | DIGITAL | %M10642 | BSR131 Battery Charger 2 BACS Ok |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.BC02.Cordex |  | BSR131BC02_CordexFlt | BR4_Cluster1 | BPL131 | DIGITAL | %M10646 | BSR131 Battery Charger 2 Codrex Fault |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.BC02.Cordex |  | BSR131BC02_CordexOK | BR4_Cluster1 | BPL131 | DIGITAL | %M10647 | BSR131 Battery Charger 2 Cordex Ok |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.BC02.CB01 |  | BSR131BC02TRP01_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M10648 | BSR131 Battery Charger 2 Main Circuit Breaker Trip Healthy |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop03 |  | BTY1502DX03VDC09_I | BR4_Cluster1 | BPL131 | DIGITAL | %M1065 | West Turkeys Nest DIO Box 3 24VDC Spare Control Supply (Q188) Healthy |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.BC02 |  | BSR131BC02_PwrUp | BR4_Cluster1 | BPL131 | DIGITAL | %M10652 | BSR131 Battery Charger 2 Power Up |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.BC02.CB01 |  | BSR131BC02CB01_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M10654 | BSR131 Battery Charger 2 Main Circuit Breaker (Q103) Open Healthy |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.BC02 |  | BSR131BC02CB02_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M10655 | BSR131 Battery Charger 2 BMC131INC01 110VDC INC01 Tripping Supply Circuit Breaker (Q114) Open Healthy |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.BC02 |  | BSR131BC02CB03_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M10656 | BSR131 Battery Charger 2 BMC131INC02 110VDC INC02 Tripping Supply Circuit Breaker (Q117) Open Healthy |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.BC02 |  | BSR131BC02CB04_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M10657 | BSR131 Battery Charger 2 BMC131INC03 110VDC INC03 Tripping Supply Circuit Breaker (Q120) Open Healthy |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.BC02 |  | BSR131BC02CB05_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M10658 | BSR131 Battery Charger 2 RSP01 110VDC Tripping Supply Circuit Breaker (Q123) Open Healthy |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop03 |  | BTY1502DX03VDC10_I | BR4_Cluster1 | BPL131 | DIGITAL | %M1066 | West Turkeys Nest DIO Box 3 24VDC Spare Control Supply (Q192) Healthy |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.BC02 |  | BSR131BC02VDC01_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M10667 | BSR131 Battery Charger 2 24VDC Control Supply (Q155) Failure Healthy |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.BC02 |  | BSR131BC02VDC02_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M10668 | BSR131 Battery Charger 2 Battery Charger 110VDC Tripping Supply (K112) Failure Healthy |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.DB01.CB01 |  | BSR131DB01CB01_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M10669 | BSR131 LSP Dist Board Main Circuit Breaker (Q103) Open Healthy |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop03 |  | BTY1502DX03VDC11_I | BR4_Cluster1 | BPL131 | DIGITAL | %M1067 | West Turkeys Nest DIO Box 3 24VDC Spare Control Supply (Q196) Healthy |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.DB01.CB01 |  | BSR131DB01TRP01_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M10670 | BSR131 LSP Dist Board Main Circuit Breaker Trip Healthy |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.DB01 |  | BSR131DB01VDC01_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M10671 | BSR131 LSP Dist Board 24VDC Control Supply (Q155) Failure Healthy |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.DB02.CB01 |  | BSR131DB02CB01_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M10672 | BSR131 415V Dewatering Laydown Lighting Dist Board Main Circuit Breaker (Q103) Open Healthy |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.DB02.CB01 |  | BSR131DB02TRP01_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M10673 | BSR131 415V Dewatering Laydown Lighting Dist Board Main Circuit Breaker Trip Healthy |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.DB02 |  | BSR131DB02VDC01_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M10674 | BSR131 415V Dewatering Laydown Lighting Dist Board 24VDC Control Supply (Q155) Failure Healthy |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.DB03.CB01 |  | BSR131DB03CB01_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M10675 | BSR131 415V HME Refuel Water Recycle Dist Board Main Circuit Breaker (Q103) Open Healthy |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.DB03.CB01 |  | BSR131DB03TRP01_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M10676 | BSR131 415V HME Refuel Water Recycle Dist Board Main Circuit Breaker Trip Healthy |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.DB03 |  | BSR131DB03VDC01_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M10677 | BSR131 415V HME Refuel Water Recycle Dist Board 24VDC Control Supply (Q155) Failure Healthy |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop01 |  | BSR131DX01_PwrOK | BR4_Cluster1 | BPL131 | DIGITAL | %M10678 | BSR131 DIO Box 1 Power Healthy Status |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop01 |  | BSR131DX01DIO1PLM0_ComFlt_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M10679 | BSR131DX01 CRA Comms Module 0 Communications Fault Healthy |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop01 |  | BSR131DX01DIO1PLM0_Flt_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M10680 | BSR131DX01 CRA Comms Module 0 Fault Healthy |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop01 |  | BSR131DX01DIO1PLM0_LnkOK | BR4_Cluster1 | BPL131 | DIGITAL | %M10681 | BSR131DX01 CRA Comms Module 0 Link Healthy |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop01 |  | BSR131DX01DIO1PLM0_OK | BR4_Cluster1 | BPL131 | DIGITAL | %M10682 | BSR131DX01 CRA Comms Module 0 Data Healthy |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop01 |  | BSR131DX01DIO1PLM1_Flt_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M10683 | BSR131DX01 DI Module 1 Fault Healthy |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop01 |  | BSR131DX01DIO1PLM1_Grp1Flt_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M10684 | BSR131DX01 DI Module 1 Group 1 Fault Healthy |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop01 |  | BSR131DX01DIO1PLM1_Grp1OK | BR4_Cluster1 | BPL131 | DIGITAL | %M10685 | BSR131DX01 DI Module 1 Group 1 (00-15) Healthy |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop01 |  | BSR131DX01DIO1PLM1_Grp2Flt_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M10686 | BSR131DX01 DI Module 1 Group 2 Fault Healthy |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop01 |  | BSR131DX01DIO1PLM1_Grp2OK | BR4_Cluster1 | BPL131 | DIGITAL | %M10687 | BSR131DX01 DI Module 1 Group 2 (16-31) Healthy |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop01 |  | BSR131DX01DIO1PLM1_OK | BR4_Cluster1 | BPL131 | DIGITAL | %M10688 | BSR131DX01 DI Module 1 Data Valid |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop01 |  | BSR131DX01DIO1PLM2_Flt_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M10689 | BSR131DX01 DI Module 2 Fault Healthy |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop01 |  | BSR131DX01DIO1PLM2_Grp1Flt_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M10690 | BSR131DX01 DI Module 2 Group 1 Fault Healthy |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop01 |  | BSR131DX01DIO1PLM2_Grp1OK | BR4_Cluster1 | BPL131 | DIGITAL | %M10691 | BSR131DX01 DI Module 2 Group 1 (00-15) Healthy |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop01 |  | BSR131DX01DIO1PLM2_Grp2Flt_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M10692 | BSR131DX01 DI Module 2 Group 2 Fault Healthy |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop01 |  | BSR131DX01DIO1PLM2_Grp2OK | BR4_Cluster1 | BPL131 | DIGITAL | %M10693 | BSR131DX01 DI Module 2 Group 2 (16-31) Healthy |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop01 |  | BSR131DX01DIO1PLM2_OK | BR4_Cluster1 | BPL131 | DIGITAL | %M10694 | BSR131DX01 DI Module 2 Data Valid |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop01 |  | BSR131DX01DIO1PLM3_Flt_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M10695 | BSR131DX01 DI Module 3 Fault Healthy |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop01 |  | BSR131DX01DIO1PLM3_Grp1Flt_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M10696 | BSR131DX01 DI Module 3 Group 1 Fault Healthy |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop01 |  | BSR131DX01DIO1PLM3_Grp1OK | BR4_Cluster1 | BPL131 | DIGITAL | %M10697 | BSR131DX01 DI Module 3 Group 1 (00-15) Healthy |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop01 |  | BSR131DX01DIO1PLM3_Grp2Flt_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M10698 | BSR131DX01 DI Module 3 Group 2 Fault Healthy |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop01 |  | BSR131DX01DIO1PLM3_Grp2OK | BR4_Cluster1 | BPL131 | DIGITAL | %M10699 | BSR131DX01 DI Module 3 Group 2 (16-31) Healthy |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop01 |  | BSR131DX01DIO1PLM3_OK | BR4_Cluster1 | BPL131 | DIGITAL | %M10700 | BSR131DX01 DI Module 3 Data Valid |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop01 |  | BSR131DX01DIO1PLM4_Flt_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M10701 | BSR131DX01 DI Module 4 Fault Healthy |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop01 |  | BSR131DX01DIO1PLM4_Grp1Flt_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M10702 | BSR131DX01 DI Module 4 Group 1 Fault Healthy |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop01 |  | BSR131DX01DIO1PLM4_Grp1OK | BR4_Cluster1 | BPL131 | DIGITAL | %M10703 | BSR131DX01 DI Module 4 Group 1 (00-15) Healthy |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop01 |  | BSR131DX01DIO1PLM4_Grp2Flt_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M10704 | BSR131DX01 DI Module 4 Group 2 Fault Healthy |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop01 |  | BSR131DX01DIO1PLM4_Grp2OK | BR4_Cluster1 | BPL131 | DIGITAL | %M10705 | BSR131DX01 DI Module 4 Group 2 (16-31) Healthy |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop01 |  | BSR131DX01DIO1PLM4_OK | BR4_Cluster1 | BPL131 | DIGITAL | %M10706 | BSR131DX01 DI Module 4 Data Valid |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop01 |  | BSR131DX01DIO1PLM5_Flt_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M10707 | BSR131DX01 DI Module 5 Fault Healthy |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop01 |  | BSR131DX01DIO1PLM5_Grp1Flt_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M10708 | BSR131DX01 DI Module 5 Group 1 Fault Healthy |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop01 |  | BSR131DX01DIO1PLM5_Grp1OK | BR4_Cluster1 | BPL131 | DIGITAL | %M10709 | BSR131DX01 DI Module 5 Group 1 (00-15) Healthy |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop01 |  | BSR131DX01DIO1PLM5_Grp2Flt_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M10710 | BSR131DX01 DI Module 5 Group 2 Fault Healthy |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop01 |  | BSR131DX01DIO1PLM5_Grp2OK | BR4_Cluster1 | BPL131 | DIGITAL | %M10711 | BSR131DX01 DI Module 5 Group 2 (16-31) Healthy |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop01 |  | BSR131DX01DIO1PLM5_OK | BR4_Cluster1 | BPL131 | DIGITAL | %M10712 | BSR131DX01 DI Module 5 Data Valid |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop01 |  | BSR131DX01DIO1PLM6_Flt_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M10713 | BSR131DX01 DI Module 6 Fault Healthy |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop01 |  | BSR131DX01DIO1PLM6_Grp1Flt_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M10714 | BSR131DX01 DI Module 6 Group 1 Fault Healthy |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop01 |  | BSR131DX01DIO1PLM6_Grp1OK | BR4_Cluster1 | BPL131 | DIGITAL | %M10715 | BSR131DX01 DI Module 6 Group 1 (00-15) Healthy |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop01 |  | BSR131DX01DIO1PLM6_Grp2Flt_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M10716 | BSR131DX01 DI Module 6 Group 2 Fault Healthy |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop01 |  | BSR131DX01DIO1PLM6_Grp2OK | BR4_Cluster1 | BPL131 | DIGITAL | %M10717 | BSR131DX01 DI Module 6 Group 2 (16-31) Healthy |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop01 |  | BSR131DX01DIO1PLM6_OK | BR4_Cluster1 | BPL131 | DIGITAL | %M10718 | BSR131DX01 DI Module 6 Data Valid |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop01 |  | BSR131DX01DIO1PLM7_Flt_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M10719 | BSR131DX01 DI Module 7 Fault Healthy |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop01 |  | BSR131DX01DIO1PLM7_Grp1Flt_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M10720 | BSR131DX01 DI Module 7 Group 1 Fault Healthy |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop01 |  | BSR131DX01DIO1PLM7_Grp1OK | BR4_Cluster1 | BPL131 | DIGITAL | %M10721 | BSR131DX01 DI Module 7 Group 1 (00-15) Healthy |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop01 |  | BSR131DX01DIO1PLM7_Grp2Flt_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M10722 | BSR131DX01 DI Module 7 Group 2 Fault Healthy |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop01 |  | BSR131DX01DIO1PLM7_Grp2OK | BR4_Cluster1 | BPL131 | DIGITAL | %M10723 | BSR131DX01 DI Module 7 Group 2 (16-31) Healthy |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop01 |  | BSR131DX01DIO1PLM7_OK | BR4_Cluster1 | BPL131 | DIGITAL | %M10724 | BSR131DX01 DI Module 7 Data Valid |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop01 |  | BSR131DX01DIO1PLM8_Flt_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M10725 | BSR131DX01 DO Module 8 Fault Healthy |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop01 |  | BSR131DX01DIO1PLM8_OK | BR4_Cluster1 | BPL131 | DIGITAL | %M10726 | BSR131DX01 DO Module 8 Data Valid |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop01 |  | BSR131DX01VDC01_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M10727 | BSR131 DIO Box 1 DX01 24VDC Control Supply Healthy (Q110) Failure Healthy |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop01 |  | BSR131DX01VDC02_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M10728 | BSR131 DIO Box 1 DX01 24VDC Output Module Control Supply (Q170) Failure Healthy |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.UP01 |  | BSR131DX01VDC03_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M10729 | BSR131 DIO Box 1 BSR131UP01 24VDC Control Supply (Q254) Failure Healthy |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.BC01 |  | BSR131DX01VDC04_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M10730 | BSR131 DIO Box 1 BSR131BC01DB01 24VDC Control Supply (Q257) Failure Healthy |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.BC02 |  | BSR131DX01VDC05_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M10731 | BSR131 DIO Box 1 BSR131BC02DB01 24VDC Control Supply (Q260) Failure Healthy |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.DB01 |  | BSR131DX01VDC06_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M10732 | BSR131 DIO Box 1 BSR131UP01DB01 24VDC Control Supply (Q263) Failure Healthy |  |  | BS1_Tags
BR4.SRV.PWR.BSR131 |  | BSR131DX01VDC07_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M10733 | BSR131 DIO Box 1 Misc Switchroom Alarms 24VDC Control Supply (Q266) Failure Healthy |  |  | BS1_Tags
BR4.SRV.PWR.BSR131 |  | BSR131FIP01IS01_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M10739 | BSR131 Fire Panel Fire Panel Isolated Open Healthy |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1103 |  | BPP1103THR01_I | BR4_Cluster1 | BPL131 | DIGITAL | %M1074 | Water Transfer Pump 1 Thermistor Relay (K190) Healthy |  |  | BS1_Tags
BR4.SRV.PWR.BSR131 |  | BSR131FIP01XS01_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M10740 | BSR131 Fire Panel Fault Healthy |  |  | BS1_Tags
BR4.SRV.PWR.BSR131 |  | BSR131FIP01XS02_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M10741 | BSR131 Fire Panel Alarm Healthy |  |  | BS1_Tags
BR4.SRV.PWR.BSR131 |  | BSR131FIP01XS03_A | BR4_Cluster1 | BPL131 | DIGITAL | %M10742 | BSR131 Fire Panel Gas Discharged Alarm |  |  | BS1_Tags
BR4.SRV.PWR.BSR131 |  | BSR131FIP01XS03_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M10743 | BSR131 Fire Panel Gas Discharged Healthy |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.NEP01 |  | BSR131NEP01CB01_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M10744 | BSR131 Network Panel 1 NEP Primary PDU Circuit Breaker (Q130) Open Healthy |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.NEP01 |  | BSR131NEP01CB02_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M10745 | BSR131 Network Panel 1 NEP Secondary PDU Circuit Breaker (Q180) Open Healthy |  |  | BS1_Tags
BR4.SRV.PWR.BSR131 |  | BSR131PB01_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M10746 | NPI Hub Substation Shutdown Pushbutton (SESP) Activated Healthy |  |  | BS1_Tags
BR4.SRV.PWR.BSR131 |  | BSR131PN01TS01_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M10747 | Switchroom Control Panel Airlock High Temperature Healthy |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1104 |  | BPP1104THR01_I | BR4_Cluster1 | BPL131 | DIGITAL | %M1075 | Water Transfer Pump 2 Thermistor Relay (K190) Healthy |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS |  | BSR131UP01_BACSComFlt | BR4_Cluster1 | BPL131 | DIGITAL | %M10751 | BSR131 UPS BACS Comms Fault |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS |  | BSR131UP01_BACSFlt | BR4_Cluster1 | BPL131 | DIGITAL | %M10752 | BSR131 UPS BACS Fault |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS |  | BSR131UP01_BACSOK | BR4_Cluster1 | BPL131 | DIGITAL | %M10754 | BSR131 UPS BACS Ok |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS |  | BSR131UP01_BACSSysOK | BR4_Cluster1 | BPL131 | DIGITAL | %M10756 | BSR131 UPS BACS System Ok |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.UP01 |  | BSR131UP01_ComFlt | BR4_Cluster1 | BPL131 | DIGITAL | %M10757 | BSR131 UPS Communications Fault |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.UP01 |  | BSR131UP01_ComFlt_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M10758 | BSR131 UPS Communications Fault Healthy |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.UPScale | DatOK | BSR131UP01_DatOK | BR4_Cluster1 | BPL131 | DIGITAL | %M10759 | BSR131UP01 Data Valid |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1105 |  | BPP1105THR01_I | BR4_Cluster1 | BPL131 | DIGITAL | %M1076 | Water Transfer Pump 3 Thermistor Relay (K190) Healthy |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.UP01 |  | BSR131UP01_Flt | BR4_Cluster1 | BPL131 | DIGITAL | %M10760 | BSR131 UPS System Fault |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.UP01 |  | BSR131UP01_Flt_A | BR4_Cluster1 | BPL131 | DIGITAL | %M10761 | BSR131 UPS System Fault Alarm Alarm |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.UP01 |  | BSR131UP01_Flt_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M10762 | BSR131 UPS System Fault Healthy |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.UP01 |  | BSR131UP01_LnkOK | BR4_Cluster1 | BPL131 | DIGITAL | %M10763 | BSR131 UPS Link OK |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.UP01 |  | BSR131UP01_OK | BR4_Cluster1 | BPL131 | DIGITAL | %M10764 | BSR131 UPS Unit Healthy |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.UP01 |  | BSR131UP01_PwrUp | BR4_Cluster1 | BPL131 | DIGITAL | %M10765 | BSR131 UPS Power Up |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.UP01 |  | BSR131UP01_UPSByp | BR4_Cluster1 | BPL131 | DIGITAL | %M10767 | BSR131 UPS Bypassed |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.UP01 |  | BSR131UP01_UPSComFlt | BR4_Cluster1 | BPL131 | DIGITAL | %M10768 | BSR131 UPS Comms Fault |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.UP01 |  | BSR131UP01_UPSFlt | BR4_Cluster1 | BPL131 | DIGITAL | %M10769 | BSR131 UPS System Fault |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1103.FieldIO.FT03 |  | BPP1103FQ03_I | BR4_Cluster1 | BPL131 | DIGITAL | %M1077 | Water Transfer Pump 1 Flow Totaliser Pulse |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.UP01 |  | BSR131UP01_UPSOK | BR4_Cluster1 | BPL131 | DIGITAL | %M10770 | BSR131 UPS UPS Healthy |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.UP01 |  | BSR131UP01_UPSOPHi | BR4_Cluster1 | BPL131 | DIGITAL | %M10771 | BSR131 UPS Output Overload |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.UP01 |  | BSR131UP01_UPSSysOff | BR4_Cluster1 | BPL131 | DIGITAL | %M10772 | BSR131 UPS System Off |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.UP01 |  | BSR131UP01_UPSSysOK | BR4_Cluster1 | BPL131 | DIGITAL | %M10773 | BSR131 UPS System OK |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.CB01 |  | BSR131UP01CB01_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M10774 | BSR131 UPS Main Circuit Breaker (Q103) Open Healthy |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.UP01 |  | BSR131UP01VDC01_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M10777 | BSR131 UPS 24VDC Control Supply (Q155) Failure Healthy |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.UP01 |  | BSR131UP01ZS01_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M10778 | BSR131 UPS UPS in Normal Mode Healthy |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1104.FieldIO.FT04 |  | BPP1104FQ04_I | BR4_Cluster1 | BPL131 | DIGITAL | %M1078 | Water Transfer Pump 2 Flow Totaliser Pulse |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BSTD1106 |  | BSTD1106FIC01_Aut | BR4_Cluster1 | BPL131 | DIGITAL | %M10781 | West Turkeys Nest LME Standpipe Flow Controller Auto Mode |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BSTD1106 |  | BSTD1106FIC01_AutEn | BR4_Cluster1 | BPL131 | DIGITAL | %M10782 | West Turkeys Nest LME Standpipe Flow Controller Auto Enabled |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BSTD1106 |  | BSTD1106FIC01_Man | BR4_Cluster1 | BPL131 | DIGITAL | %M10784 | West Turkeys Nest LME Standpipe Flow Controller Manual Mode |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BSTD1106.FieldIO.FT03 |  | BSTD1106FT03_ChOK | BR4_Cluster1 | BPL131 | DIGITAL | %M10785 | West Turkeys Nest LME Standpipe Flow Rate (m3/h) Channel Healthy |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BSTD1106.FV03 |  | BSTD1106FV03_AlmAck | BR4_Cluster1 | BPL131 | DIGITAL | %M10786 | BSTD1106FV03 West Turkeys Nest LME Standpipe Valve Alarm Acknowledge |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BSTD1106.FV03 |  | BSTD1106FV03_AlmEn | BR4_Cluster1 | BPL131 | DIGITAL | %M10787 | West Turkeys Nest LME Standpipe Valve Alarm Enable |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BSTD1106.FV03 | Auto | BSTD1106FV03_Aut | BR4_Cluster1 | BPL131 | DIGITAL | %M10788 | West Turkeys Nest LME Standpipe Valve Mode Auto |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BSTD1106.FV03 |  | BSTD1106FV03_AutRdy | BR4_Cluster1 | BPL131 | DIGITAL | %M10789 | West Turkeys Nest LME Standpipe Valve Auto Ready |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1105.FieldIO.FT05 |  | BPP1105FQ05_I | BR4_Cluster1 | BPL131 | DIGITAL | %M1079 | Water Transfer Pump 3 Flow Totaliser Pulse |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BSTD1106.FV03 |  | BSTD1106FV03_CIL | BR4_Cluster1 | BPL131 | DIGITAL | %M10790 | West Turkeys Nest LME Standpipe Valve Critical Interlock Healthy |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BSTD1106.FV03 |  | BSTD1106FV03_Cls | BR4_Cluster1 | BPL131 | DIGITAL | %M10791 | West Turkeys Nest LME Standpipe Valve Close Command |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BSTD1106.FV03 |  | BSTD1106FV03_Clsd | BR4_Cluster1 | BPL131 | DIGITAL | %M10792 | West Turkeys Nest LME Standpipe Valve Closed |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BSTD1106.FV03 |  | BSTD1106FV03_Clsg | BR4_Cluster1 | BPL131 | DIGITAL | %M10793 | West Turkeys Nest LME Standpipe Valve Closing |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BSTD1106.FV03 |  | BSTD1106FV03_ComOK | BR4_Cluster1 | BPL131 | DIGITAL | %M10794 | West Turkeys Nest LME Standpipe Valve Overall Comms Healthy |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BSTD1106.FV03 |  | BSTD1106FV03_ExcRun_A | BR4_Cluster1 | BPL131 | DIGITAL | %M10795 | West Turkeys Nest LME Standpipe Valve Excessive Open Alarm |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BSTD1106.FV03 |  | BSTD1106FV03_ExcRun_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M10796 | West Turkeys Nest LME Standpipe Valve Excessive Open Time Fault Healthy |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BSTD1106.FV03 |  | BSTD1106FV03_FltSL | BR4_Cluster1 | BPL131 | DIGITAL | %M10797 | West Turkeys Nest LME Standpipe Valve Fault Seal |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BSTD1106.FV03 |  | BSTD1106FV03_FTC | BR4_Cluster1 | BPL131 | DIGITAL | %M10798 | West Turkeys Nest LME Standpipe Valve Fail to Close |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BSTD1106.FV03 |  | BSTD1106FV03_FTC_A | BR4_Cluster1 | BPL131 | DIGITAL | %M10799 | West Turkeys Nest LME Standpipe Valve Fail to Close Alarm |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1103.FieldIO.FT06 |  | BPP1103FQ06_I | BR4_Cluster1 | BPL131 | DIGITAL | %M1080 | Water Transfer Pump 1 Flow Totaliser Pulse |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BSTD1106.FV03 |  | BSTD1106FV03_FTC_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M10800 | West Turkeys Nest LME Standpipe Valve Fail to Close Fault Healthy |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BSTD1106.FV03 |  | BSTD1106FV03_FTO | BR4_Cluster1 | BPL131 | DIGITAL | %M10801 | West Turkeys Nest LME Standpipe Valve Fail to Open |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BSTD1106.FV03 |  | BSTD1106FV03_FTO_A | BR4_Cluster1 | BPL131 | DIGITAL | %M10802 | West Turkeys Nest LME Standpipe Valve Fail to Open Alarm |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BSTD1106.FV03 |  | BSTD1106FV03_FTO_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M10803 | West Turkeys Nest LME Standpipe Valve Fail to Open Fault Healthy |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BSTD1106.FV03 |  | BSTD1106FV03_LmtFlt | BR4_Cluster1 | BPL131 | DIGITAL | %M10804 | West Turkeys Nest LME Standpipe Valve Position Fault |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BSTD1106.FV03 |  | BSTD1106FV03_LmtFlt_A | BR4_Cluster1 | BPL131 | DIGITAL | %M10805 | West Turkeys Nest LME Standpipe Valve Dual Limit Alarm |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BSTD1106.FV03 |  | BSTD1106FV03_LmtFlt_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M10806 | West Turkeys Nest LME Standpipe Valve Dual Limit Fault Healthy |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BSTD1106.FV03 | Local | BSTD1106FV03_Loc | BR4_Cluster1 | BPL131 | DIGITAL | %M10807 | West Turkeys Nest LME Standpipe Valve Mode Local |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BSTD1106.FV03 |  | BSTD1106FV03_LocClsReq | BR4_Cluster1 | BPL131 | DIGITAL | %M10808 | West Turkeys Nest LME Standpipe Valve Local Close Requested |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BSTD1106.FV03 |  | BSTD1106FV03_LocOpnReq | BR4_Cluster1 | BPL131 | DIGITAL | %M10809 | West Turkeys Nest LME Standpipe Valve Local Open Requested |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop04 |  | BTK2101DX04CB01_I | BR4_Cluster1 | BPL131 | DIGITAL | %M1081 | NPI Fire Water Tank DIO Box 1 240VAC Circuit Breaker (Q106) Closed |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BSTD1106.FV03 |  | BSTD1106FV03_Man | BR4_Cluster1 | BPL131 | DIGITAL | %M10810 | West Turkeys Nest LME Standpipe Valve Mode Manual |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BSTD1106.FV03 |  | BSTD1106FV03_NCIL | BR4_Cluster1 | BPL131 | DIGITAL | %M10811 | West Turkeys Nest LME Standpipe Valve Non-Critical Interlock Healthy |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BSTD1106.FV03 |  | BSTD1106FV03_NCILAlmEn | BR4_Cluster1 | BPL131 | DIGITAL | %M10812 | West Turkeys Nest LME Standpipe Valve NCIL Alarm Enable |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BSTD1106.FV03 |  | BSTD1106FV03_OOS | BR4_Cluster1 | BPL131 | DIGITAL | %M10813 | West Turkeys Nest LME Standpipe Valve Mode Out of Service |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BSTD1106.FV03 |  | BSTD1106FV03_Opn | BR4_Cluster1 | BPL131 | DIGITAL | %M10814 | West Turkeys Nest LME Standpipe Valve Open Command |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BSTD1106.FV03 |  | BSTD1106FV03_Opnd | BR4_Cluster1 | BPL131 | DIGITAL | %M10815 | West Turkeys Nest LME Standpipe Valve Opened |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BSTD1106.FV03 |  | BSTD1106FV03_Opng | BR4_Cluster1 | BPL131 | DIGITAL | %M10816 | West Turkeys Nest LME Standpipe Valve Opening |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BSTD1106.FV03 |  | BSTD1106FV03_PwrOK | BR4_Cluster1 | BPL131 | DIGITAL | %M10817 | West Turkeys Nest LME Standpipe Valve Overall Power Healthy |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BSTD1106.FV03 |  | BSTD1106FV03_RstRqd | BR4_Cluster1 | BPL131 | DIGITAL | %M10818 | West Turkeys Nest LME Standpipe Valve Reset Required |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BSTD1106.FV03 |  | BSTD1106FV03_SeqCls | BR4_Cluster1 | BPL131 | DIGITAL | %M10819 | West Turkeys Nest LME Standpipe Valve Sequence Close |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop04 |  | BTK2101DX04VDC01_I | BR4_Cluster1 | BPL131 | DIGITAL | %M1082 | NPI Fire Water Tank DIO Box 1 24VDC Output Control Supply (Q143) Healthy |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BSTD1106.FV03 |  | BSTD1106FV03_SeqClsSttIL | BR4_Cluster1 | BPL131 | DIGITAL | %M10820 | West Turkeys Nest LME Standpipe Valve Sequence Close Interlock |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BSTD1106.FV03 |  | BSTD1106FV03_SeqOpn | BR4_Cluster1 | BPL131 | DIGITAL | %M10821 | West Turkeys Nest LME Standpipe Valve Sequence Open |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BSTD1106.FV03 |  | BSTD1106FV03_SeqOpnSttIL | BR4_Cluster1 | BPL131 | DIGITAL | %M10822 | West Turkeys Nest LME Standpipe Valve Sequence Open Interlock |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BSTD1106.FV03.FieldIO.CB01 |  | BSTD1106FV03CB01_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M10824 | West Turkeys Nest LME Standpipe 240VAC Flow Valve Power Circuit Breaker Open Healthy |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BSTD1106.FV03 |  | BSTD1106FV03STS1_SysOK | BR4_Cluster1 | BPL131 | DIGITAL | %M10829 | West Turkeys Nest LME Standpipe Valve Overall Control System Healthy |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop04 |  | BTK2101DX04VDC02_I | BR4_Cluster1 | BPL131 | DIGITAL | %M1083 | NPI Fire Water Tank DIO Box 1 24VDC GW1 Control Supply (Q157) Healthy |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BSTD1106.FV03 |  | BSTD1106FV03XS01_A | BR4_Cluster1 | BPL131 | DIGITAL | %M10835 | West Turkeys Nest LME Standpipe Valve Unhealthy Alarm |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BSTD1106.FV03 |  | BSTD1106FV03XS01_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M10836 | West Turkeys Nest LME Standpipe Valve Unhealthy Fault Healthy |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BSTD1106.FV03.FieldIO.ZT01 |  | BSTD1106FV03ZT01_ChOK | BR4_Cluster1 | BPL131 | DIGITAL | %M10839 | West Turkeys Nest LME Standpipe Flow Valve Position (%) Channel Healthy |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop04 |  | BTK2101DX04VDC03_I | BR4_Cluster1 | BPL131 | DIGITAL | %M1084 | NPI Fire Water Tank DIO Box 1 24VDC Instrument Control Supply (Q164) Healthy |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BSTD1107 | Auto | BSTD1107FIC01_Aut | BR4_Cluster1 | BPL131 | DIGITAL | %M10842 | West Turkeys Nest HME Standpipe Flow Controller Auto Mode |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BSTD1107 |  | BSTD1107FIC01_AutEn | BR4_Cluster1 | BPL131 | DIGITAL | %M10843 | West Turkeys Nest HME Standpipe Flow Controller Auto Enabled |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BSTD1107 |  | BSTD1107FIC01_Man | BR4_Cluster1 | BPL131 | DIGITAL | %M10845 | West Turkeys Nest HME Standpipe Flow Controller Manual Mode |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BSTD1107 |  | BSTD1107FT02_ChOK | BR4_Cluster1 | BPL131 | DIGITAL | %M10846 | West Turkeys Nest HME Standpipe Flow Rate (m3/h) Channel Healthy |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BSTD1107.FV02 |  | BSTD1107FV02_AlmAck | BR4_Cluster1 | BPL131 | DIGITAL | %M10847 | West Turkeys Nest HME Standpipe Valve Alarm Acknowledge |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BSTD1107.FV02 |  | BSTD1107FV02_AlmEn | BR4_Cluster1 | BPL131 | DIGITAL | %M10848 | West Turkeys Nest HME Standpipe Valve Alarm Enable |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BSTD1107.FV02 | Auto | BSTD1107FV02_Aut | BR4_Cluster1 | BPL131 | DIGITAL | %M10849 | West Turkeys Nest HME Standpipe Valve Mode Auto |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop04 |  | BTK2101DX04VDC04_I | BR4_Cluster1 | BPL131 | DIGITAL | %M1085 | NPI Fire Water Tank DIO Box 1 24VDC Transmitter Control Supply (Q168) Healthy |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BSTD1107.FV02 |  | BSTD1107FV02_AutRdy | BR4_Cluster1 | BPL131 | DIGITAL | %M10850 | West Turkeys Nest HME Standpipe Valve Auto Ready |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BSTD1107.FV02 |  | BSTD1107FV02_CIL | BR4_Cluster1 | BPL131 | DIGITAL | %M10851 | West Turkeys Nest HME Standpipe Valve Critical Interlock Healthy |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BSTD1107.FV02 |  | BSTD1107FV02_Cls | BR4_Cluster1 | BPL131 | DIGITAL | %M10852 | West Turkeys Nest HME Standpipe Valve Close Command |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BSTD1107.FV02 |  | BSTD1107FV02_Clsd | BR4_Cluster1 | BPL131 | DIGITAL | %M10853 | West Turkeys Nest HME Standpipe Valve Closed |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BSTD1107.FV02 |  | BSTD1107FV02_Clsg | BR4_Cluster1 | BPL131 | DIGITAL | %M10854 | West Turkeys Nest HME Standpipe Valve Closing |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BSTD1107.FV02 |  | BSTD1107FV02_ComOK | BR4_Cluster1 | BPL131 | DIGITAL | %M10855 | West Turkeys Nest HME Standpipe Valve Overall Comms Healthy |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BSTD1107.FV02 |  | BSTD1107FV02_ExcRun_A | BR4_Cluster1 | BPL131 | DIGITAL | %M10856 | West Turkeys Nest HME Standpipe Valve Excessive Open Alarm |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BSTD1107.FV02 |  | BSTD1107FV02_ExcRun_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M10857 | West Turkeys Nest HME Standpipe Valve Excessive Open Time Fault Healthy |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BSTD1107.FV02 |  | BSTD1107FV02_FltSL | BR4_Cluster1 | BPL131 | DIGITAL | %M10858 | West Turkeys Nest HME Standpipe Valve Fault Seal |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BSTD1107.FV02 |  | BSTD1107FV02_FTC | BR4_Cluster1 | BPL131 | DIGITAL | %M10859 | West Turkeys Nest HME Standpipe Valve Fail to Close |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop04 |  | BTK2101DX04VDC05_I | BR4_Cluster1 | BPL131 | DIGITAL | %M1086 | NPI Fire Water Tank DIO Box 1 24VDC BTK2101DX04 Control Supply (Q172) Healthy |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BSTD1107.FV02 |  | BSTD1107FV02_FTC_A | BR4_Cluster1 | BPL131 | DIGITAL | %M10860 | West Turkeys Nest HME Standpipe Valve Fail to Close Alarm |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BSTD1107.FV02 |  | BSTD1107FV02_FTC_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M10861 | West Turkeys Nest HME Standpipe Valve Fail to Close Fault Healthy |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BSTD1107.FV02 |  | BSTD1107FV02_FTO | BR4_Cluster1 | BPL131 | DIGITAL | %M10862 | West Turkeys Nest HME Standpipe Valve Fail to Open |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.UP01 |  | BSR131UP01XS01_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M10863 | BSR131 UPS Surge Filter Healthy |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.CB01 |  | BSR131UP01TRP01_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M10864 | BSR131 UPS Main Circuit Breaker Trip Healthy |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BSTD1107.FV02 |  | BSTD1107FV02_LmtFlt | BR4_Cluster1 | BPL131 | DIGITAL | %M10865 | West Turkeys Nest HME Standpipe Valve Position Fault |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BSTD1107.FV02 |  | BSTD1107FV02_LmtFlt_A | BR4_Cluster1 | BPL131 | DIGITAL | %M10866 | West Turkeys Nest HME Standpipe Valve Dual Limit Alarm |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BSTD1107.FV02 |  | BSTD1107FV02_LmtFlt_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M10867 | West Turkeys Nest HME Standpipe Valve Dual Limit Fault Healthy |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BSTD1107.FV02 | Local | BSTD1107FV02_Loc | BR4_Cluster1 | BPL131 | DIGITAL | %M10868 | West Turkeys Nest HME Standpipe Valve Mode Local |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BSTD1107.FV02 |  | BSTD1107FV02_LocClsReq | BR4_Cluster1 | BPL131 | DIGITAL | %M10869 | West Turkeys Nest HME Standpipe Valve Local Close Requested |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop04 |  | BTK2101DX04VDC06_I | BR4_Cluster1 | BPL131 | DIGITAL | %M1087 | NPI Fire Water Tank DIO Box 1 24VDC Spare Control Supply (Q176) Healthy |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BSTD1107.FV02 |  | BSTD1107FV02_LocOpnReq | BR4_Cluster1 | BPL131 | DIGITAL | %M10870 | West Turkeys Nest HME Standpipe Valve Local Open Requested |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BSTD1107.FV02 |  | BSTD1107FV02_Man | BR4_Cluster1 | BPL131 | DIGITAL | %M10871 | West Turkeys Nest HME Standpipe Valve Mode Manual |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BSTD1107.FV02 |  | BSTD1107FV02_NCIL | BR4_Cluster1 | BPL131 | DIGITAL | %M10872 | West Turkeys Nest HME Standpipe Valve Non-Critical Interlock Healthy |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BSTD1107.FV02 |  | BSTD1107FV02_NCILAlmEn | BR4_Cluster1 | BPL131 | DIGITAL | %M10873 | West Turkeys Nest HME Standpipe Valve NCIL Alarm Enable |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BSTD1107.FV02 |  | BSTD1107FV02_OOS | BR4_Cluster1 | BPL131 | DIGITAL | %M10874 | West Turkeys Nest HME Standpipe Valve Mode Out of Service |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BSTD1107.FV02 |  | BSTD1107FV02_Opn | BR4_Cluster1 | BPL131 | DIGITAL | %M10875 | West Turkeys Nest HME Standpipe Valve Open Command |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BSTD1107.FV02 |  | BSTD1107FV02_Opnd | BR4_Cluster1 | BPL131 | DIGITAL | %M10876 | West Turkeys Nest HME Standpipe Valve Opened |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BSTD1107.FV02 |  | BSTD1107FV02_Opng | BR4_Cluster1 | BPL131 | DIGITAL | %M10877 | West Turkeys Nest HME Standpipe Valve Opening |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BSTD1107.FV02 |  | BSTD1107FV02_PwrOK | BR4_Cluster1 | BPL131 | DIGITAL | %M10878 | West Turkeys Nest HME Standpipe Valve Overall Power Healthy |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BSTD1107.FV02 |  | BSTD1107FV02_RstRqd | BR4_Cluster1 | BPL131 | DIGITAL | %M10879 | West Turkeys Nest HME Standpipe Valve Reset Required |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop04 |  | BTK2101DX04VDC07_I | BR4_Cluster1 | BPL131 | DIGITAL | %M1088 | NPI Fire Water Tank DIO Box 1 24VDC Spare Control Supply (Q180) Healthy |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BSTD1107.FV02 |  | BSTD1107FV02_SeqCls | BR4_Cluster1 | BPL131 | DIGITAL | %M10880 | West Turkeys Nest HME Standpipe Valve Sequence Close |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BSTD1107.FV02 |  | BSTD1107FV02_SeqClsSttIL | BR4_Cluster1 | BPL131 | DIGITAL | %M10881 | West Turkeys Nest HME Standpipe Valve Sequence Close Interlock |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BSTD1107.FV02 |  | BSTD1107FV02_SeqOpn | BR4_Cluster1 | BPL131 | DIGITAL | %M10882 | West Turkeys Nest HME Standpipe Valve Sequence Open |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BSTD1107.FV02 |  | BSTD1107FV02_SeqOpnSttIL | BR4_Cluster1 | BPL131 | DIGITAL | %M10883 | West Turkeys Nest HME Standpipe Valve Sequence Open Interlock |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BSTD1107.FV02.FieldIO.CB01 |  | BSTD1107FV02CB01_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M10885 | West Turkeys Nest HME Standpipe 240VAC Flow Valve Power Circuit Breaker Open Healthy |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BSTD1107.FV02 |  | BSTD1107FV02_FTO_A | BR4_Cluster1 | BPL131 | DIGITAL | %M10886 | West Turkeys Nest HME Standpipe Valve Fail to Open Alarm |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BSTD1107.FV02 |  | BSTD1107FV02_FTO_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M10887 | West Turkeys Nest HME Standpipe Valve Fail to Open Fault Healthy |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop04 |  | BTK2101DX04VDC08_I | BR4_Cluster1 | BPL131 | DIGITAL | %M1089 | NPI Fire Water Tank DIO Box 1 24VDC Spare Control Supply (Q184) Healthy |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BSTD1107.FV02 |  | BSTD1107FV02STS1_SysOK | BR4_Cluster1 | BPL131 | DIGITAL | %M10890 | West Turkeys Nest HME Standpipe Valve Overall Control System Healthy |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BSTD1107.FV02 |  | BSTD1107FV02XS01_A | BR4_Cluster1 | BPL131 | DIGITAL | %M10896 | West Turkeys Nest HME Standpipe Valve Unhealthy Alarm |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BSTD1107.FV02 |  | BSTD1107FV02XS01_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M10897 | West Turkeys Nest HME Standpipe Valve Unhealthy Fault Healthy |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop04 |  | BTK2101DX04VDC09_I | BR4_Cluster1 | BPL131 | DIGITAL | %M1090 | NPI Fire Water Tank DIO Box 1 24VDC Spare Control Supply (Q188) Healthy |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BSTD1107.FV02.FieldIO.ZT01 |  | BSTD1107FV02ZT01_ChOK | BR4_Cluster1 | BPL131 | DIGITAL | %M10900 | West Turkeys Nest HME Standpipe Flow Valve Position (%) Channel Healthy |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop04 |  | BTK2101DX04_PwrOK | BR4_Cluster1 | BPL131 | DIGITAL | %M10903 | NPI Fire Water Tank DIO Box 1 Power Healthy Status |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop04 |  | BTK2101DX04DIO1PLM0_ComFlt_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M10905 | BTK2101DX04 CRA Comms Module 0 Communications Fault Healthy |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop04 |  | BTK2101DX04DIO1PLM0_Flt_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M10906 | BTK2101DX04 CRA Comms Module 0 Fault Healthy |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop04 |  | BTK2101DX04DIO1PLM0_LnkOK | BR4_Cluster1 | BPL131 | DIGITAL | %M10907 | BTK2101DX04 CRA Comms Module 0 Link Healthy |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop04 |  | BTK2101DX04DIO1PLM0_OK | BR4_Cluster1 | BPL131 | DIGITAL | %M10908 | BTK2101DX04 CRA Comms Module 0 Data Healthy |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop04 |  | BTK2101DX04DIO1PLM1_Flt_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M10909 | BTK2101DX04 DI Module 1 Fault Healthy |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop04 |  | BTK2101DX04VDC10_I | BR4_Cluster1 | BPL131 | DIGITAL | %M1091 | NPI Fire Water Tank DIO Box 1 24VDC Spare Control Supply (Q192) Healthy |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop04 |  | BTK2101DX04DIO1PLM1_Grp1Flt_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M10910 | BTK2101DX04 DI Module 1 Group 1 Fault Healthy |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop04 |  | BTK2101DX04DIO1PLM1_Grp1OK | BR4_Cluster1 | BPL131 | DIGITAL | %M10911 | BTK2101DX04 DI Module 1 Group 1 (00-15) Healthy |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop04 |  | BTK2101DX04DIO1PLM1_Grp2Flt_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M10912 | BTK2101DX04 DI Module 1 Group 2 Fault Healthy |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop04 |  | BTK2101DX04DIO1PLM1_Grp2OK | BR4_Cluster1 | BPL131 | DIGITAL | %M10913 | BTK2101DX04 DI Module 1 Group 2 (16-31) Healthy |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop04 |  | BTK2101DX04DIO1PLM1_OK | BR4_Cluster1 | BPL131 | DIGITAL | %M10914 | BTK2101DX04 DI Module 1 Data Valid |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop04 |  | BTK2101DX04DIO1PLM3_Ch00Flt_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M10915 | BTK2101DX04 AHI Module 3 Channel 0 Fault Healthy |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop04 |  | BTK2101DX04DIO1PLM3_Ch01Flt_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M10916 | BTK2101DX04 AHI Module 3 Channel 1 Fault Healthy |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop04 |  | BTK2101DX04DIO1PLM3_Ch02Flt_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M10917 | BTK2101DX04 AHI Module 3 Channel 2 Fault Healthy |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop04 |  | BTK2101DX04DIO1PLM3_Ch03Flt_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M10918 | BTK2101DX04 AHI Module 3 Channel 3 Fault Healthy |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop04 |  | BTK2101DX04DIO1PLM3_Ch04Flt_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M10919 | BTK2101DX04 AHI Module 3 Channel 4 Fault Healthy |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop04 |  | BTK2101DX04VDC11_I | BR4_Cluster1 | BPL131 | DIGITAL | %M1092 | NPI Fire Water Tank DIO Box 1 24VDC Spare Control Supply (Q196) Healthy |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop04 |  | BTK2101DX04DIO1PLM3_Ch05Flt_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M10920 | BTK2101DX04 AHI Module 3 Channel 5 Fault Healthy |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop04 |  | BTK2101DX04DIO1PLM3_Ch06Flt_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M10921 | BTK2101DX04 AHI Module 3 Channel 6 Fault Healthy |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop04 |  | BTK2101DX04DIO1PLM3_Ch07Flt_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M10922 | BTK2101DX04 AHI Module 3 Channel 7 Fault Healthy |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop04 |  | BTK2101DX04DIO1PLM3_Flt_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M10923 | BTK2101DX04 AHI Module 3 Fault Healthy |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop04 |  | BTK2101DX04DIO1PLM3_OK | BR4_Cluster1 | BPL131 | DIGITAL | %M10924 | BTK2101DX04 AHI Module 3 Data Valid |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop04 |  | BTK2101DX04VDC01_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M10925 | NPI Fire Water Tank DIO Box 1 24VDC Output Control Supply (Q143) Failure Healthy |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop04 |  | BTK2101DX04VDC02_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M10926 | NPI Fire Water Tank DIO Box 1 24VDC GW1 Control Supply (Q157) Failure Healthy |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop04 |  | BTK2101DX04VDC03_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M10927 | NPI Fire Water Tank DIO Box 1 24VDC Instrument Control Supply (Q164) Failure Healthy |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop04 |  | BTK2101DX04VDC04_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M10928 | NPI Fire Water Tank DIO Box 1 24VDC Transmitter Control Supply (Q168) Failure Healthy |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop04 |  | BTK2101DX04VDC05_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M10929 | NPI Fire Water Tank DIO Box 1 24VDC BTK2101DX04 Control Supply (Q172) Failure Healthy |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1101.FieldIO.FT01 |  | BPP1101FQ01_I | BR4_Cluster1 | BPL131 | DIGITAL | %M1093 | Production Plant and NPI Water Supply Pump 1 Flow Totaliser Pulse |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1101 |  | BPP1101FQ02_I | BR4_Cluster1 | BPL131 | DIGITAL | %M1094 | Production Plant and NPI Water Supply Pump 1 Flow Totaliser Pulse |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.P3FIREWATER.BTK2101.FieldIO.LT01 |  | BTK2101LT01_ChOK | BR4_Cluster1 | BPL131 | DIGITAL | %M10945 | NPI Fire Water Tank 1 Tank Level (%) Channel Healthy |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.P3FIREWATER.BTK2101 |  | BTK2101FIP01XS01_I | BR4_Cluster1 | BPL131 | DIGITAL | %M1095 | NPI Fire Water Panel Fire Panel Fault Healthy |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.P3FIREWATER.BTK2102.FieldIO.LT01 |  | BTK2102LT01_ChOK | BR4_Cluster1 | BPL131 | DIGITAL | %M10950 | NPI Fire Water Tank 2 Tank Level (%) Channel Healthy |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop02 |  | BTY1502DX02_PwrOK | BR4_Cluster1 | BPL131 | DIGITAL | %M10951 | West Turkeys Nest DIO Box 2 Power Healthy Status |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop02 |  | BTY1502DX02DIO1PLM0_ComFlt_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M10953 | BTY1502DX02 CRA Comms Module 0 Communications Fault Healthy |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop02 |  | BTY1502DX02DIO1PLM0_Flt_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M10954 | BTY1502DX02 CRA Comms Module 0 Fault Healthy |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop02 |  | BTY1502DX02DIO1PLM0_LnkOK | BR4_Cluster1 | BPL131 | DIGITAL | %M10955 | BTY1502DX02 CRA Comms Module 0 Link Healthy |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop02 |  | BTY1502DX02DIO1PLM0_OK | BR4_Cluster1 | BPL131 | DIGITAL | %M10956 | BTY1502DX02 CRA Comms Module 0 Data Healthy |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop02 |  | BTY1502DX02DIO1PLM1_Flt_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M10957 | BTY1502DX02 DI Module 1 Fault Healthy |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop02 |  | BTY1502DX02DIO1PLM1_Grp1Flt_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M10958 | BTY1502DX02 DI Module 1 Group 1 Fault Healthy |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop02 |  | BTY1502DX02DIO1PLM1_Grp1OK | BR4_Cluster1 | BPL131 | DIGITAL | %M10959 | BTY1502DX02 DI Module 1 Group 1 (00-15) Healthy |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.P3FIREWATER.BTK2101 |  | BTK2101FIP01IS01_I | BR4_Cluster1 | BPL131 | DIGITAL | %M1096 | NPI Fire Water Panel Fire Panel Isolated Healthy |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop02 |  | BTY1502DX02DIO1PLM1_Grp2Flt_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M10960 | BTY1502DX02 DI Module 1 Group 2 Fault Healthy |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop02 |  | BTY1502DX02DIO1PLM1_Grp2OK | BR4_Cluster1 | BPL131 | DIGITAL | %M10961 | BTY1502DX02 DI Module 1 Group 2 (16-31) Healthy |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop02 |  | BTY1502DX02DIO1PLM1_OK | BR4_Cluster1 | BPL131 | DIGITAL | %M10962 | BTY1502DX02 DI Module 1 Data Valid |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop02 |  | BTY1502DX02DIO1PLM2_Flt_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M10963 | BTY1502DX02 DI Module 2 Fault Healthy |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop02 |  | BTY1502DX02DIO1PLM2_Grp1Flt_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M10964 | BTY1502DX02 DI Module 2 Group 1 Fault Healthy |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop02 |  | BTY1502DX02DIO1PLM2_Grp1OK | BR4_Cluster1 | BPL131 | DIGITAL | %M10965 | BTY1502DX02 DI Module 2 Group 1 (00-15) Healthy |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop02 |  | BTY1502DX02DIO1PLM2_Grp2Flt_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M10966 | BTY1502DX02 DI Module 2 Group 2 Fault Healthy |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop02 |  | BTY1502DX02DIO1PLM2_Grp2OK | BR4_Cluster1 | BPL131 | DIGITAL | %M10967 | BTY1502DX02 DI Module 2 Group 2 (16-31) Healthy |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop02 |  | BTY1502DX02DIO1PLM2_OK | BR4_Cluster1 | BPL131 | DIGITAL | %M10968 | BTY1502DX02 DI Module 2 Data Valid |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop02 |  | BTY1502DX02DIO1PLM3_Flt_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M10969 | BTY1502DX02 DI Module 3 Fault Healthy |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.P3FIREWATER.BTK2101 |  | BTK2101FIP01XS02_I | BR4_Cluster1 | BPL131 | DIGITAL | %M1097 | NPI Fire Water Panel Fire Alarm Healthy |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop02 |  | BTY1502DX02DIO1PLM3_Grp1Flt_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M10970 | BTY1502DX02 DI Module 3 Group 1 Fault Healthy |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop02 |  | BTY1502DX02DIO1PLM3_Grp1OK | BR4_Cluster1 | BPL131 | DIGITAL | %M10971 | BTY1502DX02 DI Module 3 Group 1 (00-15) Healthy |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop02 |  | BTY1502DX02DIO1PLM3_Grp2Flt_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M10972 | BTY1502DX02 DI Module 3 Group 2 Fault Healthy |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop02 |  | BTY1502DX02DIO1PLM3_Grp2OK | BR4_Cluster1 | BPL131 | DIGITAL | %M10973 | BTY1502DX02 DI Module 3 Group 2 (16-31) Healthy |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop02 |  | BTY1502DX02DIO1PLM3_OK | BR4_Cluster1 | BPL131 | DIGITAL | %M10974 | BTY1502DX02 DI Module 3 Data Valid |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop02 |  | BTY1502DX02DIO1PLM4_Flt_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M10975 | BTY1502DX02 DO Module 4 Fault Healthy |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop02 |  | BTY1502DX02DIO1PLM4_OK | BR4_Cluster1 | BPL131 | DIGITAL | %M10976 | BTY1502DX02 DO Module 4 Data Valid |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop02 |  | BTY1502DX02DIO1PLM5_Ch00Flt_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M10977 | BTY1502DX02 AHI Module 5 Channel 0 Fault Healthy |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop02 |  | BTY1502DX02DIO1PLM5_Ch01Flt_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M10978 | BTY1502DX02 AHI Module 5 Channel 1 Fault Healthy |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop02 |  | BTY1502DX02DIO1PLM5_Ch02Flt_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M10979 | BTY1502DX02 AHI Module 5 Channel 2 Fault Healthy |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.BC02 |  | BSR131BC02VDC02_I | BR4_Cluster1 | BPL131 | DIGITAL | %M1098 | BSR131 Battery Charger 2 Battery Charger 110VDC Tripping Supply (K112) Healthy |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop02 |  | BTY1502DX02DIO1PLM5_Ch03Flt_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M10980 | BTY1502DX02 AHI Module 5 Channel 3 Fault Healthy |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop02 |  | BTY1502DX02DIO1PLM5_Ch04Flt_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M10981 | BTY1502DX02 AHI Module 5 Channel 4 Fault Healthy |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop02 |  | BTY1502DX02DIO1PLM5_Ch05Flt_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M10982 | BTY1502DX02 AHI Module 5 Channel 5 Fault Healthy |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop02 |  | BTY1502DX02DIO1PLM5_Ch06Flt_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M10983 | BTY1502DX02 AHI Module 5 Channel 6 Fault Healthy |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop02 |  | BTY1502DX02DIO1PLM5_Ch07Flt_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M10984 | BTY1502DX02 AHI Module 5 Channel 7 Fault Healthy |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop02 |  | BTY1502DX02DIO1PLM5_Flt_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M10985 | BTY1502DX02 AHI Module 5 Fault Healthy |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop02 |  | BTY1502DX02DIO1PLM5_OK | BR4_Cluster1 | BPL131 | DIGITAL | %M10986 | BTY1502DX02 AHI Module 5 Data Valid |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop02 |  | BTY1502DX02DIO1PLM6_Ch00Flt_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M10987 | BTY1502DX02 AHI Module 6 Channel 0 Fault Healthy |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop02 |  | BTY1502DX02DIO1PLM6_Ch01Flt_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M10988 | BTY1502DX02 AHI Module 6 Channel 1 Fault Healthy |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop02 |  | BTY1502DX02DIO1PLM6_Ch02Flt_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M10989 | BTY1502DX02 AHI Module 6 Channel 2 Fault Healthy |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.BC02 |  | BSR131BC02CB02_I | BR4_Cluster1 | BPL131 | DIGITAL | %M1099 | BSR131 Battery Charger 2 BMC131INC01 110VDC INC01 Tripping Supply Circuit Breaker (Q114) Closed |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop02 |  | BTY1502DX02DIO1PLM6_Ch03Flt_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M10990 | BTY1502DX02 AHI Module 6 Channel 3 Fault Healthy |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop02 |  | BTY1502DX02DIO1PLM6_Ch04Flt_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M10991 | BTY1502DX02 AHI Module 6 Channel 4 Fault Healthy |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop02 |  | BTY1502DX02DIO1PLM6_Ch05Flt_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M10992 | BTY1502DX02 AHI Module 6 Channel 5 Fault Healthy |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop02 |  | BTY1502DX02DIO1PLM6_Ch06Flt_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M10993 | BTY1502DX02 AHI Module 6 Channel 6 Fault Healthy |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop02 |  | BTY1502DX02DIO1PLM6_Ch07Flt_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M10994 | BTY1502DX02 AHI Module 6 Channel 7 Fault Healthy |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop02 |  | BTY1502DX02DIO1PLM6_Flt_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M10995 | BTY1502DX02 AHI Module 6 Fault Healthy |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop02 |  | BTY1502DX02DIO1PLM6_OK | BR4_Cluster1 | BPL131 | DIGITAL | %M10996 | BTY1502DX02 AHI Module 6 Data Valid |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop02 |  | BTY1502DX02DIO1PLM7_Ch00Flt_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M10997 | BTY1502DX02 AHI Module 7 Channel 0 Fault Healthy |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop02 |  | BTY1502DX02DIO1PLM7_Ch01Flt_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M10998 | BTY1502DX02 AHI Module 7 Channel 1 Fault Healthy |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop02 |  | BTY1502DX02DIO1PLM7_Ch02Flt_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M10999 | BTY1502DX02 AHI Module 7 Channel 2 Fault Healthy |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.BC02 |  | BSR131BC02CB03_I | BR4_Cluster1 | BPL131 | DIGITAL | %M1100 | BSR131 Battery Charger 2 BMC131INC02 110VDC INC02 Tripping Supply Circuit Breaker (Q117) Closed |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop02 |  | BTY1502DX02DIO1PLM7_Ch03Flt_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M11000 | BTY1502DX02 AHI Module 7 Channel 3 Fault Healthy |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop02 |  | BTY1502DX02DIO1PLM7_Ch04Flt_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M11001 | BTY1502DX02 AHI Module 7 Channel 4 Fault Healthy |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop02 |  | BTY1502DX02DIO1PLM7_Ch05Flt_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M11002 | BTY1502DX02 AHI Module 7 Channel 5 Fault Healthy |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop02 |  | BTY1502DX02DIO1PLM7_Ch06Flt_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M11003 | BTY1502DX02 AHI Module 7 Channel 6 Fault Healthy |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop02 |  | BTY1502DX02DIO1PLM7_Ch07Flt_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M11004 | BTY1502DX02 AHI Module 7 Channel 7 Fault Healthy |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop02 |  | BTY1502DX02DIO1PLM7_Flt_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M11005 | BTY1502DX02 AHI Module 7 Fault Healthy |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop02 |  | BTY1502DX02DIO1PLM7_OK | BR4_Cluster1 | BPL131 | DIGITAL | %M11006 | BTY1502DX02 AHI Module 7 Data Valid |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop02 |  | BTY1502DX02DIO1PLM9_Ch00Flt_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M11007 | BTY1502DX02 AHO Module 9 Channel 0 Fault Healthy |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop02 |  | BTY1502DX02DIO1PLM9_Ch01Flt_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M11008 | BTY1502DX02 AHO Module 9 Channel 1 Fault Healthy |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop02 |  | BTY1502DX02DIO1PLM9_Ch02Flt_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M11009 | BTY1502DX02 AHO Module 9 Channel 2 Fault Healthy |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.BC02 |  | BSR131BC02CB04_I | BR4_Cluster1 | BPL131 | DIGITAL | %M1101 | BSR131 Battery Charger 2 BMC131INC03 110VDC INC03 Tripping Supply Circuit Breaker (Q120) Closed |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop02 |  | BTY1502DX02DIO1PLM9_Ch03Flt_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M11010 | BTY1502DX02 AHO Module 9 Channel 3 Fault Healthy |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop02 |  | BTY1502DX02DIO1PLM9_Flt_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M11011 | BTY1502DX02 AHO Module 9 Fault Healthy |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop02 |  | BTY1502DX02DIO1PLM9_OK | BR4_Cluster1 | BPL131 | DIGITAL | %M11012 | BTY1502DX02 AHO Module 9 Data Valid |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.BTY1502.FieldIO |  | BTY1502DX02VDC01_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M11013 | West Turkeys Nest DIO Box 2 24VDC Output Control Supply (Q143) Failure Healthy |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.BTY1502.FieldIO |  | BTY1502DX02VDC02_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M11014 | West Turkeys Nest DIO Box 2 24VDC GW1 Control Supply (Q157) Failure Healthy |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.BTY1502.FieldIO |  | BTY1502DX02VDC03_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M11015 | West Turkeys Nest DIO Box 2 24VDC Instrument Control Supply (Q164) Failure Healthy |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.BTY1502.FieldIO |  | BTY1502DX02VDC04_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M11016 | West Turkeys Nest DIO Box 2 24VDC Transmitter Control Supply (Q168) Failure Healthy |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.BTY1502.FieldIO |  | BTY1502DX02VDC05_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M11017 | West Turkeys Nest DIO Box 2 24VDC Process Water Control Supply (Q172) Failure Healthy |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1101.FieldIO |  | BTY1502DX02VDC06_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M11018 | West Turkeys Nest DIO Box 2 24VDC BPP1101 Control Supply (Q176) Failure Healthy |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1102.FieldIO |  | BTY1502DX02VDC07_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M11019 | West Turkeys Nest DIO Box 2 24VDC BPP1102 Control Supply (Q180) Failure Healthy |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.BC02 |  | BSR131BC02CB05_I | BR4_Cluster1 | BPL131 | DIGITAL | %M1102 | BSR131 Battery Charger 2 RSP01 110VDC Tripping Supply Circuit Breaker (Q123) Closed |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BPP1106.FieldIO |  | BTY1502DX02VDC08_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M11020 | West Turkeys Nest DIO Box 2 24VDC BPP1106 Control Supply (Q184) Failure Healthy |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BPP1107.FieldIO |  | BTY1502DX02VDC09_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M11021 | West Turkeys Nest DIO Box 2 24VDC BPP1107 Control Supply (Q188) Failure Healthy |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BSTD1106.FieldIO |  | BTY1502DX02VDC10_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M11022 | West Turkeys Nest DIO Box 2 24VDC BSTD1106 Control Supply (Q192) Failure Healthy |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BSTD1107.FieldIO |  | BTY1502DX02VDC11_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M11023 | West Turkeys Nest DIO Box 2 24VDC BSTD1107 Control Supply (Q196) Failure Healthy |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop03 |  | BTY1502DX03_PwrOK | BR4_Cluster1 | BPL131 | DIGITAL | %M11024 | West Turkeys Nest DIO Box 3 Power Healthy Status |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop03 |  | BTY1502DX03DIO1PLM0_ComFlt_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M11026 | BTY1502DX03 CRA Comms Module 0 Communications Fault Healthy |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop03 |  | BTY1502DX03DIO1PLM0_Flt_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M11027 | BTY1502DX03 CRA Comms Module 0 Fault Healthy |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop03 |  | BTY1502DX03DIO1PLM0_LnkOK | BR4_Cluster1 | BPL131 | DIGITAL | %M11028 | BTY1502DX03 CRA Comms Module 0 Link Healthy |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop03 |  | BTY1502DX03DIO1PLM0_OK | BR4_Cluster1 | BPL131 | DIGITAL | %M11029 | BTY1502DX03 CRA Comms Module 0 Data Healthy |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.BC02 |  | BSR131BC02CB06_I | BR4_Cluster1 | BPL131 | DIGITAL | %M1103 | BSR131 Battery Charger 2 Spare 110VDC Tripping Supply Circuit Breaker (Q126) Closed |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop03 |  | BTY1502DX03DIO1PLM1_Flt_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M11030 | BTY1502DX03 DI Module 1 Fault Healthy |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop03 |  | BTY1502DX03DIO1PLM1_Grp1Flt_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M11031 | BTY1502DX03 DI Module 1 Group 1 Fault Healthy |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop03 |  | BTY1502DX03DIO1PLM1_Grp1OK | BR4_Cluster1 | BPL131 | DIGITAL | %M11032 | BTY1502DX03 DI Module 1 Group 1 (00-15) Healthy |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop03 |  | BTY1502DX03DIO1PLM1_Grp2Flt_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M11033 | BTY1502DX03 DI Module 1 Group 2 Fault Healthy |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop03 |  | BTY1502DX03DIO1PLM1_Grp2OK | BR4_Cluster1 | BPL131 | DIGITAL | %M11034 | BTY1502DX03 DI Module 1 Group 2 (16-31) Healthy |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop03 |  | BTY1502DX03DIO1PLM1_OK | BR4_Cluster1 | BPL131 | DIGITAL | %M11035 | BTY1502DX03 DI Module 1 Data Valid |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop03 |  | BTY1502DX03DIO1PLM3_Ch00Flt_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M11036 | BTY1502DX03 AHI Module 3 Channel 0 Fault Healthy |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop03 |  | BTY1502DX03DIO1PLM3_Ch01Flt_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M11037 | BTY1502DX03 AHI Module 3 Channel 1 Fault Healthy |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop03 |  | BTY1502DX03DIO1PLM3_Ch02Flt_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M11038 | BTY1502DX03 AHI Module 3 Channel 2 Fault Healthy |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop03 |  | BTY1502DX03DIO1PLM3_Ch03Flt_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M11039 | BTY1502DX03 AHI Module 3 Channel 3 Fault Healthy |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.BC02 |  | BSR131BC02CB07_I | BR4_Cluster1 | BPL131 | DIGITAL | %M1104 | BSR131 Battery Charger 2 Spare 110VDC Tripping Supply Circuit Breaker (Q129) Closed |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop03 |  | BTY1502DX03DIO1PLM3_Ch04Flt_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M11040 | BTY1502DX03 AHI Module 3 Channel 4 Fault Healthy |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop03 |  | BTY1502DX03DIO1PLM3_Ch05Flt_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M11041 | BTY1502DX03 AHI Module 3 Channel 5 Fault Healthy |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop03 |  | BTY1502DX03DIO1PLM3_Ch06Flt_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M11042 | BTY1502DX03 AHI Module 3 Channel 6 Fault Healthy |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop03 |  | BTY1502DX03DIO1PLM3_Ch07Flt_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M11043 | BTY1502DX03 AHI Module 3 Channel 7 Fault Healthy |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop03 |  | BTY1502DX03DIO1PLM3_Flt_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M11044 | BTY1502DX03 AHI Module 3 Fault Healthy |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop03 |  | BTY1502DX03DIO1PLM3_OK | BR4_Cluster1 | BPL131 | DIGITAL | %M11045 | BTY1502DX03 AHI Module 3 Data Valid |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop03 |  | BTY1502DX03DIO1PLM4_Ch00Flt_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M11046 | BTY1502DX03 AHI Module 4 Channel 0 Fault Healthy |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop03 |  | BTY1502DX03DIO1PLM4_Ch01Flt_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M11047 | BTY1502DX03 AHI Module 4 Channel 1 Fault Healthy |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop03 |  | BTY1502DX03DIO1PLM4_Ch02Flt_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M11048 | BTY1502DX03 AHI Module 4 Channel 2 Fault Healthy |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop03 |  | BTY1502DX03DIO1PLM4_Ch03Flt_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M11049 | BTY1502DX03 AHI Module 4 Channel 3 Fault Healthy |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.BC02 |  | BSR131BC02CB08_I | BR4_Cluster1 | BPL131 | DIGITAL | %M1105 | BSR131 Battery Charger 2 Spare 110VDC Tripping Supply Circuit Breaker (Q132) Closed |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop03 |  | BTY1502DX03DIO1PLM4_Ch04Flt_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M11050 | BTY1502DX03 AHI Module 4 Channel 4 Fault Healthy |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop03 |  | BTY1502DX03DIO1PLM4_Ch05Flt_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M11051 | BTY1502DX03 AHI Module 4 Channel 5 Fault Healthy |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop03 |  | BTY1502DX03DIO1PLM4_Ch06Flt_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M11052 | BTY1502DX03 AHI Module 4 Channel 6 Fault Healthy |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop03 |  | BTY1502DX03DIO1PLM4_Ch07Flt_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M11053 | BTY1502DX03 AHI Module 4 Channel 7 Fault Healthy |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop03 |  | BTY1502DX03DIO1PLM4_Flt_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M11054 | BTY1502DX03 AHI Module 4 Fault Healthy |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop03 |  | BTY1502DX03DIO1PLM4_OK | BR4_Cluster1 | BPL131 | DIGITAL | %M11055 | BTY1502DX03 AHI Module 4 Data Valid |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop03 |  | BTY1502DX03VDC01_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M11056 | West Turkeys Nest DIO Box 3 24VDC Output Control Supply (Q143) Failure Healthy |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop03 |  | BTY1502DX03VDC02_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M11057 | West Turkeys Nest DIO Box 3 24VDC GW1 Control Supply (Q157) Failure Healthy |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop03 |  | BTY1502DX03VDC03_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M11058 | West Turkeys Nest DIO Box 3 24VDC Instrument Control Supply (Q164) Failure Healthy |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop03 |  | BTY1502DX03VDC04_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M11059 | West Turkeys Nest DIO Box 3 24VDC Transmitter Control Supply (Q168) Failure Healthy |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.BC02 |  | BSR131BC02CB09_I | BR4_Cluster1 | BPL131 | DIGITAL | %M1106 | BSR131 Battery Charger 2 Spare 110VDC Tripping Supply Circuit Breaker (Q135) Closed |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop03 |  | BTY1502DX03VDC05_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M11060 | West Turkeys Nest DIO Box 3 24VDC BTY1502DX03 Field Control Supply (Q172) Failure Healthy |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop03 |  | BTY1502DX03VDC06_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M11061 | West Turkeys Nest DIO Box 3 24VDC BPP1103 Field Control Supply (Q176) Failure Healthy |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop03 |  | BTY1502DX03VDC07_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M11062 | West Turkeys Nest DIO Box 3 24VDC BPP1104 Field Control Supply (Q180) Failure Healthy |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop03 |  | BTY1502DX03VDC08_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M11063 | West Turkeys Nest DIO Box 3 24VDC BPP1105 Field Control Supply (Q184) Failure Healthy |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.BTY1502.FieldIO.FT01 |  | BTY1502FT01_ChOK | BR4_Cluster1 | BPL131 | DIGITAL | %M11067 | West Turkeys Nest Flow Rate (m3/h) Channel Healthy |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.BTY1502.FieldIO.FT02 |  | BTY1502FT02_ChOK | BR4_Cluster1 | BPL131 | DIGITAL | %M11068 | West Turkeys Nest Flow Rate (m3/h) Channel Healthy |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.BTY1502.FieldIO.FT03 |  | BTY1502FT03_ChOK | BR4_Cluster1 | BPL131 | DIGITAL | %M11069 | West Turkeys Nest Flow Rate (m3/h) Channel Healthy |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.BC02 |  | BSR131BC02CB10_I | BR4_Cluster1 | BPL131 | DIGITAL | %M1107 | BSR131 Battery Charger 2 Spare 110VDC Tripping Supply Circuit Breaker (Q138) Closed |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.BTY1502.FV01 |  | BTY1502FV01_AlmAck | BR4_Cluster1 | BPL131 | DIGITAL | %M11070 | West Turkeys Nest Valve Alarm Acknowledge |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.BTY1502.FV01 |  | BTY1502FV01_AlmEn | BR4_Cluster1 | BPL131 | DIGITAL | %M11071 | West Turkeys Nest Valve Alarm Enable |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.BTY1502.FV01 | Auto | BTY1502FV01_Aut | BR4_Cluster1 | BPL131 | DIGITAL | %M11072 | West Turkeys Nest Valve Mode Auto |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.BTY1502.FV01 |  | BTY1502FV01_AutRdy | BR4_Cluster1 | BPL131 | DIGITAL | %M11073 | West Turkeys Nest Valve Auto Ready |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.BTY1502.FV01 |  | BTY1502FV01_CIL | BR4_Cluster1 | BPL131 | DIGITAL | %M11074 | West Turkeys Nest Valve Critical Interlock Healthy |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.BTY1502.FV01 |  | BTY1502FV01_Cls | BR4_Cluster1 | BPL131 | DIGITAL | %M11075 | West Turkeys Nest Valve Close Command |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.BTY1502.FV01 |  | BTY1502FV01_Clsd | BR4_Cluster1 | BPL131 | DIGITAL | %M11076 | West Turkeys Nest Valve Closed |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.BTY1502.FV01 |  | BTY1502FV01_Clsg | BR4_Cluster1 | BPL131 | DIGITAL | %M11077 | West Turkeys Nest Valve Closing |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.BTY1502.FV01 |  | BTY1502FV01_ComOK | BR4_Cluster1 | BPL131 | DIGITAL | %M11078 | West Turkeys Nest Valve Overall Comms Healthy |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.BC02 |  | BSR131BC02CB11_I | BR4_Cluster1 | BPL131 | DIGITAL | %M1108 | BSR131 Battery Charger 2 Spare 110VDC Tripping Supply Circuit Breaker (Q141) Closed |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.BTY1502.FV01 |  | BTY1502FV01_ExcRun_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M11080 | West Turkeys Nest Valve Excessive Open Time Fault Healthy |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.BTY1502.FV01 |  | BTY1502FV01_FltSL | BR4_Cluster1 | BPL131 | DIGITAL | %M11081 | West Turkeys Nest Valve Fault Seal |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.BTY1502.FV01 |  | BTY1502FV01_FTC | BR4_Cluster1 | BPL131 | DIGITAL | %M11082 | West Turkeys Nest Valve Fail to Close |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.BTY1502.FV01 |  | BTY1502FV01_FTC_A | BR4_Cluster1 | BPL131 | DIGITAL | %M11083 | West Turkeys Nest Valve Fail to Close Alarm |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.BTY1502.FV01 |  | BTY1502FV01_FTC_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M11084 | West Turkeys Nest Valve Fail to Close Fault Healthy |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.BTY1502.FV01 |  | BTY1502FV01_FTO | BR4_Cluster1 | BPL131 | DIGITAL | %M11085 | West Turkeys Nest Valve Fail to Open |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.BTY1502.FV01 |  | BTY1502FV01_FTO_A | BR4_Cluster1 | BPL131 | DIGITAL | %M11086 | West Turkeys Nest Valve Fail to Open Alarm |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.BTY1502.FV01 |  | BTY1502FV01_FTO_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M11087 | West Turkeys Nest Valve Fail to Open Fault Healthy |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.BTY1502.FV01 |  | BTY1502FV01_LmtFlt | BR4_Cluster1 | BPL131 | DIGITAL | %M11088 | West Turkeys Nest Valve Position Fault |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.BTY1502.FV01 |  | BTY1502FV01_LmtFlt_A | BR4_Cluster1 | BPL131 | DIGITAL | %M11089 | West Turkeys Nest Valve Dual Limit Alarm |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.BC02 |  | BSR131BC02CB12_I | BR4_Cluster1 | BPL131 | DIGITAL | %M1109 | BSR131 Battery Charger 2 Spare 110VDC Tripping Supply Circuit Breaker (Q144) Closed |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.BTY1502.FV01 |  | BTY1502FV01_LmtFlt_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M11090 | West Turkeys Nest Valve Dual Limit Fault Healthy |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.BTY1502.FV01 | Local | BTY1502FV01_Loc | BR4_Cluster1 | BPL131 | DIGITAL | %M11091 | West Turkeys Nest Valve Mode Local |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.BTY1502.FV01 |  | BTY1502FV01_LocClsReq | BR4_Cluster1 | BPL131 | DIGITAL | %M11092 | West Turkeys Nest Valve Local Close Requested |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.BTY1502.FV01 |  | BTY1502FV01_LocOpnReq | BR4_Cluster1 | BPL131 | DIGITAL | %M11093 | West Turkeys Nest Valve Local Open Requested |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.BTY1502.FV01 |  | BTY1502FV01_Man | BR4_Cluster1 | BPL131 | DIGITAL | %M11094 | West Turkeys Nest Valve Mode Manual |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.BTY1502.FV01 |  | BTY1502FV01_NCIL | BR4_Cluster1 | BPL131 | DIGITAL | %M11095 | West Turkeys Nest Valve Non-Critical Interlock Healthy |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.BTY1502.FV01 |  | BTY1502FV01_NCILAlmEn | BR4_Cluster1 | BPL131 | DIGITAL | %M11096 | West Turkeys Nest Valve NCIL Alarm Enable |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.BTY1502.FV01 |  | BTY1502FV01_OOS | BR4_Cluster1 | BPL131 | DIGITAL | %M11097 | West Turkeys Nest Valve Mode Out of Service |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.BTY1502.FV01 |  | BTY1502FV01_Opn | BR4_Cluster1 | BPL131 | DIGITAL | %M11098 | West Turkeys Nest Valve Open Command |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.BTY1502.FV01 |  | BTY1502FV01_Opnd | BR4_Cluster1 | BPL131 | DIGITAL | %M11099 | West Turkeys Nest Valve Opened |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.UP01 |  | BSR131UP01XS01_I | BR4_Cluster1 | BPL131 | DIGITAL | %M1110 | BSR131 UPS UPS Surge Filter Healthy |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.BTY1502.FV01 |  | BTY1502FV01_Opng | BR4_Cluster1 | BPL131 | DIGITAL | %M11100 | West Turkeys Nest Valve Opening |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.BTY1502.FV01 |  | BTY1502FV01_PwrOK | BR4_Cluster1 | BPL131 | DIGITAL | %M11101 | West Turkeys Nest Valve Overall Power Healthy |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.BTY1502.FV01 |  | BTY1502FV01_RstRqd | BR4_Cluster1 | BPL131 | DIGITAL | %M11102 | West Turkeys Nest Valve Reset Required |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.BTY1502.FV01 |  | BTY1502FV01_SeqCls | BR4_Cluster1 | BPL131 | DIGITAL | %M11103 | West Turkeys Nest Valve Sequence Close |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.BTY1502.FV01 |  | BTY1502FV01_SeqClsSttIL | BR4_Cluster1 | BPL131 | DIGITAL | %M11104 | West Turkeys Nest Valve Sequence Close Interlock |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.BTY1502.FV01 |  | BTY1502FV01_SeqOpn | BR4_Cluster1 | BPL131 | DIGITAL | %M11105 | West Turkeys Nest Valve Sequence Open |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.BTY1502.FV01 |  | BTY1502FV01_SeqOpnSttIL | BR4_Cluster1 | BPL131 | DIGITAL | %M11106 | West Turkeys Nest Valve Sequence Open Interlock |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.BTY1502.FV01.FieldIO.CB01 |  | BTY1502FV01CB01_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M11108 | West Turkeys Nest 240VAC Flow Valve Power Circuit Breaker Open Healthy |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.UP01 |  | BSR131UP01SW01_I | BR4_Cluster1 | BPL131 | DIGITAL | %M1111 | BSR131 UPS UPS Bypassed / Test Active |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.BTY1502.FV01 |  | BTY1502FV01STS1_SysOK | BR4_Cluster1 | BPL131 | DIGITAL | %M11113 | West Turkeys Nest Valve Overall Control System Healthy |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.BTY1502.FV01 |  | BTY1502FV01XS01_A | BR4_Cluster1 | BPL131 | DIGITAL | %M11119 | West Turkeys Nest Valve Unhealthy Alarm |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.UP01 |  | BSR131UP01ZS01_I | BR4_Cluster1 | BPL131 | DIGITAL | %M1112 | BSR131 UPS UPS in Normal Mode Active |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.BTY1502.FV01 |  | BTY1502FV01XS01_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M11120 | West Turkeys Nest Valve Unhealthy Fault Healthy |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.BTY1502.FV01.FieldIO.ZT01 |  | BTY1502FV01ZT01_ChOK | BR4_Cluster1 | BPL131 | DIGITAL | %M11123 | West Turkeys Nest Flow Valve Position (%) Channel Healthy |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.BTY1502 |  | BTY1502LS01_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M11124 | West Turkeys Nest West Turkeys Nest Healthy |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC03 |  | BMC131VAMPPR1_ComFlt_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M11125 | BMC131VAMPPR1 Incomer Relay Communications Fault Healthy |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC03 |  | BMC131VAMPPR1_ProFlt_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M11126 | BMC131VAMPPR1 Vamp Arc Flash Protection Fault Healthy |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC03 |  | BMC131VAMPPR1_SysFlt_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M11127 | BMC131VAMPPR1 Vamp Arc Flash Protection Fault Healthy |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC03 |  | BPL131_CshStp_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M11128 | BPL131 NPI Hub PLC Crash Stop Healthy |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131 |  | BPL131_Def_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M11129 | NPI Hub BPL131 Default Values Not Loaded |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.DB01 |  | BSR131UP01DB01R1_I | BR4_Cluster1 | BPL131 | DIGITAL | %M1113 | BSR131 UPS Dist Board DX01 Primary 240VAC UPS Circuit Breaker (R1) Closed |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1 |  | BPP1101_2_EqpAvlFlt_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M11130 | No NPI and Process Water Pumps Available Fault Healthy |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1101 |  | BPP1101FS09_FailStp_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M11131 | BPP1101FS09 Fail to Stop Healthy |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1101 |  | BPP1101FS09_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M11132 | BPP1101FS09 Pump Flow Switch Low Healthy |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1101.FieldIO.FT03 |  | BPP1101FT03_Frz_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M11133 | BPP1101FT03 Flow Transmitter Frozen Healthy |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1101.FieldIO.FT03 |  | BPP1101FT03_Hi_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M11134 | BPP1101FT03 Flow High Healthy |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1101.FieldIO.FT03 |  | BPP1101FT03_HiHi_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M11135 | BPP1101FT03 NPI and Process Water Supply Flow High High Healthy |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1101.FieldIO.FT03 |  | BPP1101FT03_Lo_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M11136 | BPP1101FT03 Flow Low Healthy |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1101 | Closed | BPP1101IS01_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M11137 | BPP1101 Isolator Healthy |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1101.FieldIO.PT03 |  | BPP1101PT03_Frz_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M11138 | BPP1101PT03 Pump Discharge Pressure Transmitter Frozen Healthy |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1101.FieldIO.PT03 |  | BPP1101PT03_HiHi_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M11139 | BPP1101PT03 System Pressure High High Healthy |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.DB01 |  | BSR131UP01DB01W1_I | BR4_Cluster1 | BPL131 | DIGITAL | %M1114 | BSR131 UPS Dist Board DX01 Secondary 240VAC UPS Circuit Breaker (W1) Closed |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1101.FieldIO.PT03 |  | BPP1101PT03_LoLo_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M11140 | BPP1101PT03 Pump Discharge Pressure Low Low Healthy |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1101.FieldIO.PT10 |  | BPP1101PT10_Diff_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M11141 | NPI and Process Water Network Pressure Variance (PT10/PT11) Healthy |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1101.FieldIO.PT10 |  | BPP1101PT10_Frz_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M11142 | BPP1101PT10 System Pressure Frozen Healthy |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1101.FieldIO.PT10 |  | BPP1101PT10_Hi_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M11143 | BPP1101PT10 Discharge Header Pressure High Healthy |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1101.FieldIO.PT10 |  | BPP1101PT10_Lo_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M11144 | BPP1101PT10 Discharge Header Pressure Low Healthy |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1101.FieldIO.PT11 |  | BPP1101PT11_Frz_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M11145 | BPP1101PT11 Discharge Header Pressure Transmitter Frozen Healthy |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1101.FieldIO.PT11 |  | BPP1101PT11_Hi_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M11146 | BPP1101PT11 System Pressure High Healthy |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1101.FieldIO.PT11 |  | BPP1101PT11_Lo_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M11147 | BPP1101PT11 Discharge Header Pressure Low Healthy |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1101.Sub.CB01 |  | BPP1101TRP01_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M11148 | BPP1101 Main Circuit Breaker Tripped Healthy |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1101.VS01 |  | BPP1101VS01_ComFlt_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M11149 | BPP1101VS01 VSD Communications Fault Alarm |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.DB01 |  | BSR131UP01DB01B1_I | BR4_Cluster1 | BPL131 | DIGITAL | %M1115 | BSR131 UPS Dist Board NEP130 240VAC Primary UPS Circuit Breaker (B1) Closed |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1101.VS01 |  | BPP1101VS01_Flt_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M11150 | BPP1101VS01 VSD Fault Alarm |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1101.VS01 |  | BPP1101VS01SY01_Flt_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M11151 | BPP1101VS01 Safety Relay Fault Healthy |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1102 |  | BPP1102FS10_FailStp_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M11152 | BPP1102FS10 Fail to Stop Healthy |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1102 |  | BPP1102FS10_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M11153 | BPP1102FS10 Pump Flow Switch Low Healthy |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1102 | Closed | BPP1102IS01_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M11154 | BPP1102 Isolator Healthy |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1102.FieldIO.PT04 |  | BPP1102PT04_Frz_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M11155 | BPP1102PT04 Pump Discharge Pressure Transmitter Frozen Healthy |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1102.FieldIO.PT04 |  | BPP1102PT04_HiHi_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M11156 | BPP1102PT04 Pump Discharge Pressure High High Healthy |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1102.FieldIO.PT04 |  | BPP1102PT04_LoLo_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M11157 | BPP1102PT04 Pump Discharge Pressure Low Low Healthy |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1102.Sub.CB01 |  | BPP1102TRP01_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M11158 | BPP1102 Main Circuit Breaker Tripped Healthy |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1102.VS01 |  | BPP1102VS01_ComFlt_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M11159 | BPP1102VS01 VSD Communications Fault Alarm |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.DB01 |  | BSR131UP01DB01R2_I | BR4_Cluster1 | BPL131 | DIGITAL | %M1116 | BSR131 UPS Dist Board NEP130 240VAC Secondary UPS Circuit Breaker (R2) Closed |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1102.VS01 |  | BPP1102VS01_Flt_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M11160 | BPP1101VS01 VSD Fault Alarm |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1102.VS01 |  | BPP1102VS01SY01_Flt_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M11161 | BPP1102VS01 Safety Relay Fault Healthy |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT |  | BPP1103_4_5_EqpAvlFlt_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M11162 | No Transfer Pumps Available Fault Healthy |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1103 |  | BPP1103_FailStp_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M11163 | Water Transfer Pump 1 Fail to Stop Alarm Healthy |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1103.FieldIO.FT03 |  | BPP1103FT03_Frz_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M11164 | BPP1103FT03 Pump Flow Transmitter Frozen Healthy |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1103.FieldIO.FT03 |  | BPP1103FT03_LoLo_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M11165 | BPP1103FT03 Pump Flow Low Low Healthy |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1103.FieldIO.FT06 |  | BPP1103FT06_Frz_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M11166 | BPP1103FT06 Transfer Flow Transmitter Frozen Healthy |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1103.FieldIO.FT06 |  | BPP1103FT06_HiHi_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M11167 | BPP1103FT06 Transfer Flow High High Healthy |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1103.FieldIO.FT06 |  | BPP1103FT06_LkFlt_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M11168 | BPP1103FT06 Water Transfer Pipeline Leak Detected Healthy |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1103.FieldIO.FT06 |  | BPP1103FT06_RevFlw_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M11169 | BPP1103FT06 Water Transfer Pumps Reverse Flow Detected Healthy |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.DB01 |  | BSR131UP01DB01W2_I | BR4_Cluster1 | BPL131 | DIGITAL | %M1117 | BSR131 UPS Dist Board DX02 240VAC UPS Circuit Breaker (W2) Closed |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1103 | Closed | BPP1103IS01_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M11170 | BPP1103 Isolator Healthy |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1103.FieldIO.PT05 |  | BPP1103PT05_Frz_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M11171 | BPP1103PT05 Pump Discharge Pressure Transmitter Frozen Healthy |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1103.FieldIO.PT05 |  | BPP1103PT05_HiHi_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M11172 | BPP1103PT05 Pump Discharge Pressure High High Healthy |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1103.FieldIO.PT05 |  | BPP1103PT05_LoLo_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M11173 | BPP1103PT05 Pump Discharge Pressure Low Low Healthy |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1103.FieldIO.PT08 |  | BPP1103PT08_Frz_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M11174 | BPP1103PT08 Water Transfer System Pressure Transmitter Frozen Healthy |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1103.FieldIO.PT08 |  | BPP1103PT08_HiHi_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M11175 | BPP1103PT08 Transfer System Pressure High High Healthy |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1103.FieldIO.PT08 |  | BPP1103PT08_Lo_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M11176 | HME Standpipe Pump 1 PT08 Lo Healthy |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1103.Sub.CB01 |  | BPP1103TRP01_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M11177 | BPP1103 Main Circuit Breaker Tripped Healthy |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1103.VS01 |  | BPP1103VS01_ComFlt_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M11178 | BPP1103VS01 VSD Communications Fault Alarm |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1103.VS01 |  | BPP1103VS01_Flt_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M11179 | BPP1103VS01 VSD Fault Alarm |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.DB01 |  | BSR131UP01DB01B2_I | BR4_Cluster1 | BPL131 | DIGITAL | %M1118 | BSR131 UPS Dist Board DX03 240VAC UPS Circuit Breaker (B2) Closed |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1103.VS01 |  | BPP1103VS01SY01_Flt_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M11180 | BPP1103VS01 Safety Relay Fault Healthy |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1104 |  | BPP1104_FailStp_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M11181 | Water Transfer Pump 2 Fail to Stop Alarm Healthy |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1104.FieldIO.FT04 |  | BPP1104FT04_Frz_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M11182 | BPP1104FT04 Pump Flow Transmitter Frozen Healthy |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1104.FieldIO.FT04 |  | BPP1104FT04_LoLo_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M11183 | BPP1104FT04 Pump Flow Low Low Healthy |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1104 | Closed | BPP1104IS01_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M11184 | BPP1107 Isolator Healthy |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1104.FieldIO.PT06 |  | BPP1104PT06_Frz_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M11185 | BPP1104PT06 Pump Discharge Pressure Transmitter Frozen Healthy |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1104.FieldIO.PT06 |  | BPP1104PT06_HiHi_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M11186 | BPP1104PT06 Pump Discharge Pressure High High Healthy |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1104.FieldIO.PT06 |  | BPP1104PT06_LoLo_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M11187 | BPP1104PT06 Pump Discharge Pressure Low Low Healthy |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1104.Sub.CB01 |  | BPP1104TRP01_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M11188 | BPP1104 Main Circuit Breaker Tripped Healthy |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1104.VS01 |  | BPP1104VS01_ComFlt_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M11189 | BPP1104VS01 VSD Communications Fault Alarm |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.DB01 |  | BSR131UP01DB01R3_I | BR4_Cluster1 | BPL131 | DIGITAL | %M1119 | BSR131 UPS Dist Board DX04 240VAC UPS Circuit Breaker (R3) Closed |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1104.VS01 |  | BPP1104VS01_Flt_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M11190 | BPP1104VS01 VSD Fault Healthy |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1104.VS01 |  | BPP1104VS01SY01_Flt_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M11191 | BPP1104VS01 Safety Relay Fault Alarm |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1105 |  | BPP1105_FailStp_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M11192 | Water Transfer Pump 3 Fail to Stop Alarm Healthy |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1105.FieldIO.FT05 |  | BPP1105FT05_Frz_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M11193 | BPP1105FT05 Flow Transmitter Frozen Healthy |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1105.FieldIO.FT05 |  | BPP1105FT05_LoLo_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M11194 | BPP1105FT05 Pump Flow Low Low Healthy |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1105 | Closed | BPP1105IS01_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M11195 | BPP1105 Isolator Healthy |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1105.FieldIO.PT07 |  | BPP1105PT07_Frz_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M11196 | BPP1105PT07 Pump Discharge Pressure Transmitter Frozen Healthy |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1105.FieldIO.PT07 |  | BPP1105PT07_HiHi_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M11197 | BPP1105PT07 Pump Discharge Pressure High High Healthy |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1105.FieldIO.PT07 |  | BPP1105PT07_LoLo_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M11198 | BPP1105PT07 Pump Discharge Pressure Low Low Healthy |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1105.Sub.CB01 |  | BPP1105TRP01_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M11199 | BPP1105 Main Circuit Breaker Tripped Healthy |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.DB01 |  | BSR131UP01DB01W3_I | BR4_Cluster1 | BPL131 | DIGITAL | %M1120 | BSR131 UPS Dist Board HVAC Panel 240VAC UPS Circuit Breaker (W3) Closed |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1105.VS01 |  | BPP1105VS01_ComFlt_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M11200 | BPP1105 Variable Speed Drive Communications Fault Alarm |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1105.VS01 |  | BPP1105VS01_Flt_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M11201 | BPP1105VS01 VSD Fault Healthy |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1105.VS01 |  | BPP1105VS01SY01_Flt_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M11202 | BPP1105VS01 Safety Relay Fault Healthy |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1 |  | BPP1106_7_EqpAvlFlt_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M11203 | No Standpipe Pumps Available Fault Healthy |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BPP1106 |  | BPP1106_RunNoVlv_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M11204 | BPP1106 Pump Running with No Valve Open Healthy |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BPP1106 |  | BPP1106FS07_FailStp_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M11205 | BPP1106 Fail to Stop Healthy |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BPP1106 |  | BPP1106FS07_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M11206 | BPP1106FS07 Pump Flow Switch Low Healthy |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BPP1106 | Closed | BPP1106IS01_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M11207 | BPP1106 Isolator Healthy |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BPP1106.FieldIO.PT01 |  | BPP1106PT01_Frz_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M11208 | BPP1106PT01 Pump Discharge Pressure Transmitter Frozen Healthy |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BPP1106.FieldIO.PT01 |  | BPP1106PT01_HiHi_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M11209 | BPP1106PT01 Pump Discharge Pressure High High Healthy |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.DB01 |  | BSR131UP01DB01B3_I | BR4_Cluster1 | BPL131 | DIGITAL | %M1121 | BSR131 UPS Dist Board BSR131FIP01 Fire Panel 240VAC UPS Circuit Breaker (B3) Closed |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BPP1106.FieldIO.PT01 |  | BPP1106PT01_LoLo_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M11210 | BPP1106PT01 Pump Discharge Pressure Low Low Healthy |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BPP1106.Sub.CB01 |  | BPP1106TRP01_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M11211 | BPP1106 Main Circuit Breaker Tripped Healthy |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BPP1106.VS01 |  | BPP1106VS01_ComFlt_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M11212 | BPP1106VS01 VSD Communications Fault Healthy |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BPP1106.VS01 |  | BPP1106VS01_Flt_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M11213 | BPP1106VS01 VSD Fault Healthy |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BPP1106.VS01 |  | BPP1106VS01SY01_Flt_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M11214 | BPP1106VS01 Safety Relay Fault Alarm |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BPP1107 |  | BPP1107_RunNoVlv_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M11215 | BPP1107 No Standpipe Valve Available Healthy |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BPP1107 |  | BPP1107FS08_FailStp_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M11216 | BPP1107FS08 Fail to Stop Healthy |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BPP1107 |  | BPP1107FS08_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M11217 | BPP1107FS08 Pump Flow Switch Low Healthy |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BPP1107 | Closed | BPP1107IS01_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M11218 | BPP1107 Isolator Healthy |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BPP1107.FieldIO.PT02 |  | BPP1107PT02_Frz_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M11219 | BPP1107PT02 Pump Discharge Pressure Transmitter Frozen Healthy |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.DB01 |  | BSR131UP01DB01R4_I | BR4_Cluster1 | BPL131 | DIGITAL | %M1122 | BSR131 UPS Dist Board BSR131VES01 VESDA Fire Detection Panel Breaker (R4) Closed |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BPP1107.FieldIO.PT02 |  | BPP1107PT02_HiHi_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M11220 | BPP1107PT02 Pump Discharge Pressure High High Healthy |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BPP1107.FieldIO.PT02 |  | BPP1107PT02_LoLo_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M11221 | BPP1107PT02 Pump Discharge Pressure Low Low Healthy |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BPP1107.Sub.CB01 |  | BPP1107TRP01_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M11222 | BPP1107 Main Circuit Breaker Tripped Healthy |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BPP1107.VS01 |  | BPP1107VS01_ComFlt_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M11223 | BPP1107VS01 VSD Communications Fault Healthy |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BPP1107.VS01 |  | BPP1107VS01_Flt_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M11224 | BPP1107VS01 VSD Fault Healthy |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BPP1107.VS01 |  | BPP1107VS01SY01_Flt_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M11225 | BPP1107VS01 Safety Relay Fault Healthy |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.BC02.BACS |  | BSR131BC02_BACSComFlt_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M11226 | BSR131 Battery Charger BC02 BACSComFlt Healthy |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.BC02.BACS |  | BSR131BC02_BACSFlt_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M11227 | BSR131 Battery Charger BC02 BACSFlt Healthy |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.BC02.Cordex |  | BSR131BC02_CordexComFlt_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M11228 | BSR131 Battery Charger BC02 CordexComFlt Healthy |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.BC02.Cordex |  | BSR131BC02_CordexFlt_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M11229 | BSR131 Battery Charger BC02 CordexFlt Healthy |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.DB01 |  | BSR131UP01DB01W4_I | BR4_Cluster1 | BPL131 | DIGITAL | %M1123 | BSR131 UPS Dist Board Cardax 240VAC UPS Circuit Breaker (W4) Closed |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.DB01 |  | BSR131DB01XS01_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M11230 | BSR131DB01 Surge Protection (SD107) Healthy |  |  | BS1_Tags
BR4.SRV.PWR.BSR131 |  | BSR131DX01XS01_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M11231 | BSR131DX01 24VDC Power Supply 1 Healthy |  |  | BS1_Tags
BR4.SRV.PWR.BSR131 |  | BSR131DX01XS02_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M11232 | BSR131DX01 24VDC Power Supply 2 Healthy |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop01 |  | BSR131DX01DIO1PLM2_Grp2Flt_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M11233 | BSR131DX010DIO1PLM2 Group 1 Fault Healthy |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop01 |  | BSR131DX01DIO1PLM6_Ch02Flt_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M11234 | BSR131DX010DIO1PLM6 Channel 2 Fault Healthy |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop01 |  | BSR131DX01DIO1PLM6_Ch03Flt_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M11235 | BSR131DX010DIO1PLM6 Channel 3 Fault Healthy |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop01 |  | BSR131DX01DIO1PLM6_Flt_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M11236 | BSR131DX010DIO1PLM6 PLC Module Faulted Healthy |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop01 |  | BSR131DX01DIO1PLM7_Ch01Flt_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M11237 | BSR131DX010DIO1PLM7 Channel 1 Fault Healthy |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop01 |  | BSR131DX01DIO1PLM7_Flt_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M11238 | BSR131DX010DIO1PLM7 PLC Module Fault Healthy |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop01 |  | BSR131DX01DIO1PLM8_Flt_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M11239 | BSR131DX010DIO1PLM8 Fault Healthy |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.DB01 |  | BSR131UP01DB01B4_I | BR4_Cluster1 | BPL131 | DIGITAL | %M1124 | BSR131 UPS Dist Board BSR131FSS01PN01 Supression Control Panel Breaker (B4) Closed |  |  | BS1_Tags
BR4.SRV.PWR.BSR131 |  | BSR131PN01PS01_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M11240 | BSR131PN01 Switchroom Pressurisation Fan Filter Blocked Healthy |  |  | BS1_Tags
BR4.SRV.PWR.BSR131 |  | BSR131PN01XS01_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M11241 | BSR131PN01 Air Conditioner Fault Healthy |  |  | BS1_Tags
BR4.SRV.PWR.BSR131 |  | BSR131PN01XS02_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M11242 | BSR131 Switchroom Control Panel Air Conditioner Filter Blocked Healthy |  |  | BS1_Tags
BR4.SRV.PWR.BSR131 |  | BSR131PN01XS03_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M11243 | BSR131 Switchroom Control Panel Air Con 1 Healthy |  |  | BS1_Tags
BR4.SRV.PWR.BSR131 |  | BSR131PN01XS04_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M11244 | BSR131 Switchroom Control Panel Air Con 2 Healthy |  |  | BS1_Tags
BR4.SRV.PWR.BSR131 |  | BSR131PN01XS05_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M11245 | BSR131PN01 Switchroom Humidity Healthy |  |  | BS1_Tags
BR4.SRV.PWR.BSR131 |  | BSR131PN01XS06_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M11246 | NPI Hub Switchroom Control Panel 1 Air Conditioner 6 - Airlock Fault Healthy |  |  | BS1_Tags
BR4.SRV.PWR.BSR131 |  | BSR131PN01XS07_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M11247 | NPI Hub Switchroom Control Panel 1 Air Conditioner 7 - Airlock Fault Healthy |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.DB01 |  | BSR131UP01DB01B1_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M11248 | NEP130 240VAC Primary UPS Circuit Breaker Healthy |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.DB01 |  | BSR131UP01DB01B2_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M11249 | DX03 240VAC UPS Circuit Breaker Healthy |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.DB01 |  | BSR131UP01DB01R5_I | BR4_Cluster1 | BPL131 | DIGITAL | %M1125 | BSR131 UPS Dist Board BTY1502AX01 240VAC UPS Circuit Breaker (R5) Closed |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.DB01 |  | BSR131UP01DB01B3_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M11250 | BSR131FIP01 Fire Panel 240VAC UPS Circuit Breaker Healthy |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.DB01 |  | BSR131UP01DB01B4_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M11251 | BSR131FSS01PN01 Supression Control Panel Breaker Healthy |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.DB01 |  | BSR131UP01DB01R1_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M11252 | DX01 Primary 240VAC UPS Circuit Breaker Healthy |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.DB01 |  | BSR131UP01DB01R2_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M11253 | NEP130 240VAC Secondary UPS Circuit Breaker Healthy |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.DB01 |  | BSR131UP01DB01R3_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M11254 | DX04 240VAC UPS Circuit Breaker Healthy |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.DB01 |  | BSR131UP01DB01R4_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M11255 | BSR131VES01 VESDA Fire Detection Panel Breaker Healthy |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.DB01 |  | BSR131UP01DB01R5_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M11256 | BTY1502AX01 240VAC UPS Circuit Breaker Healthy |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.DB01 |  | BSR131UP01DB01W1_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M11257 | DX01 Secondary 240VAC UPS Circuit Breaker Healthy |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.DB01 |  | BSR131UP01DB01W2_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M11258 | DX02 240VAC UPS Circuit Breaker Healthy |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.DB01 |  | BSR131UP01DB01W3_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M11259 | HVAC Panel 240VAC UPS Circuit Breaker Healthy |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.DB01 |  | BSR131UP01DB01W5_I | BR4_Cluster1 | BPL131 | DIGITAL | %M1126 | BSR131 UPS Dist Board BPQE2115MC01 Potable Water 240VAC UPS Circuit Breaker (W5) Closed |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.DB01 |  | BSR131UP01DB01W4_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M11260 | Cardax 240VAC UPS Circuit Breaker Healthy |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.DB01 |  | BSR131UP01DB01W5_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M11261 | BPQE2115MC01 Potable Water 240VAC UPS Circuit Breaker Healthy |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.DB01 |  | BSR131UP01DB01XS01_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M11262 | BSR131UP01DB01 Surge Protection (SD106) Healthy |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BSTD1106.FieldIO.FT03 |  | BSTD1106FT03_Frz_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M11263 | BSTD1106FT03 Flow Transmitter Frozen Healthy |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BSTD1106.FieldIO.FT03 |  | BSTD1106FT03_Hi_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M11264 | BPP1103FT03 Pump Flow High Healthy |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BSTD1106.FieldIO.FT03 |  | BSTD1106FT03_Lo_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M11265 | BSTD1106FT03 Flow Low Healthy |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BSTD1106.FieldIO.FT03 |  | BSTD1106FT03_Rtn_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M11266 | BSTD1106FT03 Flow Detected with Valve Closed Healthy |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BSTD1106.FV03 |  | BSTD1106FV03_LocFlt_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M11267 | West Turkeys Nest LME Standpipe Valve Left in Local Healthy |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BSTD1107 |  | BSTD1107FT02_Frz_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M11268 | BSTD1107FT02 Flow Transmitter Frozen Healthy |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BSTD1107 |  | BSTD1107FT02_Hi_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M11269 | BSTD1107FT02 Flow High Healthy |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.DB01 |  | BSR131UP01DB01B5_I | BR4_Cluster1 | BPL131 | DIGITAL | %M1127 | BSR131 UPS Dist Board Spare Circuit Breaker (B5) Closed |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BSTD1107 |  | BSTD1107FT02_Lo_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M11270 | BSTD1107FT02 Flow Low Healthy |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BSTD1107 |  | BSTD1107FT02_Rtn_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M11271 | BSTD1107FT02 Flow Detected with Valve Closed Healthy |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BSTD1107.FV02 |  | BSTD1107FV02_LocFlt_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M11272 | West Turkeys Nest HME Standpipe Valve Valve Left in Local Healthy |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.P3FIREWATER.BTK2101.FieldIO.LT01 |  | BTK2101LT01_Hi_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M11273 | BTK2101LT01 Hi Healthy |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.P3FIREWATER.BTK2101.FieldIO.LT01 |  | BTK2101LT01_HiHi_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M11274 | NPI Fire Water Tank 1 LT01 Level High High Healthy |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.P3FIREWATER.BTK2101.FieldIO.LT01 |  | BTK2101LT01_Lo_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M11275 | NPI Fire Water Tank 1 LT01 Level Low Healthy |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.P3FIREWATER.BTK2101.FieldIO.LT01 |  | BTK2101LT01_LoLo_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M11276 | BTK2101LT01 Tank Level Low Low Healthy |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.P3FIREWATER.BTK2102.FieldIO.LT01 |  | BTK2102LT01_Hi_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M11277 | BTK2102LT01 Hi Healthy |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.P3FIREWATER.BTK2102.FieldIO.LT01 |  | BTK2102LT01_HiHi_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M11278 | BTK2101LT01 Tank Level High High Healthy |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.P3FIREWATER.BTK2102.FieldIO.LT01 |  | BTK2102LT01_Lo_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M11279 | BTK2101LT01 Tank Level Low Low Healthy |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.DB01 |  | BSR131UP01DB01R6_I | BR4_Cluster1 | BPL131 | DIGITAL | %M1128 | BSR131 UPS Dist Board Spare Circuit Breaker (R6) Closed |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.P3FIREWATER.BTK2102.FieldIO.LT01 |  | BTK2102LT01_LoLo_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M11280 | BTK2101LT01 Tank Level Low Low Healthy |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.P3FIREWATER.BTK2102.FieldIO.LT01 |  | BTY1501LT01_LoLo_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M11281 | BTY1502LT01 Turkeys Nest Level Low Low Healthy |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.BTY1502.FieldIO.FT02 |  | BTY1502FT02_Flt_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M11282 | BTY1502FT02 West Turkeys Nest Recirculation Flow Fault Healthy |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.BTY1502.FieldIO.FT02 |  | BTY1502FT02_Frz_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M11283 | BTY1502FT02 Flow Transmitter Frozen Healthy |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.BTY1502.FieldIO.FT02 |  | BTY1502FT02_Hi_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M11284 | BTY1502FT02 Recirculation Flow High Healthy |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.BTY1502.FieldIO.FT02 |  | BTY1502FT02_Lo_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M11285 | East Turkeys Nest Raw Water Remote Mode FT02 Lo Healthy |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.BTY1502.FV01 |  | BTY1502FV01_LocFlt_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M11286 | BTY1502FV01 Valve Left in Local Healthy |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.BTY1502.FieldIO.LT01 |  | BTY1502LT01_Frz_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M11287 | BTY1502 Level Transmitter Freeze Healthy |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.BTY1502.FieldIO.LT01 |  | BTY1502LT01_Hi_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M11288 | BTY1502LT01 West Turkeys Nest Level High Healthy |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.BTY1502.FieldIO.LT01 |  | BTY1502LT01_HiHi_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M11289 | BTY1502LT01 West Turkeys Nest Level High High Healthy |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.DB01 |  | BSR131UP01DB01W6_I | BR4_Cluster1 | BPL131 | DIGITAL | %M1129 | BSR131 UPS Dist Board Spare Circuit Breaker (W6) Closed |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.BTY1502.FieldIO.LT01 |  | BTY1502LT01_Lo_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M11290 | BTY1502LT01 West Turkeys Nest Level Low Healthy |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.BTY1502.FieldIO.LT01 |  | BTY1502LT01_LoLo_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M11291 | BTY1502LT01 Turkeys Nest Level Low Low Healthy |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.BTY1502.FieldIO.LT01 |  | BTY1502LT01_SigFlt_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M11292 | BTY1502LT01 Level Discrepancy Fault Healthy |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.BTY1502.FieldIO.LT02 |  | BTY1502LT02_Frz_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M11293 | East Turkeys Nest Raw Water Remote Mode LT02 Freeze Healthy |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.BTY1502.FieldIO.LT02 |  | BTY1502LT02_Hi_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M11294 | BTY1502LT02 West Turkeys Nest Level High Healthy |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.BTY1502.FieldIO.LT02 |  | BTY1502LT02_HiHi_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M11295 | BTY1502LT02 West Turkeys Nest High High Healthy |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.BTY1502.FieldIO.LT02 |  | BTY1502LT02_Lo_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M11296 | BTY1502LT02 West Turkeys Nest Low Healthy |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.BTY1502.FieldIO.LT02 |  | BTY1502LT02_LoLo_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M11297 | BTK2101LT02 NPI Fire Water Tank Level Low Low Healthy |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.BTY1502.FieldIO.LT02 |  | BTY1502LT02_SigFlt_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M11298 | BTY1502LT02 West Turkeys Nest Signal Fault Healthy |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.BTY1502.FieldIO.PT01 |  | BTY1502PT01_Hi_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M11299 | BTY1502PT01 WTN East Collection Header In Flow Pressure High Alarm Healhy |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.DB01 |  | BSR131UP01DB01B6_I | BR4_Cluster1 | BPL131 | DIGITAL | %M1130 | BSR131 UPS Dist Board Spare Circuit Breaker (B6) Closed |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.BTY1502.FieldIO.PT01 |  | BTY1502PT01_Lo_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M11300 | BTY1502PT01 WTN East Collection Header In Flow Pressure Low Healthy |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.BTY1502.FieldIO.PT03 |  | BTY1502PT03_Hi_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M11301 | BTY1502PT03 WTN West Collection Header In Flow Pressure High Healthy |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.BTY1502.FieldIO.LT01 |  | BTY1502LT01_ChOK | BR4_Cluster1 | BPL131 | DIGITAL | %M11302 | West Turkeys Nest Level 1 (mm) Channel Healthy |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.BTY1502.FieldIO.LT02 |  | BTY1502LT02_ChOK | BR4_Cluster1 | BPL131 | DIGITAL | %M11303 | West Turkeys Nest Level 2 (mm) Channel Healthy |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.BTY1502.FieldIO.PT01 |  | BTY1502PT01_ChOK | BR4_Cluster1 | BPL131 | DIGITAL | %M11304 | West Turkeys Nest Pressure (kPa) Channel Healthy |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.BTY1502.FieldIO.PT03 |  | BTY1502PT03_ChOK | BR4_Cluster1 | BPL131 | DIGITAL | %M11305 | West Turkeys Nest Pressure (kPa) Channel Healthy |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.DB01 |  | BSR131UP01DB01R7_I | BR4_Cluster1 | BPL131 | DIGITAL | %M1131 | BSR131 UPS Dist Board Spare Circuit Breaker (R7) Closed |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.DB01 |  | BSR131UP01DB01W7_I | BR4_Cluster1 | BPL131 | DIGITAL | %M1132 | BSR131 UPS Dist Board Spare Circuit Breaker (W7) Closed |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.DB01 |  | BSR131UP01DB01B7_I | BR4_Cluster1 | BPL131 | DIGITAL | %M1133 | BSR131 UPS Dist Board Spare Circuit Breaker (B7) Closed |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.DB01 |  | BSR131UP01DB01R8_I | BR4_Cluster1 | BPL131 | DIGITAL | %M1134 | BSR131 UPS Dist Board Spare Circuit Breaker (R8) Closed |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.DB01 |  | BSR131UP01DB01W8_I | BR4_Cluster1 | BPL131 | DIGITAL | %M1135 | BSR131 UPS Dist Board Spare Circuit Breaker (W8) Closed |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.DB01 |  | BSR131UP01DB01B8_I | BR4_Cluster1 | BPL131 | DIGITAL | %M1136 | BSR131 UPS Dist Board Spare Circuit Breaker (B8) Closed |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop01 |  | BSR131DX01VDC01_I | BR4_Cluster1 | BPL131 | DIGITAL | %M1137 | BSR131 DIO Box 1 DX01 24VDC Control Supply Healthy (Q110) Healthy |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop01 |  | BSR131DX01VDC02_I | BR4_Cluster1 | BPL131 | DIGITAL | %M1138 | BSR131 DIO Box 1 DX01 24VDC Output Module Control Supply (Q170) Healthy |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.UP01 |  | BSR131DX01VDC03_I | BR4_Cluster1 | BPL131 | DIGITAL | %M1139 | BSR131 DIO Box 1 BSR131UP01 24VDC Control Supply (Q254) Healthy |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.BC01 |  | BSR131DX01VDC04_I | BR4_Cluster1 | BPL131 | DIGITAL | %M1140 | BSR131 DIO Box 1 BSR131BC01DB01 24VDC Control Supply (Q257) Healthy |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.BC02 |  | BSR131DX01VDC05_I | BR4_Cluster1 | BPL131 | DIGITAL | %M1141 | BSR131 DIO Box 1 BSR131BC02DB01 24VDC Control Supply (Q260) Healthy |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.DB01 |  | BSR131DX01VDC06_I | BR4_Cluster1 | BPL131 | DIGITAL | %M1142 | BSR131 DIO Box 1 BSR131UP01DB01 24VDC Control Supply (Q263) Healthy |  |  | BS1_Tags
BR4.SRV.PWR.BSR131 |  | BSR131DX01VDC07_I | BR4_Cluster1 | BPL131 | DIGITAL | %M1143 | BSR131 DIO Box 1 Misc Switchroom Alarms 24VDC Control Supply (Q266) Healthy |  |  | BS1_Tags
BR4.SRV.PWR.BSR131 |  | BSR131DX01VDC08_I | BR4_Cluster1 | BPL131 | DIGITAL | %M1144 | BSR131 DIO Box 1 Spare (Q269) Healthy |  |  | BS1_Tags
BR4.SRV.PWR.BSR131 |  | BSR131DX01VDC09_I | BR4_Cluster1 | BPL131 | DIGITAL | %M1145 | BSR131 DIO Box 1 Spare (Q272) Healthy |  |  | BS1_Tags
BR4.SRV.PWR.BSR131 |  | BSR131DX01VDC10_I | BR4_Cluster1 | BPL131 | DIGITAL | %M1146 | BSR131 DIO Box 1 Spare (Q275) Healthy |  |  | BS1_Tags
BR4.SRV.PWR.BSR131 |  | BSR131DX01VDC11_I | BR4_Cluster1 | BPL131 | DIGITAL | %M1147 | BSR131 DIO Box 1 Spare (Q278) Healthy |  |  | BS1_Tags
BR4.SRV.PWR.BSR131 |  | BSR131DX01VDC12_I | BR4_Cluster1 | BPL131 | DIGITAL | %M1148 | BSR131 DIO Box 1 Spare (Q281) Healthy |  |  | BS1_Tags
BR4.SRV.PWR.BSR131 |  | BSR131FIP01XS03_I | BR4_Cluster1 | BPL131 | DIGITAL | %M1149 | BSR131 Fire Panel Substation Gas Discharged |  |  | BS1_Tags
BR4.SRV.PWR.BSR131 |  | BSR131PB01_I | BR4_Cluster1 | BPL131 | DIGITAL | %M1150 | NPI Hub Substation BSR131 Shutdown Pushbutton (SESP) Healthy |  |  | BS1_Tags
BR4.SRV.PWR.BSR131 |  | BSR131DX01XS01_I | BR4_Cluster1 | BPL131 | DIGITAL | %M1151 | BSR131 DIO Box 1 DX01 24VDC Power Supply 1 (U103A) Healthy |  |  | BS1_Tags
BR4.SRV.PWR.BSR131 |  | BSR131DX01XS02_I | BR4_Cluster1 | BPL131 | DIGITAL | %M1152 | BSR131 DIO Box 1 DX01 24VDC Power Supply 2 (U103B) Healthy |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.NEP01 |  | BSR131NEP01CB01_I | BR4_Cluster1 | BPL131 | DIGITAL | %M1153 | BSR131 Network Panel 1 NEP Primary PDU Circuit Breaker (Q130) Healthy |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.NEP01 |  | BSR131NEP01CB02_I | BR4_Cluster1 | BPL131 | DIGITAL | %M1154 | BSR131 Network Panel 1 NEP Secondary PDU Circuit Breaker (Q180) Healthy |  |  | BS1_Tags
BR4.SRV.PWR.BSR131 |  | BSR131FIP01XS01_I | BR4_Cluster1 | BPL131 | DIGITAL | %M1155 | BSR131 Fire Panel Fire Panel Healthy |  |  | BS1_Tags
BR4.SRV.PWR.BSR131 |  | BSR131FIP01IS01_I | BR4_Cluster1 | BPL131 | DIGITAL | %M1156 | BSR131 Fire Panel Fire Panel Isolated Healthy |  |  | BS1_Tags
BR4.SRV.PWR.BSR131 |  | BSR131FIP01XS02_I | BR4_Cluster1 | BPL131 | DIGITAL | %M1157 | BSR131 Fire Panel Fire Alarm Healthy |  |  | BS1_Tags
BR4.SRV.PWR.BSR131 |  | BSR131PN01TS01_I | BR4_Cluster1 | BPL131 | DIGITAL | %M1158 | Switchroom Control Panel Airlock High Temperature Alarm |  |  | BS1_Tags
BR4.SRV.PWR.BSR131 |  | BSR131PN01TS02_I | BR4_Cluster1 | BPL131 | DIGITAL | %M1159 | Switchroom Control Panel Fixed Plant Room High Temperature Alarm |  |  | BS1_Tags
BR4.SRV.PWR.BSR131 |  | BSR131PN01PS01_I | BR4_Cluster1 | BPL131 | DIGITAL | %M1160 | Switchroom Control Panel Switchroom Pressurisation Fan Filter Healthy |  |  | BS1_Tags
BR4.SRV.PWR.BSR131 |  | BSR131PN01XS01_I | BR4_Cluster1 | BPL131 | DIGITAL | %M1161 | Switchroom Control Panel Air Conditioner Healthy |  |  | BS1_Tags
BR4.SRV.PWR.BSR131 |  | BSR131PN01XS02_I | BR4_Cluster1 | BPL131 | DIGITAL | %M1162 | Switchroom Control Panel Air Conditioner Filter Blocked Alarm |  |  | BS1_Tags
BR4.SRV.PWR.BSR131 |  | BSR131PN01XS03_I | BR4_Cluster1 | BPL131 | DIGITAL | %M1163 | Switchroom Control Panel Air Conditioner 1 - Fixed Plant Room Fault Alarm |  |  | BS1_Tags
BR4.SRV.PWR.BSR131 |  | BSR131PN01XS04_I | BR4_Cluster1 | BPL131 | DIGITAL | %M1164 | Switchroom Control Panel Air Conditioner 2 - Fixed Plant Room Fault Alarm |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.DB01 |  | BSR131DB01XS01_I | BR4_Cluster1 | BPL131 | DIGITAL | %M1165 | BSR131 LSP Dist Board BSR131DB01 Surge Protection (SD106) Healthy |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.DB01 |  | BSR131UP01DB01XS01_I | BR4_Cluster1 | BPL131 | DIGITAL | %M1166 | BSR131 UPS Dist Board BSR131UP01DB01 Surge Protection (SD106) Healthy |  |  | BS1_Tags
BR4.SRV.PWR.BSR131 |  | BSR131PN01XS06_I | BR4_Cluster1 | BPL131 | DIGITAL | %M1167 | Switchroom Control Panel Air Conditioner 6 - Airlock Fault Alarm |  |  | BS1_Tags
BR4.SRV.PWR.BSR131 |  | BSR131PN01XS07_I | BR4_Cluster1 | BPL131 | DIGITAL | %M1168 | Switchroom Control Panel Air Conditioner 7 - Airlock Fault Alarm |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC01 |  | BMC131INC01VDC01_I | BR4_Cluster1 | BPL131 | DIGITAL | %M1169 | BMC131 Process Bus Incomer 24VDC Control Supply (Q267) Healthy |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC01 |  | BMC131INC01CB02_I | BR4_Cluster1 | BPL131 | DIGITAL | %M1170 | BMC131 Process Bus Incomer Arc Flash Supply (Q204) Healthy |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC01.VAMP |  | BMC131INC01TRP02_I | BR4_Cluster1 | BPL131 | DIGITAL | %M1171 | BMC131 Process Bus Incomer Arc Flash Trip Alarm (F113) Healthy |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC01.VAMP |  | BMC131INC01XS02_I | BR4_Cluster1 | BPL131 | DIGITAL | %M1172 | BMC131 Process Bus Incomer Arc Flash Relay Self Supervision (F113) Healthy |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC01 |  | BMC131INC01CB03_I | BR4_Cluster1 | BPL131 | DIGITAL | %M1173 | BMC131 Process Bus Incomer Incomer Circuit Breaker Spring Charge Supply (Q212) OK |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC01 |  | BMC131INC01CB04_I | BR4_Cluster1 | BPL131 | DIGITAL | %M1174 | BMC131 Process Bus Incomer Incomer Circuit Breaker Trip Supply (Q220) OK |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC01 |  | BMC131INC01CB05_I | BR4_Cluster1 | BPL131 | DIGITAL | %M1175 | BMC131 Process Bus Incomer Incomer Circuit Breaker 24VDC Cubicle Bus Supply (Q256) Healthy |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC01 |  | BMC131INC01XS03_I | BR4_Cluster1 | BPL131 | DIGITAL | %M1176 | BMC131 Process Bus Incomer Surge Protection Relay (SD144-146) Healthy |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC01 |  | BMC131INC01CB06_I | BR4_Cluster1 | BPL131 | DIGITAL | %M1177 | BMC131 Process Bus Incomer 110VDC/24VDC Power Supply (Q215) Healthy |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC01 |  | BMC131INC01TRP03_I | BR4_Cluster1 | BPL131 | DIGITAL | %M1178 | BMC131 Process Bus Incomer Upstream Intertrip (K294) Active |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC02 |  | BMC131INC02VDC01_I | BR4_Cluster1 | BPL131 | DIGITAL | %M1179 | BMC131 Essential Bus Incomer 24VDC Control Supply (Q267) Healthy |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC02 |  | BMC131INC02CB03_I | BR4_Cluster1 | BPL131 | DIGITAL | %M1180 | BMC131 Essential Bus Incomer Incomer Circuit Breaker Spring Charge Supply (Q212) OK |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC02 |  | BMC131INC02CB04_I | BR4_Cluster1 | BPL131 | DIGITAL | %M1181 | BMC131 Essential Bus Incomer Incomer Circuit Breaker Trip Supply (Q220) OK |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC02 |  | BMC131INC02CB05_I | BR4_Cluster1 | BPL131 | DIGITAL | %M1182 | BMC131 Essential Bus Incomer Incomer Circuit Breaker 24VDC Cubicle Bus Supply (Q256) Healthy |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC02 |  | BMC131INC02XS03_I | BR4_Cluster1 | BPL131 | DIGITAL | %M1183 | BMC131 Essential Bus Incomer Surge Protection Relay (SD144-146) Healthy |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC02 |  | BMC131INC02CB06_I | BR4_Cluster1 | BPL131 | DIGITAL | %M1184 | BMC131 Essential Bus Incomer 110VDC/24VDC Power Supply (Q215) Healthy |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC03 |  | BMC131INC03VDC01_I | BR4_Cluster1 | BPL131 | DIGITAL | %M1185 | BMC131 Generator Bus Incomer 24VDC Control Supply (Q267) Healthy |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC03 |  | BMC131INC03TRP02_I | BR4_Cluster1 | BPL131 | DIGITAL | %M1186 | BMC131 Generator Bus Incomer Arc Flash Trip Alarm (F110) Healthy |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC03 |  | BMC131INC03CB03_I | BR4_Cluster1 | BPL131 | DIGITAL | %M1187 | BMC131 Generator Bus Incomer Incomer Circuit Breaker Spring Charge Supply (Q212) OK |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC03 |  | BMC131INC03CB04_I | BR4_Cluster1 | BPL131 | DIGITAL | %M1188 | BMC131 Generator Bus Incomer Incomer Circuit Breaker Trip Supply (Q220) OK |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC03 |  | BMC131INC03CB05_I | BR4_Cluster1 | BPL131 | DIGITAL | %M1189 | BMC131 Generator Bus Incomer Incomer Circuit Breaker 24VDC Cubicle Bus Supply (Q256) Healthy |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC03 |  | BMC131INC03CB06_I | BR4_Cluster1 | BPL131 | DIGITAL | %M1190 | BMC131 Generator Bus Incomer Arc Flash Expansion Module 24VDC Supply (Q258) Healthy |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC03 |  | BMC131INC03CB07_I | BR4_Cluster1 | BPL131 | DIGITAL | %M1191 | BMC131 Generator Bus Incomer 110VDC/24VDC Power Supply (Q215) Healthy |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.P3FIREWATER.BPQE2101.Sub.PN01 |  | BPQE2101PN01VDC01_I | BR4_Cluster1 | BPL131 | DIGITAL | %M1192 | NPI & Primary Crushing Fire Water Container Panel 24VDC Control Supply (Q155) Healthy |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.P3FIREWATER.BPQE2101.Sub.PN01.CB01 |  | BPQE2101PN01CB01_I | BR4_Cluster1 | BPL131 | DIGITAL | %M1193 | NPI & Primary Crushing Fire Water Container Panel Main Circuit Breaker (Q103) Closed |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.P3FIREWATER.BPQE2101.Sub.PN01.CB01 |  | BPQE2101PN01TRP01_I | BR4_Cluster1 | BPL131 | DIGITAL | %M1194 | NPI & Primary Crushing Fire Water Container Panel Main Circuit Breaker (Q103) Tripped |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.P3FIREWATER.BPQE2101.Sub.DB01 |  | BPQE2101DB01VDC01_I | BR4_Cluster1 | BPL131 | DIGITAL | %M1195 | NPI & Primary Crusher Fire Water Pump Dist Board 24VDC Control Supply (Q155) Healthy |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.P3FIREWATER.BPQE2101.Sub.DB01.CB01 |  | BPQE2101DB01CB01_I | BR4_Cluster1 | BPL131 | DIGITAL | %M1196 | NPI & Primary Crusher Fire Water Pump Dist Board Main Circuit Breaker (Q103) Closed |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.P3FIREWATER.BPQE2101.Sub.DB01.CB01 |  | BPQE2101DB01TRP01_I | BR4_Cluster1 | BPL131 | DIGITAL | %M1197 | NPI & Primary Crusher Fire Water Pump Dist Board Main Circuit Breaker (Q103) Tripped |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.BC01 |  | BSR131BC01VDC01_I | BR4_Cluster1 | BPL131 | DIGITAL | %M1198 | BSR131 Battery Charger 1 24VDC Control Supply (Q155) Healthy |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.BC01.CB01 |  | BSR131BC01CB01_I | BR4_Cluster1 | BPL131 | DIGITAL | %M1199 | BSR131 Battery Charger 1 Main Circuit Breaker (Q103) Closed |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.BC01.CB01 |  | BSR131BC01TRP01_I | BR4_Cluster1 | BPL131 | DIGITAL | %M1200 | BSR131 Battery Charger 1 Main Circuit Breaker (Q103) Tripped |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.BC02 |  | BSR131BC02VDC01_I | BR4_Cluster1 | BPL131 | DIGITAL | %M1201 | BSR131 Battery Charger 2 24VDC Control Supply (Q155) Healthy |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.BC02.CB01 |  | BSR131BC02CB01_I | BR4_Cluster1 | BPL131 | DIGITAL | %M1202 | BSR131 Battery Charger 2 Main Circuit Breaker (Q103) Closed |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.BC02.CB01 |  | BSR131BC02TRP01_I | BR4_Cluster1 | BPL131 | DIGITAL | %M1203 | BSR131 Battery Charger 2 Main Circuit Breaker (Q103) Tripped |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.UP01 |  | BSR131UP01VDC01_I | BR4_Cluster1 | BPL131 | DIGITAL | %M1204 | BSR131 UPS 24VDC Control Supply (Q155) Healthy |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.CB01 |  | BSR131UP01CB01_I | BR4_Cluster1 | BPL131 | DIGITAL | %M1205 | BSR131 UPS Main Circuit Breaker (Q103) Closed |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.CB01 |  | BSR131UP01TRP01_I | BR4_Cluster1 | BPL131 | DIGITAL | %M1206 | BSR131 UPS Main Circuit Breaker (Q103) Tripped |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.AC01 |  | BSR131AC01VDC01_I | BR4_Cluster1 | BPL131 | DIGITAL | %M1207 | BSR131 Aircon 1 24VDC Control Supply (Q155) Healthy |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.AC01.CB01 |  | BSR131AC01CB01_I | BR4_Cluster1 | BPL131 | DIGITAL | %M1208 | BSR131 Aircon 1 Main Circuit Breaker (Q103) Closed |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.AC01.CB01 |  | BSR131AC01TRP01_I | BR4_Cluster1 | BPL131 | DIGITAL | %M1209 | BSR131 Aircon 1 Main Circuit Breaker (Q103) Tripped |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.AC02 |  | BSR131AC02VDC01_I | BR4_Cluster1 | BPL131 | DIGITAL | %M1210 | BSR131 Aircon 2 24VDC Control Supply (Q155) Healthy |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.AC02.CB01 |  | BSR131AC02CB01_I | BR4_Cluster1 | BPL131 | DIGITAL | %M1211 | BSR131 Aircon 2 Main Circuit Breaker (Q103) Closed |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.AC02.CB01 |  | BSR131AC02TRP01_I | BR4_Cluster1 | BPL131 | DIGITAL | %M1212 | BSR131 Aircon 2 Main Circuit Breaker (Q103) Tripped |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.DB01 |  | BSR131DB01VDC01_I | BR4_Cluster1 | BPL131 | DIGITAL | %M1213 | BSR131 LSP Dist Board 24VDC Control Supply (Q155) Healthy |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.DB01.CB01 |  | BSR131DB01CB01_I | BR4_Cluster1 | BPL131 | DIGITAL | %M1214 | BSR131 LSP Dist Board Main Circuit Breaker (Q103) Closed |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.DB01.CB01 |  | BSR131DB01TRP01_I | BR4_Cluster1 | BPL131 | DIGITAL | %M1215 | BSR131 LSP Dist Board Main Circuit Breaker (Q103) Tripped |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.DB02 |  | BSR131DB02VDC01_I | BR4_Cluster1 | BPL131 | DIGITAL | %M1216 | BSR131 415V Dewatering Laydown Lighting Dist Board 24VDC Control Supply (Q155) Healthy |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.DB02.CB01 |  | BSR131DB02CB01_I | BR4_Cluster1 | BPL131 | DIGITAL | %M1217 | BSR131 415V Dewatering Laydown Lighting Dist Board Main Circuit Breaker (Q103) Closed |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.DB02.CB01 |  | BSR131DB02TRP01_I | BR4_Cluster1 | BPL131 | DIGITAL | %M1218 | BSR131 415V Dewatering Laydown Lighting Dist Board Main Circuit Breaker (Q103) Tripped |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.DB03 |  | BSR131DB03VDC01_I | BR4_Cluster1 | BPL131 | DIGITAL | %M1219 | BSR131 415V HME Refuel Water Recycle Dist Board 24VDC Control Supply (Q155) Healthy |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.DB03.CB01 |  | BSR131DB03CB01_I | BR4_Cluster1 | BPL131 | DIGITAL | %M1220 | BSR131 415V HME Refuel Water Recycle Dist Board Main Circuit Breaker (Q103) Closed |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.DB03.CB01 |  | BSR131DB03TRP01_I | BR4_Cluster1 | BPL131 | DIGITAL | %M1221 | BSR131 415V HME Refuel Water Recycle Dist Board Main Circuit Breaker (Q103) Tripped |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.P3POTWATER.BPQE2115.Sub.DB01 |  | BPQE2115MC01VDC01_I | BR4_Cluster1 | BPL131 | DIGITAL | %M1222 | Potable Water MCC 24VDC Control Supply (PWTP) (Q155) Healthy |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.P3POTWATER.BPQE2115.Sub.DB01.CB01 |  | BPQE2115MC01CB01_I | BR4_Cluster1 | BPL131 | DIGITAL | %M1223 | Potable Water MCC Main Circuit Breaker (PWTP) (Q103) Closed |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.P3POTWATER.BPQE2115.Sub.DB01.CB01 |  | BPQE2115MC01TRP01_I | BR4_Cluster1 | BPL131 | DIGITAL | %M1224 | Potable Water MCC Main Circuit Breaker (PWTP) (Q103) Tripped |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.BMC1311 |  | BMC1311VDC01_I | BR4_Cluster1 | BPL131 | DIGITAL | %M1225 | HME Refuelling MCC 24VDC Control Supply (Q155) Healthy |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.BMC1311.Sub.CB01 |  | BMC1311CB01_I | BR4_Cluster1 | BPL131 | DIGITAL | %M1226 | HME Refuelling MCC Main Circuit Breaker (Q103) Closed |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.BMC1311.Sub.CB01 |  | BMC1311TRP01_I | BR4_Cluster1 | BPL131 | DIGITAL | %M1227 | HME Refuelling MCC Main Circuit Breaker (Q103) Tripped |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1101 |  | BPP1101VDC01_I | BR4_Cluster1 | BPL131 | DIGITAL | %M1228 | Production Plant and NPI Water Supply Pump 1 24VDC Control Supply (Q155) Healthy |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1101 |  | BPP1101SYS01_I | BR4_Cluster1 | BPL131 | DIGITAL | %M1229 | Production Plant and NPI Water Supply Pump 1 Safety Relay (K161) Healthy |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1101.Sub.CB01 |  | BPP1101CB01_I | BR4_Cluster1 | BPL131 | DIGITAL | %M1230 | Production Plant and NPI Water Supply Pump 1 Main Circuit Breaker (Q103) Closed |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1101.Sub.CB01 |  | BPP1101TRP01_I | BR4_Cluster1 | BPL131 | DIGITAL | %M1231 | Production Plant and NPI Water Supply Pump 1 Main Circuit Breaker (Q103) Tripped |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1102 |  | BPP1102VDC01_I | BR4_Cluster1 | BPL131 | DIGITAL | %M1232 | Production Plant and NPI Water Supply Pump 2 24VDC Control Supply (Q155) Healthy |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1102 |  | BPP1102SYS01_I | BR4_Cluster1 | BPL131 | DIGITAL | %M1233 | Production Plant and NPI Water Supply Pump 2 Safety Relay (K161) Healthy |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1102.Sub.CB01 |  | BPP1102CB01_I | BR4_Cluster1 | BPL131 | DIGITAL | %M1234 | Production Plant and NPI Water Supply Pump 2 Main Circuit Breaker (Q103) Tripped |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1102.Sub.CB01 |  | BPP1102TRP01_I | BR4_Cluster1 | BPL131 | DIGITAL | %M1235 | Production Plant and NPI Water Supply Pump 2 Main Circuit Breaker (Q103) Healthy |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1103 |  | BPP1103VDC01_I | BR4_Cluster1 | BPL131 | DIGITAL | %M1236 | Water Transfer Pump 1 24VDC Control Supply (Q155) Healthy |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1103 |  | BPP1103SYS01_I | BR4_Cluster1 | BPL131 | DIGITAL | %M1237 | Water Transfer Pump 1 Safety Relay (K161) Healthy |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1103.Sub.CB01 |  | BPP1103CB01_I | BR4_Cluster1 | BPL131 | DIGITAL | %M1238 | Water Transfer Pump 1 Main Circuit Breaker (Q103) Closed |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1103.Sub.CB01 |  | BPP1103TRP01_I | BR4_Cluster1 | BPL131 | DIGITAL | %M1239 | Water Transfer Pump 1 Main Circuit Breaker (Q103) Tripped |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1104 |  | BPP1104VDC01_I | BR4_Cluster1 | BPL131 | DIGITAL | %M1240 | Water Transfer Pump 2 24VDC Control Supply (Q155) Healthy |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1104 |  | BPP1104SYS01_I | BR4_Cluster1 | BPL131 | DIGITAL | %M1241 | Water Transfer Pump 2 Safety Relay (K161) Healthy |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1104.Sub.CB01 |  | BPP1104CB01_I | BR4_Cluster1 | BPL131 | DIGITAL | %M1242 | Water Transfer Pump 2 Main Circuit Breaker (Q103) Tripped |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1104.Sub.CB01 |  | BPP1104TRP01_I | BR4_Cluster1 | BPL131 | DIGITAL | %M1243 | Water Transfer Pump 2 Main Circuit Breaker (Q103) Healthy |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1105 |  | BPP1105VDC01_I | BR4_Cluster1 | BPL131 | DIGITAL | %M1244 | Water Transfer Pump 3 24VDC Control Supply (Q155) Healthy |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1105 |  | BPP1105SYS01_I | BR4_Cluster1 | BPL131 | DIGITAL | %M1245 | Water Transfer Pump 3 Safety Relay (K161) Healthy |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1105.Sub.CB01 |  | BPP1105CB01_I | BR4_Cluster1 | BPL131 | DIGITAL | %M1246 | Water Transfer Pump 3 Main Circuit Breaker (Q103) Closed |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1105.Sub.CB01 |  | BPP1105TRP01_I | BR4_Cluster1 | BPL131 | DIGITAL | %M1247 | Water Transfer Pump 3 Main Circuit Breaker (Q103) Tripped |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BPP1106 |  | BPP1106VDC01_I | BR4_Cluster1 | BPL131 | DIGITAL | %M1248 | HME & LME Standpipe Pump 3 24VDC Control Supply (Q155) Healthy |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BPP1106 |  | BPP1106SYS01_I | BR4_Cluster1 | BPL131 | DIGITAL | %M1249 | HME & LME Standpipe Pump 3 Safety Relay (K161) Healthy |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BPP1106.Sub.CB01 |  | BPP1106CB01_I | BR4_Cluster1 | BPL131 | DIGITAL | %M1250 | HME & LME Standpipe Pump 3 Main Circuit Breaker (Q103) Tripped |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BPP1106.Sub.CB01 |  | BPP1106TRP01_I | BR4_Cluster1 | BPL131 | DIGITAL | %M1251 | HME & LME Standpipe Pump 3 Main Circuit Breaker (Q103) Healthy |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BPP1107 |  | BPP1107VDC01_I | BR4_Cluster1 | BPL131 | DIGITAL | %M1252 | HME & LME Standpipe Pump 4 24VDC Control Supply (Q155) Healthy |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BPP1107 |  | BPP1107SYS01_I | BR4_Cluster1 | BPL131 | DIGITAL | %M1253 | HME & LME Standpipe Pump 4 Safety Relay (K161) Healthy |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BPP1107.Sub.CB01 |  | BPP1107CB01_I | BR4_Cluster1 | BPL131 | DIGITAL | %M1254 | HME & LME Standpipe Pump 4 Main Circuit Breaker (Q103) Closed |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BPP1107 |  | BPP1107TRP01_I | BR4_Cluster1 | BPL131 | DIGITAL | %M1255 | HME & LME Standpipe Pump 4 Main Circuit Breaker (Q103) Tripped |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1101.VS01 |  | BPP1101VS01VDC01_I | BR4_Cluster1 | BPL131 | DIGITAL | %M1259 | BPP1101VS01 VVVF Drive BPP1101VS01 Control Supply (Q204) Healthy |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1102.VS01 |  | BPP1102VS01VDC01_I | BR4_Cluster1 | BPL131 | DIGITAL | %M1260 | BPP1101VS01 VVVF Drive BPP1102VS01 Control Supply (Q207) Healthy |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1103.VS01 |  | BPP1103VS01VDC01_I | BR4_Cluster1 | BPL131 | DIGITAL | %M1261 | BPP1101VS01 VVVF Drive BPP1103VS01 Control Supply (Q210) Healthy |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1104.VS01 |  | BPP1104VS01VDC01_I | BR4_Cluster1 | BPL131 | DIGITAL | %M1262 | BPP1101VS01 VVVF Drive BPP1104VS01 Control Supply (Q213) Healthy |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1105.VS01 |  | BPP1105VS01VDC01_I | BR4_Cluster1 | BPL131 | DIGITAL | %M1263 | BPP1101VS01 VVVF Drive BPP1105VS01 Control Supply (Q216) Healthy |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BPP1106.VS01 |  | BPP1106VS01VDC01_I | BR4_Cluster1 | BPL131 | DIGITAL | %M1264 | BPP1101VS01 VVVF Drive BPP1106VS01 Control Supply (Q219) Healthy |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BPP1107.VS01 |  | BPP1107VS01VDC01_I | BR4_Cluster1 | BPL131 | DIGITAL | %M1265 | BPP1101VS01 VVVF Drive BPP1107VS01 Control Supply (Q222) Healthy |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop01 |  | BSR131DX01DIO1PLM2_Flt_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M13852 | BSR131DX01 DI Module 2 Fault Healthy |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131 | AlmAckCmd | BPL131_FltAck_CmdHMI | BR4_Cluster1 | BPL131 | DIGITAL | %M16000 | NPI Hub PLC Control System Alarm Acknowledge Command |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1101 |  | BPP1101_Aut_CmdHMI | BR4_Cluster1 | BPL131 | DIGITAL | %M16001 | Production Plant and NPI Water Supply Pump 1 Mode to Auto Command |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1101 |  | BPP1101_FltAck_CmdHMI | BR4_Cluster1 | BPL131 | DIGITAL | %M16002 | Production Plant and NPI Water Supply Pump 1 Control Fault Acknowledge Command |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1101 |  | BPP1101_Loc_CmdHMI | BR4_Cluster1 | BPL131 | DIGITAL | %M16003 | Production Plant and NPI Water Supply Pump 1 Mode to Local Command |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1101 |  | BPP1101_OOS_CmdHMI | BR4_Cluster1 | BPL131 | DIGITAL | %M16004 | Production Plant and NPI Water Supply Pump 1 Mode to Out of Service Command |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1101 |  | BPP1101PIC01_Aut_CmdHMI | BR4_Cluster1 | BPL131 | DIGITAL | %M16006 | BPP1101 Pressure Controller HMI Auto Command |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1101 |  | BPP1101PIC01_Man_CmdHMI | BR4_Cluster1 | BPL131 | DIGITAL | %M16008 | BPP1101 Pressure Controller HMI Manual Command |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1102 |  | BPP1102_Aut_CmdHMI | BR4_Cluster1 | BPL131 | DIGITAL | %M16009 | Production Plant and NPI Water Supply Pump 2 Mode to Auto Command |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1102 |  | BPP1102_FltAck_CmdHMI | BR4_Cluster1 | BPL131 | DIGITAL | %M16010 | Production Plant and NPI Water Supply Pump 2 Control Fault Acknowledge Command |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1102 |  | BPP1102_Loc_CmdHMI | BR4_Cluster1 | BPL131 | DIGITAL | %M16011 | Production Plant and NPI Water Supply Pump 2 Mode to Local Command |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1102 |  | BPP1102_OOS_CmdHMI | BR4_Cluster1 | BPL131 | DIGITAL | %M16012 | Production Plant and NPI Water Supply Pump 2 Mode to Out of Service Command |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1103 |  | BPP1103_Aut_CmdHMI | BR4_Cluster1 | BPL131 | DIGITAL | %M16015 | Water Transfer Pump 1 Mode to Auto Command |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1103 |  | BPP1103LIC01_Aut_CmdHMI | BR4_Cluster1 | BPL131 | DIGITAL | %M16021 | West Turkeys Nest Level Controller HMI Auto Command |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1103 |  | BPP1103LIC01_Man_CmdHMI | BR4_Cluster1 | BPL131 | DIGITAL | %M16023 | West Turkeys Nest Level Controller HMI Manual Command |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1104 |  | BPP1104_Aut_CmdHMI | BR4_Cluster1 | BPL131 | DIGITAL | %M16024 | Water Transfer Pump 2 Mode to Auto Command |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1104 |  | BPP1104_FltAck_CmdHMI | BR4_Cluster1 | BPL131 | DIGITAL | %M16025 | Water Transfer Pump 2 Control Fault Acknowledge Command |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1104 |  | BPP1104_Loc_CmdHMI | BR4_Cluster1 | BPL131 | DIGITAL | %M16026 | Water Transfer Pump 2 Mode to Local Command |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1104 |  | BPP1104_OOS_CmdHMI | BR4_Cluster1 | BPL131 | DIGITAL | %M16027 | Water Transfer Pump 2 Mode to Out of Service Command |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1105 |  | BPP1105_Aut_CmdHMI | BR4_Cluster1 | BPL131 | DIGITAL | %M16030 | Water Transfer Pump 3 Mode to Auto Command |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1105 |  | BPP1105_FltAck_CmdHMI | BR4_Cluster1 | BPL131 | DIGITAL | %M16031 | Water Transfer Pump 3 Control Fault Acknowledge Command |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1105 |  | BPP1105_Loc_CmdHMI | BR4_Cluster1 | BPL131 | DIGITAL | %M16032 | Water Transfer Pump 3 Mode to Local Command |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1105 |  | BPP1105_OOS_CmdHMI | BR4_Cluster1 | BPL131 | DIGITAL | %M16033 | Water Transfer Pump 3 Mode to Out of Service Command |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BPP1106 |  | BPP1106_Aut_CmdHMI | BR4_Cluster1 | BPL131 | DIGITAL | %M16036 | HME & LME Standpipe Pump 3 Mode to Auto Command |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BPP1106 |  | BPP1106_FltAck_CmdHMI | BR4_Cluster1 | BPL131 | DIGITAL | %M16037 | HME & LME Standpipe Pump 3 Control Fault Acknowledge Command |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BPP1106 |  | BPP1106_Loc_CmdHMI | BR4_Cluster1 | BPL131 | DIGITAL | %M16038 | HME & LME Standpipe Pump 3 Mode to Local Command |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BPP1106 |  | BPP1106_OOS_CmdHMI | BR4_Cluster1 | BPL131 | DIGITAL | %M16039 | HME & LME Standpipe Pump 3 Mode to Out of Service Command |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BPP1107 |  | BPP1107_Aut_CmdHMI | BR4_Cluster1 | BPL131 | DIGITAL | %M16042 | HME & LME Standpipe Pump 4 Mode to Auto Command |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BPP1107 |  | BPP1107_FltAck_CmdHMI | BR4_Cluster1 | BPL131 | DIGITAL | %M16043 | HME & LME Standpipe Pump 4 Control Fault Acknowledge Command |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BPP1107 |  | BPP1107_Loc_CmdHMI | BR4_Cluster1 | BPL131 | DIGITAL | %M16044 | HME & LME Standpipe Pump 4 Mode to Local Command |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BPP1107 |  | BPP1107_OOS_CmdHMI | BR4_Cluster1 | BPL131 | DIGITAL | %M16045 | HME & LME Standpipe Pump 4 Mode to Out of Service Command |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BSTD1106 |  | BSTD1106FIC01_Aut_CmdHMI | BR4_Cluster1 | BPL131 | DIGITAL | %M16048 | West Turkeys Nest LME Standpipe Flow Controller HMI Auto Command |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BSTD1106 |  | BSTD1106FIC01_Man_CmdHMI | BR4_Cluster1 | BPL131 | DIGITAL | %M16050 | West Turkeys Nest LME Standpipe Flow Controller HMI Manual Command |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BSTD1107 |  | BSTD1107FIC01_Aut_CmdHMI | BR4_Cluster1 | BPL131 | DIGITAL | %M16051 | West Turkeys Nest HME Standpipe Flow Controller HMI Auto Command |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BSTD1107 |  | BSTD1107FIC01_Man_CmdHMI | BR4_Cluster1 | BPL131 | DIGITAL | %M16053 | West Turkeys Nest HME Standpipe Flow Controller HMI Manual Command |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.BTY1502.FV01 |  | BTY1502FV01_Aut_CmdHMI | BR4_Cluster1 | BPL131 | DIGITAL | %M16061 | East Turkeys Nest Raw Water Remote Mode Valve Position Mode Auto HMI Command |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.BTY1502.FV01 |  | BTY1502FV01_Man_CmdHMI | BR4_Cluster1 | BPL131 | DIGITAL | %M16062 | East Turkeys Nest Raw Water Remote Mode Valve Position Mode Manual HMI Command |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.BTY1502.FV01 |  | BTY1502FV01_ManCls_CmdHMI | BR4_Cluster1 | BPL131 | DIGITAL | %M16063 | East Turkeys Nest Raw Water Remote Mode FV01 ManCls HMI Command |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.BTY1502.FV01 |  | BTY1502FV01_ManOpn_CmdHMI | BR4_Cluster1 | BPL131 | DIGITAL | %M16064 | East Turkeys Nest Raw Water Remote Mode FV01 ManOpn HMI Command |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BSTD1107.FV02 |  | BSTD1107FV02_Aut_CmdHMI | BR4_Cluster1 | BPL131 | DIGITAL | %M16071 | West Turkeys Nest HME Standpipe Valve Position Mode Auto HMI Command |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BSTD1107.FV02 |  | BSTD1107FV02_Man_CmdHMI | BR4_Cluster1 | BPL131 | DIGITAL | %M16072 | West Turkeys Nest HME Standpipe Valve Position Mode Manual HMI Command |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BSTD1107.FV02 |  | BSTD1107FV02_ManCls_CmdHMI | BR4_Cluster1 | BPL131 | DIGITAL | %M16073 | West Turkeys Nest HME Standpipe FV02 ManCls HMI Command |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BSTD1107.FV02 |  | BSTD1107FV02_ManOpn_CmdHMI | BR4_Cluster1 | BPL131 | DIGITAL | %M16074 | West Turkeys Nest HME Standpipe FV02 ManOpn HMI Command |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BSTD1107 |  | BSTD1107_GrpAut_CmdHMI | BR4_Cluster1 | BPL131 | DIGITAL | %M16081 | West Turkeys Nest HME Standpipe Group Auto HMI Command |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BSTD1107 |  | BSTD1107_GrpLoc_CmdHMI | BR4_Cluster1 | BPL131 | DIGITAL | %M16082 | West Turkeys Nest HME Standpipe Group Local HMI Command |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BSTD1107 |  | BSTD1107_GrpStp_CmdHMI | BR4_Cluster1 | BPL131 | DIGITAL | %M16083 | West Turkeys Nest HME Standpipe Group Stop HMI Command |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BSTD1107 |  | BSTD1107_GrpStt_CmdHMI | BR4_Cluster1 | BPL131 | DIGITAL | %M16084 | West Turkeys Nest HME Standpipe Group Local Start HMI Command |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BSTD1107 |  | BSTD1107_FltAck_CmdHMI | BR4_Cluster1 | BPL131 | DIGITAL | %M16085 | West Turkeys Nest HME Standpipe Fault Acknowlege HMI Command |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BSTD1107 |  | BSTD1107_CshStp_CmdHMI | BR4_Cluster1 | BPL131 | DIGITAL | %M16086 | West Turkeys Nest HME Standpipe Crash Stop HMI Command |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BSTD1106.FV03 |  | BSTD1106FV03_Aut_CmdHMI | BR4_Cluster1 | BPL131 | DIGITAL | %M16091 | West Turkeys Nest LME Standpipe Valve Position Mode Auto HMI Command |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BSTD1106.FV03 |  | BSTD1106FV03_Man_CmdHMI | BR4_Cluster1 | BPL131 | DIGITAL | %M16092 | West Turkeys Nest LME Standpipe Valve Position Mode Manual HMI Command |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BSTD1106 |  | BSTD1106_GrpAut_CmdHMI | BR4_Cluster1 | BPL131 | DIGITAL | %M16101 | West Turkeys Nest LME Standpipe Group Auto HMI Command |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BSTD1106 |  | BSTD1106_GrpLoc_CmdHMI | BR4_Cluster1 | BPL131 | DIGITAL | %M16102 | West Turkeys Nest LME Standpipe Group Local HMI Command |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BSTD1106 |  | BSTD1106_GrpStp_CmdHMI | BR4_Cluster1 | BPL131 | DIGITAL | %M16103 | West Turkeys Nest LME Standpipe Group Stop HMI Command |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BSTD1106 |  | BSTD1106_GrpStt_CmdHMI | BR4_Cluster1 | BPL131 | DIGITAL | %M16104 | West Turkeys Nest LME Standpipe Group Start HMI Command |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BSTD1106 |  | BSTD1106_CshStp_CmdHMI | BR4_Cluster1 | BPL131 | DIGITAL | %M16105 | West Turkeys Nest LME Standpipe Crash Stop HMI Command |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BSTD1106 |  | BSTD1106_FltAck_CmdHMI | BR4_Cluster1 | BPL131 | DIGITAL | %M16106 | West Turkeys Nest LME Standpipe Fault AcknowledgeHMI Command |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1 |  | BPP1106_7_PRI1_CycHrs_CmdHMI | BR4_Cluster1 | BPL131 | DIGITAL | %M16111 | HME Standpipe Pump 1 7 PRI1 Cycle Hours HMI Command |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1 |  | BPP1106_7_PRI1_Fix_CmdHMI | BR4_Cluster1 | BPL131 | DIGITAL | %M16112 | HME Standpipe Pump 1 7 PRI1 Fix HMI Command |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1 |  | BPP1101_2_GrpAut_CmdHMI | BR4_Cluster1 | BPL131 | DIGITAL | %M16121 | HME Standpipe Pump 1 2 GrpAut HMI Command |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1 |  | BPP1101_2_GrpLoc_CmdHMI | BR4_Cluster1 | BPL131 | DIGITAL | %M16122 | HME Standpipe Pump 1 2 GrpLoc HMI Command |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1 |  | BPP1101_2_GrpStp_CmdHMI | BR4_Cluster1 | BPL131 | DIGITAL | %M16123 | HME Standpipe Pump 1 2 GrpStp HMI Command |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1 |  | BPP1101_2_GrpStt_CmdHMI | BR4_Cluster1 | BPL131 | DIGITAL | %M16124 | HME Standpipe Pump 1 2 GrpStt HMI Command |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1 |  | BPP1101_2_PRI1_CycHrs_CmdHMI | BR4_Cluster1 | BPL131 | DIGITAL | %M16125 | HME Standpipe Pump 1 2 PRI1 Cycle Hours HMI Command |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1 |  | BPP1101_2_CshStp_CmdHMI | BR4_Cluster1 | BPL131 | DIGITAL | %M16126 | HME Standpipe Pump 1 2 CshStp HMI Command |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1 |  | BPP1101_2_FltAck_CmdHMI | BR4_Cluster1 | BPL131 | DIGITAL | %M16127 | HME Standpipe Pump 1 2 FltAck HMI Command |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1101.FieldIO.PT10 |  | BPP1101PT10_Sel_CmdHMI | BR4_Cluster1 | BPL131 | DIGITAL | %M16131 | BPP1101PT10 Flow Switch Value Frozen HMI Select Command |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1101.FieldIO.PT11 |  | BPP1101PT11_Sel_CmdHMI | BR4_Cluster1 | BPL131 | DIGITAL | %M16132 | HME Standpipe Pump 1 PT11 HMI Select Command |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT |  | BPP1103_4_5_GrpAut_CmdHMI | BR4_Cluster1 | BPL131 | DIGITAL | %M16141 | HME Standpipe Pump 1 4 5 GrpAut HMI Command |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT |  | BPP1103_4_5_GrpLoc_CmdHMI | BR4_Cluster1 | BPL131 | DIGITAL | %M16142 | HME Standpipe Pump 1 4 5 GrpLoc HMI Command |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT |  | BPP1103_4_5_GrpStp_CmdHMI | BR4_Cluster1 | BPL131 | DIGITAL | %M16143 | HME Standpipe Pump 1 4 5 GrpStp HMI Command |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT |  | BPP1103_4_5_GrpStt_CmdHMI | BR4_Cluster1 | BPL131 | DIGITAL | %M16144 | HME Standpipe Pump 1 4 5 GrpStt HMI Command |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT |  | BPP1103_4_5_CshStp_CmdHMI | BR4_Cluster1 | BPL131 | DIGITAL | %M16145 | HME Standpipe Pump 1 4 5 CshStp HMI Command |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT |  | BPP1103_4_5_FltAck_CmdHMI | BR4_Cluster1 | BPL131 | DIGITAL | %M16146 | HME Standpipe Pump 1 4 5 FltAck HMI Command |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT |  | BPP1103_4_5_PRI1_CycHrs_CmdHMI | BR4_Cluster1 | BPL131 | DIGITAL | %M16147 | HME Standpipe Pump 1 4 5 PRI1 Cycle Hours HMI Command |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT |  | BPP1103_4_5_PRI1_Fix_CmdHMI | BR4_Cluster1 | BPL131 | DIGITAL | %M16148 | HME Standpipe Pump 1 4 5 PRI1 Fix HMI Command |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1103 |  | BPP1103_Man_CmdHMI | BR4_Cluster1 | BPL131 | DIGITAL | %M16151 | HME Standpipe Pump 1 Mode Manual HMI Command |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1103 |  | BPP1103_ManCls_CmdHMI | BR4_Cluster1 | BPL131 | DIGITAL | %M16152 | HME Standpipe Pump 1 ManCls HMI Command |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1103 |  | BPP1103_ManOpn_CmdHMI | BR4_Cluster1 | BPL131 | DIGITAL | %M16153 | HME Standpipe Pump 1 ManOpn HMI Command |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131 | Slot0_A | BPL131_Flt_A | BR4_Cluster1 | BPL131 | DIGITAL | %M3001 | NPI Hub PLC Fault |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.DB02 |  | BSR131DB02SR01_O | BR4_Cluster1 | BPL131 | DIGITAL | %M3006 | BSR131 415V Dewatering Laydown Lighting Dist Board Lightning Control Relay Enabled |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.DB01 |  | BSR131DB01SR01_O | BR4_Cluster1 | BPL131 | DIGITAL | %M3007 | BSR131 LSP Dist Board Lightning Control Relay Enabled |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.BMC1311.Sub.CB01 |  | BMC1311CB01_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4000 | HME Refuelling MCC Main Circuit Breaker (Q103) Open |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.BMC1311.Sub.CB01 |  | BMC1311TRP01_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4001 | HME Refuelling MCC Main Circuit Breaker Tripped |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.BMC1311 |  | BMC1311VDC01_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4002 | HME Refuelling MCC 24VDC Control Supply (Q155) Failure |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC01 |  | BMC131INC01CB02_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4003 | BMC131 Process Bus Incomer Arc Flash Supply (Q204) Open |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC01 |  | BMC131INC01CB03_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4004 | BMC131 Process Bus Incomer Incomer Circuit Breaker Spring Charge Supply (Q212) Open |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC01 |  | BMC131INC01CB04_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4005 | BMC131 Process Bus Incomer Incomer Circuit Breaker Trip Supply (Q220) Open |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC01 |  | BMC131INC01CB05_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4006 | BMC131 Process Bus Incomer Incomer Circuit Breaker 24VDC Cubicle Bus Supply (Q256) Open |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC01 |  | BMC131INC01CB06_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4007 | BMC131 Process Bus Incomer 110VDC/24VDC Power Supply (Q215) Open |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC01 |  | BMC131INC01PR1_CBCls_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4008 | BMC131 Process Bus Incomer Protection Relay Circuit Breaker Alarm Alarm |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC01 |  | BMC131INC01PR1_CBFlt_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M4009 | BMC131 Process Bus Incomer Protection Relay Fault Healthy Alarm |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC01 |  | BMC131INC01PR1_ComFlt_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4010 | BMC131 Process Bus Incomer Protection Relay Communications Fault Alarm Alarm |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC01 |  | BMC131INC01PR1_Flt_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4011 | BMC131 Process Bus Incomer Protection Relay Fault Alarm Alarm |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC01 |  | BMC131INC01PR1_MntRqd_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4012 | BMC131 Process Bus Incomer Protection Relay Contactor Replacement Required Alarm Alarm |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC01.VAMP |  | BMC131INC01TRP02_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4013 | BMC131 Process Bus Incomer Arc Flash Tripped |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC01 |  | BMC131INC01VDC01_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4017 | BMC131 Process Bus Incomer 24VDC Control Supply (Q267) Failure |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC01.VAMP |  | BMC131INC01XS02_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4019 | BMC131 Process Bus Incomer Vamp Self Supervision Alarm |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC01 |  | BMC131INC01XS03_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4020 | BMC131 Process Bus Incomer Surge Protection Unhealthy Alarm |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC02 |  | BMC131INC02CB03_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4021 | BMC131 Essential Bus Incomer Incomer Circuit Breaker Spring Charge Supply (Q212) Open |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC02 |  | BMC131INC02CB04_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4022 | BMC131 Essential Bus Incomer Incomer Circuit Breaker Trip Supply (Q220) Open |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC02 |  | BMC131INC02CB05_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4023 | BMC131 Essential Bus Incomer Incomer Circuit Breaker 24VDC Cubicle Bus Supply (Q256) Open |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC02 |  | BMC131INC02CB06_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4024 | BMC131 Essential Bus Incomer 110VDC/24VDC Power Supply (Q215) Open |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC02 |  | BMC131INC02PR1_CBCls_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4025 | BMC131 Essential Bus Incomer Protection Relay Circuit Breaker Alarm Alarm |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC02 |  | BMC131INC02PR1_CBFlt_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M4026 | BMC131 Essential Bus Incomer Protection Relay Fault Healthy Alarm |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC02 |  | BMC131INC02PR1_ComFlt_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4027 | BMC131 Essential Bus Incomer Protection Relay Communications Fault Alarm Alarm |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC02 |  | BMC131INC02PR1_Flt_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4028 | BMC131 Essential Bus Incomer Protection Relay Fault Alarm Alarm |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC02 |  | BMC131INC02PR1_MntRqd_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4029 | BMC131 Essential Bus Incomer Protection Relay Contactor Replacement Required Alarm Alarm |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC02 |  | BMC131INC02VDC01_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4031 | BMC131 Essential Bus Incomer 24VDC Control Supply (Q267) Failure |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC02 |  | BMC131INC02XS03_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4034 | BMC131 Essential Bus Incomer Surge Protection Unhealthy Alarm |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC03 |  | BMC131INC03PR1_CBCls_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4040 | BMC131 Generator Bus Incomer Protection Relay Circuit Breaker Alarm Alarm |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC03 |  | BMC131INC03PR1_CBFlt_Hty | BR4_Cluster1 | BPL131 | DIGITAL | %M4041 | BMC131 Generator Bus Incomer Protection Relay Fault Healthy Alarm |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC03 |  | BMC131INC03PR1_ComFlt_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4042 | BMC131 Generator Bus Incomer Protection Relay Communications Fault Alarm Alarm |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC03 |  | BMC131INC03PR1_Flt_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4043 | BMC131 Generator Bus Incomer Protection Relay Fault Alarm Alarm |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC03 |  | BMC131INC03PR1_MntRqd_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4044 | BMC131 Generator Bus Incomer Protection Relay Contactor Replacement Required Alarm Alarm |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC03 |  | BMC131INC03VDC01_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4046 | BMC131 Generator Bus Incomer 24VDC Control Supply (Q267) Failure |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131 |  | BPL131_Def_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4047 | NPI Hub BPL131 Default Values Loaded Alarm |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131 |  | BPL131_MemFlt_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4048 | NPI Hub PLC CPU Memory Card Error Alarm |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131 |  | BPL131_Sys1Flt_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4049 | NPI Hub PLC CPU Arithmetic Fault Alarm |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131 |  | BPL131_Sys2Flt_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4050 | NPI Hub PLC CPU Index OverFlow Fault Alarm |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131 |  | BPL131IPC2_Flt_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4051 | BPL131 Communications From BPL130 Fault Alarm |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131 |  | BPL131IPC2_PriFlt_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4052 | BPL131 Communications From BPL130 Primary Path Fault Alarm |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131 |  | BPL131IPC2_SecFlt_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4053 | BPL131 Communications From BPL130 Secondary Path Fault Alarm |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131 |  | BPL131IPC3_Flt_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4054 | BPL131 Communications From BPL132 Fault Alarm |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131 |  | BPL131IPC3_PriFlt_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4055 | BPL131 Communications From BPL132 Primary Path Fault Alarm |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131 |  | BPL131IPC3_SecFlt_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4056 | BPL131 Communications From BPL132 Secondary Path Fault Alarm |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131 |  | BPL131PLM0_Flt_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4057 | NPI Hub PLC CPU RIO Network Fault Alarm |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131 | Slot3_A | BPL131PLM3_Flt_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4059 | NPI Hub PLC Ethernet Module Slot 3 Fault Alarm |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131 | Slot4_A | BPL131PLM4_Flt_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4060 | NPI Hub PLC Ethernet Module Slot 4 Fault Alarm |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131 | Slot5_A | BPL131PLM5_Flt_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4061 | NPI Hub PLC Ethernet Module Slot 5 Fault Alarm |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1101.Sub.CB01 |  | BPP1101CB01_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4063 | Production Plant and NPI Water Supply Pump 1 Main Circuit Breaker (Q103) Open |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1101 |  | BPP1101THR01_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4069 | Production Plant and NPI Water Supply Pump 1 Production Plant & NPI Water Supply Pump 1 (Duty) (K190) |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1101 |  | BPP1101VDC01_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4073 | Production Plant and NPI Water Supply Pump 1 24VDC Control Supply (Q155) Failure |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1101.VS01 |  | BPP1101VS01VDC01_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4074 | BPP1101VS01 VVVF Drive BPP1101VS01 Control Supply (Q204) Failure |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1102.Sub.CB01 |  | BPP1102CB01_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4078 | Production Plant and NPI Water Supply Pump 2 Main Circuit Breaker (Q103) Open |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1102 |  | BPP1102THR01_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4084 | Production Plant and NPI Water Supply Pump 2 Production Plant & NPI Water Supply Pump 2 (Standby) (K190) |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1102 |  | BPP1102VDC01_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4085 | Production Plant and NPI Water Supply Pump 2 24VDC Control Supply (Q155) Failure |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1102.VS01 |  | BPP1102VS01VDC01_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4086 | BPP1101VS01 VVVF Drive BPP1102VS01 Control Supply (Q207) Failure |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1103.Sub.CB01 |  | BPP1103CB01_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4090 | Water Transfer Pump 1 Main Circuit Breaker (Q103) Open |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1103 |  | BPP1103THR01_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4096 | Water Transfer Pump 1 Thermistor Relay (K190) |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1103 |  | BPP1103VDC01_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4097 | Water Transfer Pump 1 24VDC Control Supply (Q155) Failure |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1103.VS01 |  | BPP1103VS01VDC01_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4098 | BPP1101VS01 VVVF Drive BPP1103VS01 Control Supply (Q210) Failure |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1104.Sub.CB01 |  | BPP1104CB01_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4102 | Water Transfer Pump 2 Main Circuit Breaker (Q103) Open |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1104 |  | BPP1104THR01_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4108 | Water Transfer Pump 2 Thermistor Relay (K190) |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1104 |  | BPP1104VDC01_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4109 | Water Transfer Pump 2 24VDC Control Supply (Q155) Failure |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1104.VS01 |  | BPP1104VS01VDC01_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4110 | BPP1101VS01 VVVF Drive BPP1104VS01 Control Supply (Q213) Failure |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1105 |  | BPP1105CB01_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4114 | Water Transfer Pump 3 Main Circuit Breaker (Q103) Open |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1105 |  | BPP1105THR01_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4120 | Water Transfer Pump 3 Thermistor Relay (K190) |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1105 |  | BPP1105VDC01_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4121 | Water Transfer Pump 3 24VDC Control Supply (Q155) Failure |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1105.VS01 |  | BPP1105VS01VDC01_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4122 | BPP1101VS01 VVVF Drive BPP1105VS01 Control Supply (Q216) Failure |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BPP1106.Sub.CB01 |  | BPP1106CB01_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4126 | HME & LME Standpipe Pump 3 Main Circuit Breaker (Q103) Open |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BPP1106 |  | BPP1106THR01_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4132 | HME & LME Standpipe Pump 3 HME And LME Standpipe Pump 3 (Duty) (K190) |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BPP1106 |  | BPP1106VDC01_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4133 | HME & LME Standpipe Pump 3 24VDC Control Supply (Q155) Failure |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BPP1106.VS01 |  | BPP1106VS01VDC01_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4134 | BPP1101VS01 VVVF Drive BPP1106VS01 Control Supply (Q219) Failure |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BPP1107.Sub.CB01 |  | BPP1107CB01_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4138 | HME & LME Standpipe Pump 4 Main Circuit Breaker (Q103) Open |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BPP1107 |  | BPP1107THR01_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4144 | HME & LME Standpipe Pump 4 HME And LME Standpipe Pump 4 (Standby) (K190) |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BPP1107 |  | BPP1107VDC01_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4145 | HME & LME Standpipe Pump 4 24VDC Control Supply (Q155) Failure |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BPP1107.VS01 |  | BPP1107VS01VDC01_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4146 | BPP1101VS01 VVVF Drive BPP1107VS01 Control Supply (Q222) Failure |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.P3FIREWATER.BPQE2101.Sub.DB01.CB01 |  | BPQE2101DB01CB01_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4149 | NPI & Primary Crusher Fire Water Pump Dist Board Main Circuit Breaker (Q103) Open |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.P3FIREWATER.BPQE2101.Sub.DB01.CB01 |  | BPQE2101DB01TRP01_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4150 | NPI & Primary Crusher Fire Water Pump Dist Board Main Circuit Breaker Tripped |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.P3FIREWATER.BPQE2101.Sub.DB01 |  | BPQE2101DB01VDC01_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4151 | NPI & Primary Crusher Fire Water Pump Dist Board 24VDC Control Supply (Q155) Failure |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.P3FIREWATER.BPQE2101.Sub.PN01 |  | BPQE2101PN01VDC01_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4154 | NPI & Primary Crushing Fire Water Container Panel 24VDC Control Supply (Q155) Failure |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.P3POTWATER.BPQE2115.Sub.DB01 |  | BPQE2115MC01VDC01_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4157 | Potable Water MCC 24VDC Control Supply (PWTP) (Q155) Failure |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.AC01.CB01 |  | BSR131AC01CB01_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4158 | BSR131 Aircon 1 Main Circuit Breaker (Q103) Open |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.AC01.CB01 |  | BSR131AC01TRP01_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4159 | BSR131 Aircon 1 Main Circuit Breaker Tripped |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.AC01 |  | BSR131AC01VDC01_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4160 | BSR131 Aircon 1 24VDC Control Supply (Q155) Failure |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.AC02.CB01 |  | BSR131AC02CB01_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4162 | BSR131 Aircon 2 Main Circuit Breaker (Q103) Open |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.AC02.CB01 |  | BSR131AC02TRP01_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4163 | BSR131 Aircon 2 Main Circuit Breaker Tripped |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.AC02 |  | BSR131AC02VDC01_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4164 | BSR131 Aircon 2 24VDC Control Supply (Q155) Failure |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.BC01.CB01 |  | BSR131BC01CB01_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4168 | BSR131 Battery Charger 1 Main Circuit Breaker (Q103) Open |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.BC01 |  | BSR131BC01VDC01_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4169 | BSR131 Battery Charger 1 24VDC Control Supply (Q155) Failure |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.BC02.CB01 |  | BSR131BC02CB01_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4172 | BSR131 Battery Charger 2 Main Circuit Breaker (Q103) Open |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.BC02 |  | BSR131BC02CB02_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4173 | BSR131 Battery Charger 2 BMC131INC01 110VDC INC01 Tripping Supply Circuit Breaker (Q114) Open |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.BC02 |  | BSR131BC02CB03_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4174 | BSR131 Battery Charger 2 BMC131INC02 110VDC INC02 Tripping Supply Circuit Breaker (Q117) Open |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.BC02 |  | BSR131BC02CB04_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4175 | BSR131 Battery Charger 2 BMC131INC03 110VDC INC03 Tripping Supply Circuit Breaker (Q120) Open |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.BC02 |  | BSR131BC02CB05_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4176 | BSR131 Battery Charger 2 RSP01 110VDC Tripping Supply Circuit Breaker (Q123) Open |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.BC02 |  | BSR131BC02VDC01_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4184 | BSR131 Battery Charger 2 24VDC Control Supply (Q155) Failure |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.BC02 |  | BSR131BC02VDC02_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4185 | BSR131 Battery Charger 2 Battery Charger 110VDC Tripping Supply (K112) Failure |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.DB01.CB01 |  | BSR131DB01CB01_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4186 | BSR131 LSP Dist Board Main Circuit Breaker (Q103) Open |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.DB01.CB01 |  | BSR131DB01TRP01_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4187 | BSR131 LSP Dist Board Main Circuit Breaker Tripped |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.DB01 |  | BSR131DB01VDC01_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4188 | BSR131 LSP Dist Board 24VDC Control Supply (Q155) Failure |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.DB02.CB01 |  | BSR131DB02CB01_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4189 | BSR131 415V Dewatering Laydown Lighting Dist Board Main Circuit Breaker (Q103) Open |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.DB02.CB01 |  | BSR131DB02TRP01_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4190 | BSR131 415V Dewatering Laydown Lighting Dist Board Main Circuit Breaker Tripped |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.DB02 |  | BSR131DB02VDC01_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4191 | BSR131 415V Dewatering Laydown Lighting Dist Board 24VDC Control Supply (Q155) Failure |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.DB03.CB01 |  | BSR131DB03CB01_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4192 | BSR131 415V HME Refuel Water Recycle Dist Board Main Circuit Breaker (Q103) Open |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.DB03.CB01 |  | BSR131DB03TRP01_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4193 | BSR131 415V HME Refuel Water Recycle Dist Board Main Circuit Breaker Tripped |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.DB03 |  | BSR131DB03VDC01_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4194 | BSR131 415V HME Refuel Water Recycle Dist Board 24VDC Control Supply (Q155) Failure |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop01 |  | BSR131DX01DIO1PLM0_ComFlt_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4195 | BSR131DX01 CRA Comms Module 0 Communications Fault Alarm |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop01 | Slot0_A | BSR131DX01DIO1PLM0_Flt_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4196 | BSR131DX01 CRA Comms Module 0 Fault Alarm |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop01 | Slot1_A | BSR131DX01DIO1PLM1_Flt_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4197 | BSR131DX01 DI Module 1 Fault Alarm |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop01 |  | BSR131DX01DIO1PLM1_Grp1Flt_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4198 | BSR131DX01 DI Module 1 Group 1 Fault Alarm |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop01 |  | BSR131DX01DIO1PLM1_Grp2Flt_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4199 | BSR131DX01 DI Module 1 Group 2 Fault Alarm |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop01 | Slot2_A | BSR131DX01DIO1PLM2_Flt_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4200 | BSR131DX01 DI Module 2 Fault Alarm |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop01 |  | BSR131DX01DIO1PLM2_Grp1Flt_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4201 | BSR131DX01 DI Module 2 Group 1 Fault Alarm |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop01 |  | BSR131DX01DIO1PLM2_Grp2Flt_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4202 | BSR131DX01 DI Module 2 Group 2 Fault Alarm |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop01 | Slot3_A | BSR131DX01DIO1PLM3_Flt_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4203 | BSR131DX01 DI Module 3 Fault Alarm |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop01 |  | BSR131DX01DIO1PLM3_Grp1Flt_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4204 | BSR131DX01 DI Module 3 Group 1 Fault Alarm |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop01 |  | BSR131DX01DIO1PLM3_Grp2Flt_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4205 | BSR131DX01 DI Module 3 Group 2 Fault Alarm |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop01 | Slot4_A | BSR131DX01DIO1PLM4_Flt_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4206 | BSR131DX01 DI Module 4 Fault Alarm |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop01 |  | BSR131DX01DIO1PLM4_Grp1Flt_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4207 | BSR131DX01 DI Module 4 Group 1 Fault Alarm |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop01 |  | BSR131DX01DIO1PLM4_Grp2Flt_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4208 | BSR131DX01 DI Module 4 Group 2 Fault Alarm |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop01 | Slot5_A | BSR131DX01DIO1PLM5_Flt_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4209 | BSR131DX01 DI Module 5 Fault Alarm |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop01 |  | BSR131DX01DIO1PLM5_Grp1Flt_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4210 | BSR131DX01 DI Module 5 Group 1 Fault Alarm |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop01 |  | BSR131DX01DIO1PLM5_Grp2Flt_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4211 | BSR131DX01 DI Module 5 Group 2 Fault Alarm |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop01 | Slot6_A | BSR131DX01DIO1PLM6_Flt_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4212 | BSR131DX01 DI Module 6 Fault Alarm |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop01 |  | BSR131DX01DIO1PLM6_Grp1Flt_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4213 | BSR131DX01 DI Module 6 Group 1 Fault Alarm |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop01 |  | BSR131DX01DIO1PLM6_Grp2Flt_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4214 | BSR131DX01 DI Module 6 Group 2 Fault Alarm |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop01 | Slot7_A | BSR131DX01DIO1PLM7_Flt_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4215 | BSR131DX01 DI Module 7 Fault Alarm |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop01 |  | BSR131DX01DIO1PLM7_Grp1Flt_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4216 | BSR131DX01 DI Module 7 Group 1 Fault Alarm |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop01 |  | BSR131DX01DIO1PLM7_Grp2Flt_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4217 | BSR131DX01 DI Module 7 Group 2 Fault Alarm |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop01 | Slot8_A | BSR131DX01DIO1PLM8_Flt_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4218 | BSR131DX01 DO Module 8 Fault Alarm |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop01 |  | BSR131DX01VDC01_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4219 | BSR131 DIO Box 1 DX01 24VDC Control Supply Healthy (Q110) Failure |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop01 |  | BSR131DX01VDC02_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4220 | BSR131 DIO Box 1 DX01 24VDC Output Module Control Supply (Q170) Failure |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.UP01 |  | BSR131DX01VDC03_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4221 | BSR131 DIO Box 1 BSR131UP01 24VDC Control Supply (Q254) Failure |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.BC01 |  | BSR131DX01VDC04_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4222 | BSR131 DIO Box 1 BSR131BC01DB01 24VDC Control Supply (Q257) Failure |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.BC02 |  | BSR131DX01VDC05_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4223 | BSR131 DIO Box 1 BSR131BC02DB01 24VDC Control Supply (Q260) Failure |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.DB01 |  | BSR131DX01VDC06_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4224 | BSR131 DIO Box 1 BSR131UP01DB01 24VDC Control Supply (Q263) Failure |  |  | BS1_Tags
BR4.SRV.PWR.BSR131 |  | BSR131DX01VDC07_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4225 | BSR131 DIO Box 1 Misc Switchroom Alarms 24VDC Control Supply (Q266) Failure |  |  | BS1_Tags
BR4.SRV.PWR.BSR131 |  | BSR131FIP01IS01_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4231 | BSR131 Fire Panel Fire Panel Isolated Open |  |  | BS1_Tags
BR4.SRV.PWR.BSR131 |  | BSR131FIP01XS01_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4232 | BSR131 Fire Panel Fault Alarm |  |  | BS1_Tags
BR4.SRV.PWR.BSR131 |  | BSR131FIP01XS02_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4233 | BSR131 Fire Panel Unhealthy Alarm |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.NEP01 |  | BSR131NEP01CB01_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4234 | BSR131 Network Panel 1 NEP Primary PDU Circuit Breaker (Q130) Open |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.NEP01 |  | BSR131NEP01CB02_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4235 | BSR131 Network Panel 1 NEP Secondary PDU Circuit Breaker (Q180) Open |  |  | BS1_Tags
BR4.SRV.PWR.BSR131 |  | BSR131PB01_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4236 | NPI Hub Substation Shutdown Pushbutton (SESP) Activated Alarm |  |  | BS1_Tags
BR4.SRV.PWR.BSR131 |  | BSR131PN01TS01_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4237 | Switchroom Control Panel Airlock High Temperature |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.UP01 |  | BSR131UP01_ComFlt_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4240 | BSR131 UPS Communications Fault Alarm Alarm |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.CB01 |  | BSR131UP01CB01_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4241 | BSR131 UPS Main Circuit Breaker (Q103) Open |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.UP01 |  | BSR131UP01VDC01_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4244 | BSR131 UPS 24VDC Control Supply (Q155) Failure |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.UP01 |  | BSR131UP01ZS01_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4245 | BSR131 UPS UPS in Normal Mode |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BSTD1106.FV03.FieldIO.CB01 |  | BSTD1106FV03CB01_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4248 | West Turkeys Nest LME Standpipe 240VAC Flow Valve Power Circuit Breaker Open |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BSTD1107.FV02.FieldIO.CB01 |  | BSTD1107FV02CB01_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4252 | West Turkeys Nest HME Standpipe 240VAC Flow Valve Power Circuit Breaker Open |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop04 |  | BTK2101DX04DIO1PLM0_ComFlt_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4257 | BTK2101DX04 CRA Comms Module 0 Communications Fault Alarm |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop04 | Slot0_A | BTK2101DX04DIO1PLM0_Flt_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4258 | BTK2101DX04 CRA Comms Module 0 Fault Alarm |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop04 | Slot1_A | BTK2101DX04DIO1PLM1_Flt_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4259 | BTK2101DX04 DI Module 1 Fault Alarm |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop04 |  | BTK2101DX04DIO1PLM1_Grp1Flt_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4260 | BTK2101DX04 DI Module 1 Group 1 Fault Alarm |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop04 |  | BTK2101DX04DIO1PLM1_Grp2Flt_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4261 | BTK2101DX04 DI Module 1 Group 2 Fault Alarm |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop04 |  | BTK2101DX04DIO1PLM3_Ch00Flt_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4262 | BTK2101DX04 AHI Module 3 Channel 0 Fault Alarm |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop04 |  | BTK2101DX04DIO1PLM3_Ch01Flt_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4263 | BTK2101DX04 AHI Module 3 Channel 1 Fault Alarm |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop04 |  | BTK2101DX04DIO1PLM3_Ch02Flt_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4264 | BTK2101DX04 AHI Module 3 Channel 2 Fault Alarm |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop04 |  | BTK2101DX04DIO1PLM3_Ch03Flt_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4265 | BTK2101DX04 AHI Module 3 Channel 3 Fault Alarm |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop04 |  | BTK2101DX04DIO1PLM3_Ch04Flt_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4266 | BTK2101DX04 AHI Module 3 Channel 4 Fault Alarm |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop04 |  | BTK2101DX04DIO1PLM3_Ch05Flt_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4267 | BTK2101DX04 AHI Module 3 Channel 5 Fault Alarm |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop04 |  | BTK2101DX04DIO1PLM3_Ch06Flt_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4268 | BTK2101DX04 AHI Module 3 Channel 6 Fault Alarm |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop04 |  | BTK2101DX04DIO1PLM3_Ch07Flt_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4269 | BTK2101DX04 AHI Module 3 Channel 7 Fault Alarm |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop04 | Slot3_A | BTK2101DX04DIO1PLM3_Flt_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4270 | BTK2101DX04 AHI Module 3 Fault Alarm |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop04 |  | BTK2101DX04VDC01_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4271 | NPI Fire Water Tank DIO Box 1 24VDC Output Control Supply (Q143) Failure |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop04 |  | BTK2101DX04VDC02_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4272 | NPI Fire Water Tank DIO Box 1 24VDC GW1 Control Supply (Q157) Failure |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop04 |  | BTK2101DX04VDC03_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4273 | NPI Fire Water Tank DIO Box 1 24VDC Instrument Control Supply (Q164) Failure |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop04 |  | BTK2101DX04VDC04_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4274 | NPI Fire Water Tank DIO Box 1 24VDC Transmitter Control Supply (Q168) Failure |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop04 |  | BTK2101DX04VDC05_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4275 | NPI Fire Water Tank DIO Box 1 24VDC BTK2101DX04 Control Supply (Q172) Failure |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop02 |  | BTY1502DX02DIO1PLM0_ComFlt_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4294 | BTY1502DX02 CRA Comms Module 0 Communications Fault Alarm |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop02 | Slot0_A | BTY1502DX02DIO1PLM0_Flt_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4295 | BTY1502DX02 CRA Comms Module 0 Fault Alarm |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop02 | Slot1_A | BTY1502DX02DIO1PLM1_Flt_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4296 | BTY1502DX02 DI Module 1 Fault Alarm |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop02 |  | BTY1502DX02DIO1PLM1_Grp1Flt_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4297 | BTY1502DX02 DI Module 1 Group 1 Fault Alarm |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop02 |  | BTY1502DX02DIO1PLM1_Grp2Flt_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4298 | BTY1502DX02 DI Module 1 Group 2 Fault Alarm |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop02 | Slot2_A | BTY1502DX02DIO1PLM2_Flt_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4299 | BTY1502DX02 DI Module 2 Fault Alarm |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop02 |  | BTY1502DX02DIO1PLM2_Grp1Flt_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4300 | BTY1502DX02 DI Module 2 Group 1 Fault Alarm |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop02 |  | BTY1502DX02DIO1PLM2_Grp2Flt_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4301 | BTY1502DX02 DI Module 2 Group 2 Fault Alarm |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop02 | Slot3_A | BTY1502DX02DIO1PLM3_Flt_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4302 | BTY1502DX02 DI Module 3 Fault Alarm |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop02 |  | BTY1502DX02DIO1PLM3_Grp1Flt_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4303 | BTY1502DX02 DI Module 3 Group 1 Fault Alarm |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop02 |  | BTY1502DX02DIO1PLM3_Grp2Flt_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4304 | BTY1502DX02 DI Module 3 Group 2 Fault Alarm |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop02 | Slot4_A | BTY1502DX02DIO1PLM4_Flt_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4305 | BTY1502DX02 DO Module 4 Fault Alarm |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop02 |  | BTY1502DX02DIO1PLM5_Ch00Flt_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4306 | BTY1502DX02 AHI Module 5 Channel 0 Fault Alarm |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop02 |  | BTY1502DX02DIO1PLM5_Ch01Flt_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4307 | BTY1502DX02 AHI Module 5 Channel 1 Fault Alarm |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop02 |  | BTY1502DX02DIO1PLM5_Ch02Flt_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4308 | BTY1502DX02 AHI Module 5 Channel 2 Fault Alarm |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop02 |  | BTY1502DX02DIO1PLM5_Ch03Flt_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4309 | BTY1502DX02 AHI Module 5 Channel 3 Fault Alarm |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop02 |  | BTY1502DX02DIO1PLM5_Ch04Flt_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4310 | BTY1502DX02 AHI Module 5 Channel 4 Fault Alarm |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop02 |  | BTY1502DX02DIO1PLM5_Ch05Flt_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4311 | BTY1502DX02 AHI Module 5 Channel 5 Fault Alarm |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop02 |  | BTY1502DX02DIO1PLM5_Ch06Flt_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4312 | BTY1502DX02 AHI Module 5 Channel 6 Fault Alarm |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop02 |  | BTY1502DX02DIO1PLM5_Ch07Flt_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4313 | BTY1502DX02 AHI Module 5 Channel 7 Fault Alarm |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop02 | Slot5_A | BTY1502DX02DIO1PLM5_Flt_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4314 | BTY1502DX02 AHI Module 5 Fault Alarm |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop02 |  | BTY1502DX02DIO1PLM6_Ch00Flt_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4315 | BTY1502DX02 AHI Module 6 Channel 0 Fault Alarm |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop02 |  | BTY1502DX02DIO1PLM6_Ch01Flt_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4316 | BTY1502DX02 AHI Module 6 Channel 1 Fault Alarm |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop02 |  | BTY1502DX02DIO1PLM6_Ch02Flt_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4317 | BTY1502DX02 AHI Module 6 Channel 2 Fault Alarm |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop02 |  | BTY1502DX02DIO1PLM6_Ch03Flt_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4318 | BTY1502DX02 AHI Module 6 Channel 3 Fault Alarm |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop02 |  | BTY1502DX02DIO1PLM6_Ch04Flt_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4319 | BTY1502DX02 AHI Module 6 Channel 4 Fault Alarm |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop02 |  | BTY1502DX02DIO1PLM6_Ch05Flt_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4320 | BTY1502DX02 AHI Module 6 Channel 5 Fault Alarm |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop02 |  | BTY1502DX02DIO1PLM6_Ch06Flt_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4321 | BTY1502DX02 AHI Module 6 Channel 6 Fault Alarm |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop02 |  | BTY1502DX02DIO1PLM6_Ch07Flt_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4322 | BTY1502DX02 AHI Module 6 Channel 7 Fault Alarm |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop02 | Slot6_A | BTY1502DX02DIO1PLM6_Flt_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4323 | BTY1502DX02 AHI Module 6 Fault Alarm |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop02 |  | BTY1502DX02DIO1PLM7_Ch00Flt_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4324 | BTY1502DX02 AHI Module 7 Channel 0 Fault Alarm |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop02 |  | BTY1502DX02DIO1PLM7_Ch01Flt_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4325 | BTY1502DX02 AHI Module 7 Channel 1 Fault Alarm |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop02 |  | BTY1502DX02DIO1PLM7_Ch02Flt_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4326 | BTY1502DX02 AHI Module 7 Channel 2 Fault Alarm |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop02 |  | BTY1502DX02DIO1PLM7_Ch03Flt_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4327 | BTY1502DX02 AHI Module 7 Channel 3 Fault Alarm |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop02 |  | BTY1502DX02DIO1PLM7_Ch04Flt_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4328 | BTY1502DX02 AHI Module 7 Channel 4 Fault Alarm |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop02 |  | BTY1502DX02DIO1PLM7_Ch05Flt_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4329 | BTY1502DX02 AHI Module 7 Channel 5 Fault Alarm |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop02 |  | BTY1502DX02DIO1PLM7_Ch06Flt_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4330 | BTY1502DX02 AHI Module 7 Channel 6 Fault Alarm |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop02 |  | BTY1502DX02DIO1PLM7_Ch07Flt_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4331 | BTY1502DX02 AHI Module 7 Channel 7 Fault Alarm |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop02 | Slot7_A | BTY1502DX02DIO1PLM7_Flt_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4332 | BTY1502DX02 AHI Module 7 Fault Alarm |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop02 |  | BTY1502DX02DIO1PLM9_Ch00Flt_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4333 | BTY1502DX02 AHO Module 9 Channel 0 Fault Alarm |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop02 |  | BTY1502DX02DIO1PLM9_Ch01Flt_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4334 | BTY1502DX02 AHO Module 9 Channel 1 Fault Alarm |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop02 |  | BTY1502DX02DIO1PLM9_Ch02Flt_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4335 | BTY1502DX02 AHO Module 9 Channel 2 Fault Alarm |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop02 |  | BTY1502DX02DIO1PLM9_Ch03Flt_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4336 | BTY1502DX02 AHO Module 9 Channel 3 Fault Alarm |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop02 | Slot9_A | BTY1502DX02DIO1PLM9_Flt_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4337 | BTY1502DX02 AHO Module 9 Fault Alarm |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.BTY1502.FieldIO |  | BTY1502DX02VDC01_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4338 | West Turkeys Nest DIO Box 2 24VDC Output Control Supply (Q143) Failure |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.BTY1502.FieldIO |  | BTY1502DX02VDC02_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4339 | West Turkeys Nest DIO Box 2 24VDC GW1 Control Supply (Q157) Failure |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.BTY1502.FieldIO |  | BTY1502DX02VDC03_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4340 | West Turkeys Nest DIO Box 2 24VDC Instrument Control Supply (Q164) Failure |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.BTY1502.FieldIO |  | BTY1502DX02VDC04_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4341 | West Turkeys Nest DIO Box 2 24VDC Transmitter Control Supply (Q168) Failure |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.BTY1502.FieldIO |  | BTY1502DX02VDC05_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4342 | West Turkeys Nest DIO Box 2 24VDC Process Water Control Supply (Q172) Failure |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1101.FieldIO |  | BTY1502DX02VDC06_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4343 | West Turkeys Nest DIO Box 2 24VDC BPP1101 Control Supply (Q176) Failure |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1102.FieldIO |  | BTY1502DX02VDC07_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4344 | West Turkeys Nest DIO Box 2 24VDC BPP1102 Control Supply (Q180) Failure |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BPP1106.FieldIO |  | BTY1502DX02VDC08_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4345 | West Turkeys Nest DIO Box 2 24VDC BPP1106 Control Supply (Q184) Failure |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BPP1107.FieldIO |  | BTY1502DX02VDC09_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4346 | West Turkeys Nest DIO Box 2 24VDC BPP1107 Control Supply (Q188) Failure |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BSTD1106.FieldIO |  | BTY1502DX02VDC10_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4347 | West Turkeys Nest DIO Box 2 24VDC BSTD1106 Control Supply (Q192) Failure |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BSTD1107.FieldIO |  | BTY1502DX02VDC11_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4348 | West Turkeys Nest DIO Box 2 24VDC BSTD1107 Control Supply (Q196) Failure |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop03 |  | BTY1502DX03DIO1PLM0_ComFlt_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4350 | BTY1502DX03 CRA Comms Module 0 Communications Fault Alarm |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop03 | Slot0_A | BTY1502DX03DIO1PLM0_Flt_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4351 | BTY1502DX03 CRA Comms Module 0 Fault Alarm |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop03 | Slot1_A | BTY1502DX03DIO1PLM1_Flt_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4352 | BTY1502DX03 DI Module 1 Fault Alarm |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop03 |  | BTY1502DX03DIO1PLM1_Grp1Flt_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4353 | BTY1502DX03 DI Module 1 Group 1 Fault Alarm |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop03 |  | BTY1502DX03DIO1PLM1_Grp2Flt_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4354 | BTY1502DX03 DI Module 1 Group 2 Fault Alarm |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop03 |  | BTY1502DX03DIO1PLM3_Ch00Flt_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4355 | BTY1502DX03 AHI Module 3 Channel 0 Fault Alarm |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop03 |  | BTY1502DX03DIO1PLM3_Ch01Flt_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4356 | BTY1502DX03 AHI Module 3 Channel 1 Fault Alarm |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop03 |  | BTY1502DX03DIO1PLM3_Ch02Flt_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4357 | BTY1502DX03 AHI Module 3 Channel 2 Fault Alarm |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop03 |  | BTY1502DX03DIO1PLM3_Ch03Flt_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4358 | BTY1502DX03 AHI Module 3 Channel 3 Fault Alarm |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop03 |  | BTY1502DX03DIO1PLM3_Ch04Flt_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4359 | BTY1502DX03 AHI Module 3 Channel 4 Fault Alarm |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop03 |  | BTY1502DX03DIO1PLM3_Ch05Flt_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4360 | BTY1502DX03 AHI Module 3 Channel 5 Fault Alarm |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC01 |  | BMC131INC01_AlmAck | BR4_Cluster1 | BPL131 | DIGITAL | %M4361 | BMC131 INC01 Alarm Acknowledged |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop03 |  | BTY1502DX03DIO1PLM3_Ch07Flt_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4362 | BTY1502DX03 AHI Module 3 Channel 7 Fault Alarm |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop03 | Slot3_A | BTY1502DX03DIO1PLM3_Flt_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4363 | BTY1502DX03 AHI Module 3 Fault Alarm |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop03 |  | BTY1502DX03DIO1PLM4_Ch00Flt_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4364 | BTY1502DX03 AHI Module 4 Channel 0 Fault Alarm |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop03 |  | BTY1502DX03DIO1PLM4_Ch01Flt_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4365 | BTY1502DX03 AHI Module 4 Channel 1 Fault Alarm |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop03 |  | BTY1502DX03DIO1PLM4_Ch02Flt_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4366 | BTY1502DX03 AHI Module 4 Channel 2 Fault Alarm |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop03 |  | BTY1502DX03DIO1PLM4_Ch03Flt_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4367 | BTY1502DX03 AHI Module 4 Channel 3 Fault Alarm |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop03 |  | BTY1502DX03DIO1PLM4_Ch04Flt_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4368 | BTY1502DX03 AHI Module 4 Channel 4 Fault Alarm |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop03 |  | BTY1502DX03DIO1PLM4_Ch05Flt_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4369 | BTY1502DX03 AHI Module 4 Channel 5 Fault Alarm |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop03 |  | BTY1502DX03DIO1PLM4_Ch06Flt_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4370 | BTY1502DX03 AHI Module 4 Channel 6 Fault Alarm |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop03 |  | BTY1502DX03DIO1PLM4_Ch07Flt_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4371 | BTY1502DX03 AHI Module 4 Channel 7 Fault Alarm |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC02 |  | BMC131INC02_AlmAck | BR4_Cluster1 | BPL131 | DIGITAL | %M4372 | BMC131 INC02 Alarm Acknowledged |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop03 |  | BTY1502DX03VDC01_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4373 | West Turkeys Nest DIO Box 3 24VDC Output Control Supply (Q143) Failure |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop03 |  | BTY1502DX03VDC02_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4374 | West Turkeys Nest DIO Box 3 24VDC GW1 Control Supply (Q157) Failure |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop03 |  | BTY1502DX03VDC03_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4375 | West Turkeys Nest DIO Box 3 24VDC Instrument Control Supply (Q164) Failure |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop03 |  | BTY1502DX03VDC04_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4376 | West Turkeys Nest DIO Box 3 24VDC Transmitter Control Supply (Q168) Failure |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop03 |  | BTY1502DX03VDC05_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4377 | West Turkeys Nest DIO Box 3 24VDC BTY1502DX03 Field Control Supply (Q172) Failure |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop03 |  | BTY1502DX03VDC06_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4378 | West Turkeys Nest DIO Box 3 24VDC BPP1103 Field Control Supply (Q176) Failure |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC03 |  | BMC131INC03_AlmAck | BR4_Cluster1 | BPL131 | DIGITAL | %M4379 | BMC131 INC03 Alarm Acknowledged |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop03 |  | BTY1502DX03VDC08_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4380 | West Turkeys Nest DIO Box 3 24VDC BPP1105 Field Control Supply (Q184) Failure |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop03 |  | BTY1502DX03DIO1PLM3_Ch06Flt_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4381 | BTY1502DX03 AHI Module 3 Channel 6 Fault Alarm |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop03 | Slot4_A | BTY1502DX03DIO1PLM4_Flt_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4382 | BTY1502DX03 AHI Module 4 Fault Alarm |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop03 |  | BTY1502DX03VDC07_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4383 | West Turkeys Nest DIO Box 3 24VDC BPP1104 Field Control Supply (Q180) Failure |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.BTY1502.FV01.FieldIO.CB01 |  | BTY1502FV01CB01_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4384 | West Turkeys Nest 240VAC Flow Valve Power Circuit Breaker Open |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.BTY1502 |  | BTY1502LS01_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4388 | West Turkeys Nest West Turkeys Nest |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC03 |  | BMC131VAMPPR1_ComFlt_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4389 | BMC131 Incomer Vamp Relay Communications Fault Alarm |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC03 |  | BMC131VAMPPR1_ProFlt_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4390 | BMC131VAMPPR1 Vamp Arc Flash Protection Fault |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC03 |  | BMC131VAMPPR1_SysFlt_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4391 | BMC131VAMPPR1 Vamp Arc Flash Protection Fault Alarm |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1 |  | BPP1101_2_EqpAvlFlt_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4392 | No NPI and Process Water Pumps Available Fault Alarm |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1101 |  | BPP1101FS09_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4393 | BPP1101FS09 Pump Flow Switch Low Alarm |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1101 |  | BPP1101FS09_FailStp_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4394 | BPP1101FS09 Fail to Stop Alarm |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1101.FieldIO.FT03 |  | BPP1101FT03_Frz_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4395 | BPP1101FT03 Flow Transmitter Frozen Alarm |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1101.FieldIO.FT03 |  | BPP1101FT03_Hi_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4396 | BPP1101FT03 Pump Flow High Alarm |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1101.FieldIO.FT03 |  | BPP1101FT03_HiHi_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4397 | BPP1101FT03 NPI and Process Water Supply Flow High High Healthy |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1101.FieldIO.FT03 |  | BPP1101FT03_Lo_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4398 | BPP1101FT03 Flow Low Alarm |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1101 |  | BPP1101IS01_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4399 | BPP1101 Isolator Open Alarm |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1101.FieldIO.PT03 |  | BPP1101PT03_Frz_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4400 | BPP1101PT03 Pump Discharge Pressure Transmitter Frozen Alarm |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1101.FieldIO.PT03 |  | BPP1101PT03_HiHi_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4401 | BPP1101PT03 System Pressure High High Alarm |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1101.FieldIO.PT03 |  | BPP1101PT03_LoLo_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4402 | BPP1101PT03 Pump Discharge Pressure Low Low Alarm |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1101.FieldIO.PT10 |  | BPP1101PT10_Diff_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4403 | NPI and Process Water Network Pressure Variance (PT10/PT11) Alarm |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1101.FieldIO.PT10 |  | BPP1101PT10_Frz_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4404 | BPP1101PT10 System Pressure Frozen Alarm |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1101.FieldIO.PT10 |  | BPP1101PT10_Hi_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4405 | BPP1101PT10 Discharge Header Pressure High Alarm |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1101.FieldIO.PT10 |  | BPP1101PT10_Lo_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4406 | BPP1101PT10 Discharge Header Pressure Low Akarn |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1101.FieldIO.PT11 |  | BPP1101PT11_Frz_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4407 | BPP1101PT11 Discharge Header Pressure Transmitter Frozen Alarm |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1101.FieldIO.PT11 |  | BPP1101PT11_Hi_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4408 | BPP1101PT11 System Pressure High Alarm |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1101.FieldIO.PT11 |  | BPP1101PT11_Lo_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4409 | BPP1101PT11 Discharge Header Pressure Low Alarm |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1101.Sub.CB01 |  | BPP1101TRP01_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4410 | BPP1101 Main Circuit Breaker Tripped Alarm |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1101.VS01 |  | BPP1101VS01_ComFlt_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4411 | BPP1101VS01 VSD Communications Fault Alarm |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1101.VS01 |  | BPP1101VS01_Flt_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4412 | BPP1101VS01 VSD Fault Alarm |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1101.VS01 |  | BPP1101VS01SY01_Flt_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4413 | BPP1101VS01 Safety Relay Fault Healthy |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1102 |  | BPP1102FS10_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4414 | BPP1102FS10 Pump Flow Switch Low Alarm |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1102 |  | BPP1102FS10_FailStp_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4415 | BPP1102FS10 Pump Fail to Stop Alarm |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1102 |  | BPP1102IS01_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4416 | BPP1102 Isolator Open Alarm |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1102.FieldIO.PT04 |  | BPP1102PT04_Frz_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4417 | BPP1102PT04 Pump Discharge Pressure Transmitter Frozen Alarm |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1102.FieldIO.PT04 |  | BPP1102PT04_HiHi_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4418 | BPP1102PT04 Pump Discharge Pressure High High Alarm |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1102.FieldIO.PT04 |  | BPP1102PT04_LoLo_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4419 | BPP1102PT04 Pump Discharge Pressure Low Low Alarm |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1102.Sub.CB01 |  | BPP1102TRP01_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4420 | BPP1102 Main Circuit Breaker Tripped Alarm |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1102.VS01 |  | BPP1102VS01_ComFlt_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4421 | BPP1107VS01 VSD Communications Fault Alarm |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1102.VS01 |  | BPP1102VS01_Flt_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4422 | BPP1102VS01 VSD Fault Alarm |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1102.VS01 |  | BPP1102VS01SY01_Flt_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4423 | BPP1102VS01 Safety Relay Fault Healthy |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT |  | BPP1103_4_5_EqpAvlFlt_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4424 | No Transfer Pumps Available Fault Alarm |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1103 |  | BPP1103_FailStp_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4425 | Water Transfer Pump 1 Fail to Stop Alarm |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1103.FieldIO.FT03 |  | BPP1103FT03_Frz_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4426 | BPP1103FT03 Pump Flow Transmitter Frozen Alarm |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1103.FieldIO.FT03 |  | BPP1103FT03_LoLo_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4427 | BPP1103FT03 Pump Flow Low Low Alarm |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1103.FieldIO.FT06 |  | BPP1103FT06_Frz_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4428 | BPP1103FT06 Transfer Flow Transmitter Frozen Alarm |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1103.FieldIO.FT06 |  | BPP1103FT06_HiHi_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4429 | BPP1103FT06 Transfer Flow High High Alarm |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1103.FieldIO.FT06 |  | BPP1103FT06_LkFlt_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4430 | BPP1103FT06 Water Transfer Pipeline Leak Detected Alarm |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1103.FieldIO.FT06 |  | BPP1103FT06_RevFlw_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4431 | BPP1103FT06 Water Transfer Pumps Reverse Flow Detected Alarm |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1103 |  | BPP1103IS01_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4432 | BPP1103 Isolator Alarm |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1103.FieldIO.PT05 |  | BPP1103PT05_Frz_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4433 | BPP1103PT05 Pump Discharge Pressure Transmitter Frozen Alarm |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1103.FieldIO.PT05 |  | BPP1103PT05_HiHi_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4434 | BPP1103PT05 Pump Discharge Pressure High High Alarm |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1103.FieldIO.PT05 |  | BPP1103PT05_LoLo_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4435 | BPP1103PT05 Pump Discharge Pressure Low Low Alarm |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1103.FieldIO.PT08 |  | BPP1103PT08_Frz_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4436 | BPP1103PT08 Water Transfer System Pressure Transmitter Frozen Alarm |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1103.FieldIO.PT08 |  | BPP1103PT08_HiHi_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4437 | BPP1103PT08 Water Transfer System Pressure High High Alarm |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1103.FieldIO.PT08 |  | BPP1103PT08_Lo_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4438 | HME Standpipe Pump 1 PT08 Lo Alarm |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1103.Sub.CB01 |  | BPP1103TRP01_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4439 | BPP1103 Main Circuit Breaker Tripped Alarm |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1103.VS01 |  | BPP1103VS01_ComFlt_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4440 | BPP1103VS01 VSD Communications Fault Alarm |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1103.VS01 |  | BPP1103VS01_Flt_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4441 | BPP1103VS01 VSD Fault Alarm |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.BC01.CB01 |  | BSR131BC01TRP01_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4442 | BSR131 Battery Charger 1 Main Circuit Breaker Tripped |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1103.VS01 |  | BPP1103VS01SY01_Flt_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4443 | BPP1103VS01 Safety Relay Fault Alarm |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1104 |  | BPP1104_FailStp_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4444 | Water Transfer Pump 2 Fail to Stop Alarm |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1104.FieldIO.FT04 |  | BPP1104FT04_Frz_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4445 | BPP1104FT04 Pump Flow Transmitter Frozen Alarm |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1104.FieldIO.FT04 |  | BPP1104FT04_LoLo_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4446 | BPP1104FT04 Pump Flow Low Low Alarm |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1104 |  | BPP1104IS01_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4447 | BPP1104 Isolator Open Alarm |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1104.FieldIO.PT06 |  | BPP1104PT06_Frz_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4448 | BPP1104PT06 Pump Discharge Pressure Transmitter Frozen Alarm |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1104.FieldIO.PT06 |  | BPP1104PT06_HiHi_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4449 | BPP1104PT06 Pump Discharge Pressure High High Alarm |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1104.FieldIO.PT06 |  | BPP1104PT06_LoLo_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4450 | BPP1104PT06 Pump Discharge Pressure Low Low Alarm |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1104.Sub.CB01 |  | BPP1104TRP01_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4451 | BPP1104 Main Circuit Breaker Tripped Alarm |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1104.VS01 |  | BPP1104VS01_ComFlt_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4452 | BPP1104VS01 VSD Communications Fault Alarm |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1104.VS01 |  | BPP1104VS01_Flt_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4453 | BPP1104VS01 VSD Fault Alarm |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.BC02.CB01 |  | BSR131BC02TRP01_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4454 | BSR131 Battery Charger 2 Main Circuit Breaker Tripped |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1104.VS01 |  | BPP1104VS01SY01_Flt_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4455 | BPP1104VS01 Safety Relay Fault Alarm |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1105 |  | BPP1105_FailStp_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4456 | Water Transfer Pump 3 Fail to Stop Alarm |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1105.FieldIO.FT05 |  | BPP1105FT05_Frz_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4457 | BPP1105FT05 Pump Flow Transmitter Frozen Alarm |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1105.FieldIO.FT05 |  | BPP1105FT05_LoLo_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4458 | BPP1105FT05 Pump Flow Low Low Alarm |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1105 |  | BPP1105IS01_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4459 | BPP1105 Isolator Open Alarm |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1105.FieldIO.PT07 |  | BPP1105PT07_Frz_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4460 | BPP1105PT07 Pump Discharge Pressure Transmitter Frozen Alarm |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1105.FieldIO.PT07 |  | BPP1105PT07_HiHi_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4461 | BPP1105PT07 Pump Discharge Pressure High High Alarm |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1105.FieldIO.PT07 |  | BPP1105PT07_LoLo_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4462 | BPP1105PT07 Pump Discharge Pressure Low Low Alarm |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1105.Sub.CB01 |  | BPP1105TRP01_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4463 | BPP1105 Main Circuit Breaker Tripped Alarm |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1105.VS01 |  | BPP1105VS01_ComFlt_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4464 | BPP1105VS01 VSD Communications Fault Alarm |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1105.VS01 |  | BPP1105VS01_Flt_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4465 | BPP1105VS01 VSD Fault Alarm |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1105.VS01 |  | BPP1105VS01SY01_Flt_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4466 | BPP1105VS01 Safety Relay Fault Alarm |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1 |  | BPP1106_7_EqpAvlFlt_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4467 | No Standpipe Pumps Available Fault Alarm |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BPP1106 |  | BPP1106_RunNoVlv_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4468 | BPP1106 Pump Running with No Valve Open Alarm |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BPP1106 |  | BPP1106FS07_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4469 | BPP1106FS07 Pump Flow Switch Low Alarm |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BPP1106 |  | BPP1106FS07_FailStp_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4470 | BPP1106FS07 Fail to Stop Alarm |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BPP1106 |  | BPP1106IS01_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4471 | BPP1106 Isolator Open Alarm |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BPP1106.FieldIO.PT01 |  | BPP1106PT01_Frz_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4472 | BPP1106PT01 Pump Discharge Pressure Transmitter Frozen Alarm |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BPP1106.FieldIO.PT01 |  | BPP1106PT01_HiHi_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4473 | BPP1106PT01 Pump Discharge Pressure High High Alarm |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BPP1106.FieldIO.PT01 |  | BPP1106PT01_LoLo_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4474 | BPP1106PT01 Pump Discharge Pressure Low Low Alarm |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BPP1106.Sub.CB01 |  | BPP1106TRP01_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4475 | BPP1106 Main Circuit Breaker Tripped Alarm |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BPP1106.VS01 |  | BPP1106VS01_ComFlt_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4476 | BPP1106VS01 VSD Communications Fault Alarm |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BPP1106.VS01 |  | BPP1106VS01_Flt_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4477 | BPP1106VS01 VSD Fault Alarm |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BPP1106.VS01 |  | BPP1106VS01SY01_Flt_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4478 | BPP1106VS01 Safety Relay Fault Healthy |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BPP1107 |  | BPP1107FS08_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4479 | BPP1107FS08 Pump Flow Switch Low Alarm |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BPP1107 |  | BPP1107FS08_FailStp_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4480 | BPP1107FS08 Fail to Stop Alarm |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BPP1107 |  | BPP1107IS01_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4481 | BPP1107 Isolator Open Alarm |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BPP1107.FieldIO.PT02 |  | BPP1107PT02_Frz_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4482 | BPP1107PT02 Pump Discharge Pressure Transmitter Frozen Alarm |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BPP1107.FieldIO.PT02 |  | BPP1107PT02_HiHi_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4483 | BPP1107PT02 Pump Discharge Pressure High High Alarm |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BPP1107.FieldIO.PT02 |  | BPP1107PT02_LoLo_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4484 | BPP1107PT02 Pump Discharge Pressure Low Low Alarm |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BPP1107.Sub.CB01 |  | BPP1107TRP01_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4485 | BPP1107 Main Circuit Breaker Tripped Alarm |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BPP1107.VS01 |  | BPP1107VS01_ComFlt_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4486 | BPP1107VS01 VSD Communications Fault Alarm |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BPP1107.VS01 |  | BPP1107VS01_Flt_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4487 | BPP1107VS01 VSD Fault Alarm |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BPP1107.VS01 |  | BPP1107VS01SY01_Flt_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4488 | BPP1107VS01 Safety Relay Fault Alarm |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.BC02.BACS |  | BSR131BC02_BACSComFlt_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4489 | BSR131 Battery Charger BC02 BACSComFlt Alarm |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.BC02.BACS |  | BSR131BC02_BACSFlt_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4490 | BSR131 Battery Charger BC02 BACSFlt Alarm |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.BC02.Cordex |  | BSR131BC02_CordexComFlt_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4491 | BSR131 Battery Charger BC02 CordexComFlt Alarm |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.BC02.Cordex |  | BSR131BC02_CordexFlt_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4492 | BSR131 Battery Charger BC02 CordexFlt Alarm |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.DB01 |  | BSR131DB01XS01_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4493 | BSR131DB01 Surge Protection (SD107) Alarm |  |  | BS1_Tags
BR4.SRV.PWR.BSR131 |  | BSR131DX01XS01_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4494 | BSR131DX01 24VDC Power Supply 1 Fail Alarm |  |  | BS1_Tags
BR4.SRV.PWR.BSR131 |  | BSR131DX01XS02_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4495 | BSR131DX01 24VDC Power Supply 2 Fail Alarm |  |  | BS1_Tags
BR4.SRV.PWR.BSR131 |  | BSR131PN01PS01_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4496 | BSR131PN01 Switchroom Pressurisation Fan Filter Blocked Alarm |  |  | BS1_Tags
BR4.SRV.PWR.BSR131 |  | BSR131PN01XS01_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4497 | BSR131PN01 Air Conditioner Fault Alarm |  |  | BS1_Tags
BR4.SRV.PWR.BSR131 |  | BSR131PN01XS02_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4498 | BSR131 Switchroom Control Panel Air Conditioner Filter Blocked Alarm |  |  | BS1_Tags
BR4.SRV.PWR.BSR131 |  | BSR131PN01XS03_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4499 | BSR131PN01 Air Con 1 Fault Alarm |  |  | BS1_Tags
BR4.SRV.PWR.BSR131 |  | BSR131PN01XS04_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4500 | BSR131 Switchroom Control Panel Air Con 2 Healthy |  |  | BS1_Tags
BR4.SRV.PWR.BSR131 |  | BSR131PN01XS05_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4501 | BSR131PN01 Switchroom Humidity Alarm |  |  | BS1_Tags
BR4.SRV.PWR.BSR131 |  | BSR131PN01XS06_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4502 | NPI Hub Switchroom Control Panel 1 Air Conditioner 6 - Airlock Fault Alarm |  |  | BS1_Tags
BR4.SRV.PWR.BSR131 |  | BSR131PN01XS07_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4503 | NPI Hub Switchroom Control Panel 1 Air Conditioner 7 - Airlock Fault Alarm |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.DB01 |  | BSR131UP01DB01B1_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4504 | NEP130 240VAC Primary UPS Circuit Breaker Open Alarm |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.DB01 |  | BSR131UP01DB01B2_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4505 | DX03 240VAC UPS Circuit Breaker Open Alarm |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.DB01 |  | BSR131UP01DB01B3_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4506 | BSR131FIP01 Fire Panel 240VAC UPS Circuit Breaker Open Alarm |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.DB01 |  | BSR131UP01DB01B4_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4507 | BSR131FSS01PN01 Supression Control Panel Breaker Open Alarm |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.DB01 |  | BSR131UP01DB01R1_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4508 | DX01 Primary 240VAC UPS Circuit Breaker Open Alarm |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.DB01 |  | BSR131UP01DB01R2_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4509 | NEP130 240VAC Secondary UPS Circuit Breaker Open Alarm |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.DB01 |  | BSR131UP01DB01R3_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4510 | DX04 240VAC UPS Circuit Breaker Open Alarm |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.DB01 |  | BSR131UP01DB01R4_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4511 | BSR131VES01 VESDA Fire Detection Panel Breaker Open Alarm |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.DB01 |  | BSR131UP01DB01R5_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4512 | BTY1502AX01 240VAC UPS Circuit Breaker Open Alarm |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.DB01 |  | BSR131UP01DB01W1_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4513 | DX01 Secondary 240VAC UPS Circuit Breaker Open Alarm |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.DB01 |  | BSR131UP01DB01W2_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4514 | DX02 240VAC UPS Circuit Breaker Open Alarm |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.DB01 |  | BSR131UP01DB01W3_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4515 | HVAC Panel 240VAC UPS Circuit Breaker Open Alarm |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.DB01 |  | BSR131UP01DB01W4_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4516 | Cardax 240VAC UPS Circuit Breaker Open Alarm |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.DB01 |  | BSR131UP01DB01W5_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4517 | BPQE2115MC01 Potable Water 240VAC UPS Circuit Breaker Alarm |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.DB01 |  | BSR131UP01DB01XS01_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4518 | BSR131UP01DB01 Surge Protection (SD106) Alarm |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BSTD1106.FieldIO.FT03 |  | BSTD1106FT03_Frz_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4519 | BSTD1106FT03 Flow Transmitter Frozen Alarm |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BSTD1106.FieldIO.FT03 |  | BSTD1106FT03_Hi_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4520 | BSTD1106FT03 Flow High Alarm |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BSTD1106.FieldIO.FT03 |  | BSTD1106FT03_Rtn_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4521 | BPP1103FT03 Pump Flow Detected with Valve Closed Alarm |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BSTD1106.FV03 |  | BSTD1106FV03_LocFlt_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4522 | West Turkeys Nest LME Standpipe Valve Left in Local Alarm |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BSTD1107 |  | BSTD1107FT02_Frz_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4523 | BSTD1107FT02 Flow Transmitter Frozen Alarm |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BSTD1107 |  | BSTD1107FT02_Hi_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4524 | BSTD1107FT02 Flow High Alarm |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BSTD1107 |  | BSTD1107FT02_Rtn_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4525 | BSTD1107FT02 Flow Detected with Valve Closed Alarm |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BSTD1107.FV02 |  | BSTD1107FV02_LocFlt_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4526 | West Turkeys Nest HME Standpipe Valve Left in Local Alarm |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.P3FIREWATER.BTK2101.FieldIO.LT01 |  | BTK2101LT01_Hi_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4527 | BTK2101LT01 Hi Alarm |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.P3FIREWATER.BTK2101.FieldIO.LT01 |  | BTK2101LT01_HiHi_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4528 | BTK2101LT01 NPI Fire Water Tank Level High High Alarm |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.P3FIREWATER.BTK2101.FieldIO.LT01 |  | BTK2101LT01_Lo_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4529 | NPI Fire Water Tank 1 LT01 Level Low Alarm |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.P3FIREWATER.BTK2101.FieldIO.LT01 |  | BTK2101LT01_LoLo_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4530 | BTK2101LT01 Level Low Low Alarm |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.P3FIREWATER.BTK2102.FieldIO.LT01 |  | BTK2102LT01_Hi_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4531 | BTK2102LT01 Hi Alarm |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.P3FIREWATER.BTK2102.FieldIO.LT01 |  | BTK2102LT01_HiHi_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4532 | BTK2102LT01 NPI Fire Water Tank LT01 Level High High Alarm |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.P3FIREWATER.BTK2102.FieldIO.LT01 |  | BTK2102LT01_Lo_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4533 | BTK2101LT01 Tank Level Low Healthy |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.P3FIREWATER.BTK2102.FieldIO.LT01 |  | BTK2102LT01_LoLo_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4534 | BTK2101LT01 Tank Level Low Low Alarm |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.BTY1502.FieldIO.FT02 |  | BTY1502FT02_Flt_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4535 | BTY1502FT02 West Turkeys Nest Recirculation Flow Fault Alarm |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.BTY1502.FieldIO.FT02 |  | BTY1502FT02_Frz_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4536 | BTY1502FT02 Recirculation FlowTransmitter Frozen Alarm |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.BTY1502.FieldIO.FT02 |  | BTY1502FT02_Hi_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4537 | BTY1502FT02 Recirculation Flow High Alarm |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.BTY1502.FieldIO.FT02 |  | BTY1502FT02_Lo_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4538 | BTY1502FT02 Recirculation Flow Low Alarm |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.BTY1502.FV01 |  | BTY1502FV01_LocFlt_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4539 | BTY1502FV01 Left in Local Alarm |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.BTY1502.FieldIO.LT01 |  | BTY1502LT01_Frz_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4540 | BTY1502 Level Transmitter Freeze Alarm |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.BTY1502.FieldIO.LT01 |  | BTY1502LT01_Hi_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4541 | BTY1502LT01 West Turkeys Nest Level High Alarm |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.BTY1502.FieldIO.LT01 |  | BTY1502LT01_HiHi_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4542 | BTY1502LT01 West Turkeys Nest Level High High Alarm |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.BTY1502.FieldIO.LT01 |  | BTY1502LT01_Lo_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4543 | BTY1502LT01 West Turkeys Nest Level Low Alarm |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.BTY1502.FieldIO.LT01 |  | BTY1502LT01_LoLo_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4544 | BTY1502LT01 Turkeys Nest Low Low Alarm |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.BTY1502.FieldIO.LT01 |  | BTY1502LT01_SigFlt_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4545 | BTY1502LT01 Level Discrepancy Fault Alarm |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.BTY1502.FieldIO.LT02 |  | BTY1502LT02_Frz_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4546 | East Turkeys Nest Raw Water Remote Mode LT02 Freeze Alarm |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.BTY1502.FieldIO.LT02 |  | BTY1502LT02_Hi_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4547 | BTY1502LT02 West Turkeys Nest Level High Alarm |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.BTY1502.FieldIO.LT02 |  | BTY1502LT02_HiHi_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4548 | BTY1502LT02 West Turkeys Nest High High Alarm |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.BTY1502.FieldIO.LT02 |  | BTY1502LT02_Lo_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4549 | BTY1502LT02 West Turkeys Nest Low Alarm |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.BTY1502.FieldIO.LT02 |  | BTY1502LT02_LoLo_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4550 | BTK2101LT02 NPI Fire Water Tank Level Low Low Alarm |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.BTY1502.FieldIO.LT02 |  | BTY1502LT02_SigFlt_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4551 | BTY1502LT02 West Turkeys Nest Signal Fault Alarm |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.BTY1502.FieldIO.PT01 |  | BTY1502PT01_Hi_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4552 | BTY1502PT01 WTN East Collection Header In Flow Pressure High Alarm |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.BTY1502.FieldIO.PT01 |  | BTY1502PT01_Lo_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4553 | BTY1502PT01 WTN East Collection Header In Flow Pressure Low Alarm |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.BTY1502.FieldIO.PT03 |  | BTY1502PT03_Hi_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4554 | BTY1502PT03 WTN West Collection Header In Flow Pressure High Alarm |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.UP01 |  | BSR131UP01XS01_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4592 | BSR131 UPS Surge Filter Alarm |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.CB01 |  | BSR131UP01TRP01_A | BR4_Cluster1 | BPL131 | DIGITAL | %M4593 | BSR131 UPS Main Circuit Breaker Tripped |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.BC02.BACS | DatOK | BSR131BC02_BACSDatOK | BR4_Cluster1 | BPL131 | DIGITAL | %M4594 | BSR131BC02 Battery Charger BACS Data Valid |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.BC02.Cordex | DatOK | BSR131BC02_CordexDatOK | BR4_Cluster1 | BPL131 | DIGITAL | %M4595 | BSR131BC02 Battery Charger Cordex Data Valid |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | DatOK | BSR131UP01_BACSDatOK | BR4_Cluster1 | BPL131 | DIGITAL | %M4596 | BSR131UP01 Data Valid |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC03.MasterPact | FltSts1OK | BMC131INC03PR1DAT1_FltSts1OK | BR4_Cluster1 | BPL131 | INT | %MW1064 | BMC131INC03 Process Incomer MasterPact Fault Status 1 Data Valid |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC03.MasterPact | FltSts1 | BMC131INC03PR1DAT1_FltSts1 | BR4_Cluster1 | BPL131 | INT | %MW1065 | BMC131INC03 Process Incomer MasterPact Fault Status 1 |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC03.MasterPact | FltSts2OK | BMC131INC03PR1DAT1_FltSts2OK | BR4_Cluster1 | BPL131 | INT | %MW1066 | BMC131INC03 Process Incomer MasterPact Fault Status 2 Data Valid |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC03.MasterPact | FltSts2 | BMC131INC03PR1DAT1_FltSts2 | BR4_Cluster1 | BPL131 | INT | %MW1067 | BMC131INC03 Process Incomer MasterPact Fault Status 2 |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC01.MasterPact | FltSts1OK | BMC131INC01PR1DAT1_FltSts1OK | BR4_Cluster1 | BPL131 | INT | %MW914 | BMC131INC01 Process Incomer MasterPact Fault Status 1 Data Valid |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC01.MasterPact | FltSts1 | BMC131INC01PR1DAT1_FltSts1 | BR4_Cluster1 | BPL131 | INT | %MW915 | BMC131INC01 Process Incomer MasterPact Fault Status 1 |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC01.MasterPact | FltSts2OK | BMC131INC01PR1DAT1_FltSts2OK | BR4_Cluster1 | BPL131 | INT | %MW916 | BMC131INC01 Process Incomer MasterPact Fault Status 2 Data Valid |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC01.MasterPact | FltSts2 | BMC131INC01PR1DAT1_FltSts2 | BR4_Cluster1 | BPL131 | INT | %MW917 | BMC131INC01 Process Incomer MasterPact Fault Status 2 |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC02.MasterPact | FltSts1OK | BMC131INC02PR1DAT1_FltSts1OK | BR4_Cluster1 | BPL131 | INT | %MW990 | BMC131INC02 Process Incomer MasterPact Fault Status 1 Data Valid |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC02.MasterPact | FltSts1 | BMC131INC02PR1DAT1_FltSts1 | BR4_Cluster1 | BPL131 | INT | %MW991 | BMC131INC02 Process Incomer MasterPact Fault Status 1 |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC02.MasterPact | FltSts2OK | BMC131INC02PR1DAT1_FltSts2OK | BR4_Cluster1 | BPL131 | INT | %MW992 | BMC131INC02 Process Incomer MasterPact Fault Status 2 Data Valid |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC02.MasterPact | FltSts2 | BMC131INC02PR1DAT1_FltSts2 | BR4_Cluster1 | BPL131 | INT | %MW993 | BMC131INC02 Process Incomer MasterPact Fault Status 2 |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC03 |  | BMC131INC03PR1DAT1 | BR4_Cluster1 | BPL131 | INT | %MW1050[73] | BMC131 Generator Bus Incomer Protection Relay Status Data for HMI Display |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC03 |  | BPL131_CfgID | BR4_Cluster1 | BPL131 | INT | %MW1128 | NPI Hub PLC CPU Current Build Number |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131 |  | BPL131_ScnAvg | BR4_Cluster1 | BPL131 | INT | %MW1136 | NPI Hub PLC CPU Average Scan Time (ms) |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131 |  | BPL131_ScnMax | BR4_Cluster1 | BPL131 | INT | %MW1137 | NPI Hub PLC CPU Maximum Scan Time (ms) |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131 |  | BPL131_ScnMin | BR4_Cluster1 | BPL131 | INT | %MW1138 | NPI Hub PLC CPU Minimum Scan Time (ms) |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131 | ScanTm | BPL131_ScnVal | BR4_Cluster1 | BPL131 | INT | %MW1139 | NPI Hub PLC CPU Last Scan Time (ms) | 0 | 1000 | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131 |  | BPL131_SysScnAvg | BR4_Cluster1 | BPL131 | INT | %MW1140 | NPI Hub PLC CPU Average Overhead Scan Time (ms) |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131 |  | BPL131_SysScnMax | BR4_Cluster1 | BPL131 | INT | %MW1141 | NPI Hub PLC CPU Maximum Overhead Scan Time (ms) |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131 |  | BPL131_SysScnMin | BR4_Cluster1 | BPL131 | INT | %MW1142 | NPI Hub PLC CPU Minimum Overhead Scan Time (ms) |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131 |  | BPL131_SysScnVal | BR4_Cluster1 | BPL131 | INT | %MW1143 | NPI Hub PLC CPU Last Overhead Scan Time (ms) |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131 |  | BPL131_WD | BR4_Cluster1 | BPL131 | INT | %MW1144 | NPI Hub PLC CPU Heart Beat Watchdog |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131 |  | BPL131PLM0STS2 | BR4_Cluster1 | BPL131 | INT | %MW1145[4] | NPI Hub PLC CPU RIO Network Status Data |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1101 |  | BPP1101DRVSTAT | BR4_Cluster1 | BPL131 | INT | %MW1183 | Production Plant and NPI Water Supply Pump 1 Status Word |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1102 |  | BPP1102DRVSTAT | BR4_Cluster1 | BPL131 | INT | %MW1277 | Production Plant and NPI Water Supply Pump 2 Status Word |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1103 |  | BPP1103DRVSTAT | BR4_Cluster1 | BPL131 | INT | %MW1307 | Water Transfer Pump 1 Status Word |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1103.FieldIO.FT03 |  | BPP1103FT03_Tot | BR4_Cluster1 | BPL131 | INT | %MW1308[18] | Water Transfer Pump 1 Flow Rate (m3/h) Flow Totals |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1103.FieldIO.FT06 |  | BPP1103FT06_Tot | BR4_Cluster1 | BPL131 | INT | %MW1326[18] | Water Transfer Pump 1 Flow Rate (m3/h) Flow Totals |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1104 |  | BPP1104DRVSTAT | BR4_Cluster1 | BPL131 | INT | %MW1381 | Water Transfer Pump 2 Status Word |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1104.FieldIO.FT04 |  | BPP1104FT04_Tot | BR4_Cluster1 | BPL131 | INT | %MW1382[18] | Water Transfer Pump 2 Flow Rate (m3/h) Flow Totals |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1105.Sub.CB01 |  | BPP1105DRVSTAT | BR4_Cluster1 | BPL131 | INT | %MW1429 | Water Transfer Pump 3 Status Word |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1105.FieldIO.FT05 |  | BPP1105FT05_Tot | BR4_Cluster1 | BPL131 | INT | %MW1430[18] | Water Transfer Pump 3 Flow Rate (m3/h) Flow Totals |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BPP1106 |  | BPP1106DRVSTAT | BR4_Cluster1 | BPL131 | INT | %MW1477 | HME & LME Standpipe Pump 3 Status Word |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BPP1107 |  | BPP1107DRVSTAT | BR4_Cluster1 | BPL131 | INT | %MW1507 | HME & LME Standpipe Pump 4 Status Word |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop01 |  | BSR131DX01DIO1PLM0STS1 | BR4_Cluster1 | BPL131 | INT | %MW1532[7] | BSR131DX01 CRA Comms Module 0 Modules Status |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop01 |  | BSR131DX01DIO1PLM1STS1 | BR4_Cluster1 | BPL131 | INT | %MW1539 | BSR131DX01 DI Module 1 Status |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop01 |  | BSR131DX01DIO1PLM2STS1 | BR4_Cluster1 | BPL131 | INT | %MW1540 | BSR131DX01 DI Module 2 Status |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop01 |  | BSR131DX01DIO1PLM3STS1 | BR4_Cluster1 | BPL131 | INT | %MW1541 | BSR131DX01 DI Module 3 Status |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop01 |  | BSR131DX01DIO1PLM4STS1 | BR4_Cluster1 | BPL131 | INT | %MW1542 | BSR131DX01 DI Module 4 Status |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop01 |  | BSR131DX01DIO1PLM5STS1 | BR4_Cluster1 | BPL131 | INT | %MW1543 | BSR131DX01 DI Module 5 Status |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop01 |  | BSR131DX01DIO1PLM6STS1 | BR4_Cluster1 | BPL131 | INT | %MW1544 | BSR131DX01 DI Module 6 Status |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop01 |  | BSR131DX01DIO1PLM7STS1 | BR4_Cluster1 | BPL131 | INT | %MW1545 | BSR131DX01 DI Module 7 Status |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop01 |  | BSR131DX01DIO1PLM8STS1 | BR4_Cluster1 | BPL131 | INT | %MW1546[2] | BSR131DX01 DO Module 8 Status |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop04 |  | BTK2101DX04DIO1PLM0STS1 | BR4_Cluster1 | BPL131 | INT | %MW1644[7] | BTK2101DX04 CRA Comms Module 0 Modules Status |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop04 |  | BTK2101DX04DIO1PLM1STS1 | BR4_Cluster1 | BPL131 | INT | %MW1651 | BTK2101DX04 DI Module 1 Status |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop04 |  | BTK2101DX04DIO1PLM3STS1 | BR4_Cluster1 | BPL131 | INT | %MW1652[9] | BTK2101DX04 AHI Module 3 Module Status |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop02 |  | BTY1502DX02DIO1PLM0STS1 | BR4_Cluster1 | BPL131 | INT | %MW1798[7] | BTY1502DX02 CRA Comms Module 0 Modules Status |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop02 |  | BTY1502DX02DIO1PLM1STS1 | BR4_Cluster1 | BPL131 | INT | %MW1805 | BTY1502DX02 DI Module 1 Status |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop02 |  | BTY1502DX02DIO1PLM2STS1 | BR4_Cluster1 | BPL131 | INT | %MW1806 | BTY1502DX02 DI Module 2 Status |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop02 |  | BTY1502DX02DIO1PLM3STS1 | BR4_Cluster1 | BPL131 | INT | %MW1807 | BTY1502DX02 DI Module 3 Status |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop02 |  | BTY1502DX02DIO1PLM4STS1 | BR4_Cluster1 | BPL131 | INT | %MW1808[2] | BTY1502DX02 DO Module 4 Status |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop02 |  | BTY1502DX02DIO1PLM5STS1 | BR4_Cluster1 | BPL131 | INT | %MW1810[9] | BTY1502DX02 AHI Module 5 Module Status |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop02 |  | BTY1502DX02DIO1PLM6STS1 | BR4_Cluster1 | BPL131 | INT | %MW1956[9] | BTY1502DX02 AHI Module 6 Module Status |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop02 |  | BTY1502DX02DIO1PLM7STS1 | BR4_Cluster1 | BPL131 | INT | %MW2102[9] | BTY1502DX02 AHI Module 7 Module Status |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop02 |  | BTY1502DX02DIO1PLM9STS1 | BR4_Cluster1 | BPL131 | INT | %MW2248[5] | BTY1502DX02 AHO Module 9 Module Status |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop03 |  | BTY1502DX03DIO1PLM0STS1 | BR4_Cluster1 | BPL131 | INT | %MW2322[7] | BTY1502DX03 CRA Comms Module 0 Modules Status |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop03 |  | BTY1502DX03DIO1PLM1STS1 | BR4_Cluster1 | BPL131 | INT | %MW2329 | BTY1502DX03 DI Module 1 Status |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop03 |  | BTY1502DX03DIO1PLM3STS1 | BR4_Cluster1 | BPL131 | INT | %MW2330[9] | BTY1502DX03 AHI Module 3 Module Status |  |  | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop03 |  | BTY1502DX03DIO1PLM4STS1 | BR4_Cluster1 | BPL131 | INT | %MW2476[9] | BTY1502DX03 AHI Module 4 Module Status |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.BTY1502.FieldIO.FT01 |  | BTY1502FT01_Tot | BR4_Cluster1 | BPL131 | INT | %MW2622[18] | West Turkeys Nest Flow Rate (m3/h) Flow Totals |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.BTY1502.FieldIO.FT03 |  | BTY1502FT03_Tot | BR4_Cluster1 | BPL131 | INT | %MW2658[18] | West Turkeys Nest Flow Rate (m3/h) Flow Totals |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.BC02.BACS | Str1I | BSR131BC02BACSDAT1_Str1I | BR4_Cluster1 | BPL131 | INT | %MW4005 | BSR131BC02 Battery Charger BACS String 1 Current | 0 | 1000 | BS1_Tags
BR4.SRV.PWR.BSR131.BC02.BACS | Str1AltI | BSR131BC02BACSDAT1_Str1AltI | BR4_Cluster1 | BPL131 | INT | %MW4006 | BSR131BC02 Battery Charger BACS String 1 AC Current | 0 | 1000 | BS1_Tags
BR4.SRV.PWR.BSR131.BC02.BACS | Str1SumV | BSR131BC02BACSDAT1_Str1SumV | BR4_Cluster1 | BPL131 | INT | %MW4007 | BSR131BC02 Battery Charger BACS String 1 Overall Voltage | 0 | 1000 | BS1_Tags
BR4.SRV.PWR.BSR131.BC02.BACS | Str1AvgV | BSR131BC02BACSDAT1_Str1AvgV | BR4_Cluster1 | BPL131 | INT | %MW4008 | BSR131BC02 Battery Charger BACS String 1 Average Voltage | 0 | 1000 | BS1_Tags
BR4.SRV.PWR.BSR131.BC02.BACS | Mod1Tmp | BSR131BC02BACSDAT1_Mod1Tmp | BR4_Cluster1 | BPL131 | INT | %MW4009 | BSR131BC02 Battery Charger BACS Module 1 Temperature | 0 | 100 | BS1_Tags
BR4.SRV.PWR.BSR131.BC02.BACS | Mod1V | BSR131BC02BACSDAT1_Mod1V | BR4_Cluster1 | BPL131 | INT | %MW4010 | BSR131BC02 Battery Charger BACS Module 1 Voltage | 0 | 1000 | BS1_Tags
BR4.SRV.PWR.BSR131.BC02.BACS | Mod1Imp | BSR131BC02BACSDAT1_Mod1Imp | BR4_Cluster1 | BPL131 | INT | %MW4011 | BSR131BC02 Battery Charger BACS Module 1 Impedance | 0 | 1000 | BS1_Tags
BR4.SRV.PWR.BSR131.BC02.BACS | Mod1EqPerc | BSR131BC02BACSDAT1_Mod1EqPerc | BR4_Cluster1 | BPL131 | INT | %MW4013 | BSR131BC02 Battery Charger BACS Module 1 Equalizing / Balancing | 0 | 100 | BS1_Tags
BR4.SRV.PWR.BSR131.BC02.BACS | Mod2Tmp | BSR131BC02BACSDAT1_Mod2Tmp | BR4_Cluster1 | BPL131 | INT | %MW4014 | BSR131BC02 Battery Charger BACS Module 2 Temperature | 0 | 100 | BS1_Tags
BR4.SRV.PWR.BSR131.BC02.BACS | Mod2V | BSR131BC02BACSDAT1_Mod2V | BR4_Cluster1 | BPL131 | INT | %MW4015 | BSR131BC02 Battery Charger BACS Module 2 Voltage | 0 | 1000 | BS1_Tags
BR4.SRV.PWR.BSR131.BC02.BACS | Mod2Imp | BSR131BC02BACSDAT1_Mod2Imp | BR4_Cluster1 | BPL131 | INT | %MW4016 | BSR131BC02 Battery Charger BACS Module 2 Impedance | 0 | 1000 | BS1_Tags
BR4.SRV.PWR.BSR131.BC02.BACS | Mod2EqPerc | BSR131BC02BACSDAT1_Mod2EqPerc | BR4_Cluster1 | BPL131 | INT | %MW4018 | BSR131BC02 Battery Charger BACS Module 2 Equalizing / Balancing | 0 | 100 | BS1_Tags
BR4.SRV.PWR.BSR131.BC02.BACS | Mod3Tmp | BSR131BC02BACSDAT1_Mod3Tmp | BR4_Cluster1 | BPL131 | INT | %MW4019 | BSR131BC02 Battery Charger BACS Module 3 Temperature | 0 | 100 | BS1_Tags
BR4.SRV.PWR.BSR131.BC02.BACS | Mod3V | BSR131BC02BACSDAT1_Mod3V | BR4_Cluster1 | BPL131 | INT | %MW4020 | BSR131BC02 Battery Charger BACS Module 3 Voltage | 0 | 1000 | BS1_Tags
BR4.SRV.PWR.BSR131.BC02.BACS | Mod3Imp | BSR131BC02BACSDAT1_Mod3Imp | BR4_Cluster1 | BPL131 | INT | %MW4021 | BSR131BC02 Battery Charger BACS Module 3 Impedance | 0 | 1000 | BS1_Tags
BR4.SRV.PWR.BSR131.BC02.BACS | Mod3EqPerc | BSR131BC02BACSDAT1_Mod3EqPerc | BR4_Cluster1 | BPL131 | INT | %MW4023 | BSR131BC02 Battery Charger BACS Module 3 Equalizing / Balancing | 0 | 100 | BS1_Tags
BR4.SRV.PWR.BSR131.BC02.BACS | Mod4Tmp | BSR131BC02BACSDAT1_Mod4Tmp | BR4_Cluster1 | BPL131 | INT | %MW4024 | BSR131BC02 Battery Charger BACS Module 4 Temperature | 0 | 100 | BS1_Tags
BR4.SRV.PWR.BSR131.BC02.BACS | Mod4V | BSR131BC02BACSDAT1_Mod4V | BR4_Cluster1 | BPL131 | INT | %MW4025 | BSR131BC02 Battery Charger BACS Module 4 Voltage | 0 | 1000 | BS1_Tags
BR4.SRV.PWR.BSR131.BC02.BACS | Mod4Imp | BSR131BC02BACSDAT1_Mod4Imp | BR4_Cluster1 | BPL131 | INT | %MW4026 | BSR131BC02 Battery Charger BACS Module 4 Impedance | 0 | 1000 | BS1_Tags
BR4.SRV.PWR.BSR131.BC02.BACS | Mod4EqPerc | BSR131BC02BACSDAT1_Mod4EqPerc | BR4_Cluster1 | BPL131 | INT | %MW4028 | BSR131BC02 Battery Charger BACS Module 4 Equalizing / Balancing | 0 | 100 | BS1_Tags
BR4.SRV.PWR.BSR131.BC02.BACS | Mod5Tmp | BSR131BC02BACSDAT1_Mod5Tmp | BR4_Cluster1 | BPL131 | INT | %MW4029 | BSR131BC02 Battery Charger BACS Module 5 Temperature | 0 | 100 | BS1_Tags
BR4.SRV.PWR.BSR131.BC02.BACS | Mod5V | BSR131BC02BACSDAT1_Mod5V | BR4_Cluster1 | BPL131 | INT | %MW4030 | BSR131BC02 Battery Charger BACS Module 5 Voltage | 0 | 1000 | BS1_Tags
BR4.SRV.PWR.BSR131.BC02.BACS | Mod5Imp | BSR131BC02BACSDAT1_Mod5Imp | BR4_Cluster1 | BPL131 | INT | %MW4031 | BSR131BC02 Battery Charger BACS Module 5 Impedance | 0 | 1000 | BS1_Tags
BR4.SRV.PWR.BSR131.BC02.BACS | Mod5EqPerc | BSR131BC02BACSDAT1_Mod5EqPerc | BR4_Cluster1 | BPL131 | INT | %MW4033 | BSR131BC02 Battery Charger BACS Module 5 Equalizing / Balancing | 0 | 100 | BS1_Tags
BR4.SRV.PWR.BSR131.BC02.BACS | Mod6Tmp | BSR131BC02BACSDAT1_Mod6Tmp | BR4_Cluster1 | BPL131 | INT | %MW4034 | BSR131BC02 Battery Charger BACS Module 6 Temperature | 0 | 100 | BS1_Tags
BR4.SRV.PWR.BSR131.BC02.BACS | Mod6V | BSR131BC02BACSDAT1_Mod6V | BR4_Cluster1 | BPL131 | INT | %MW4035 | BSR131BC02 Battery Charger BACS Module 6 Voltage | 0 | 1000 | BS1_Tags
BR4.SRV.PWR.BSR131.BC02.BACS | Mod6Imp | BSR131BC02BACSDAT1_Mod6Imp | BR4_Cluster1 | BPL131 | INT | %MW4036 | BSR131BC02 Battery Charger BACS Module 6 Impedance | 0 | 1000 | BS1_Tags
BR4.SRV.PWR.BSR131.BC02.BACS | Mod6EqPerc | BSR131BC02BACSDAT1_Mod6EqPerc | BR4_Cluster1 | BPL131 | INT | %MW4038 | BSR131BC02 Battery Charger BACS Module 6 Equalizing / Balancing | 0 | 100 | BS1_Tags
BR4.SRV.PWR.BSR131.BC02.BACS | Mod7Tmp | BSR131BC02BACSDAT1_Mod7Tmp | BR4_Cluster1 | BPL131 | INT | %MW4039 | BSR131BC02 Battery Charger BACS Module 7 Temperature | 0 | 100 | BS1_Tags
BR4.SRV.PWR.BSR131.BC02.BACS | Mod7V | BSR131BC02BACSDAT1_Mod7V | BR4_Cluster1 | BPL131 | INT | %MW4040 | BSR131BC02 Battery Charger BACS Module 7 Voltage | 0 | 1000 | BS1_Tags
BR4.SRV.PWR.BSR131.BC02.BACS | Mod7Imp | BSR131BC02BACSDAT1_Mod7Imp | BR4_Cluster1 | BPL131 | INT | %MW4041 | BSR131BC02 Battery Charger BACS Module 7 Impedance | 0 | 1000 | BS1_Tags
BR4.SRV.PWR.BSR131.BC02.BACS | Mod7EqPerc | BSR131BC02BACSDAT1_Mod7EqPerc | BR4_Cluster1 | BPL131 | INT | %MW4043 | BSR131BC02 Battery Charger BACS Module 7 Equalizing / Balancing | 0 | 100 | BS1_Tags
BR4.SRV.PWR.BSR131.BC02.BACS | Mod8Tmp | BSR131BC02BACSDAT1_Mod8Tmp | BR4_Cluster1 | BPL131 | INT | %MW4044 | BSR131BC02 Battery Charger BACS Module 8 Temperature | 0 | 100 | BS1_Tags
BR4.SRV.PWR.BSR131.BC02.BACS | Mod8V | BSR131BC02BACSDAT1_Mod8V | BR4_Cluster1 | BPL131 | INT | %MW4045 | BSR131BC02 Battery Charger BACS Module 8 Voltage | 0 | 1000 | BS1_Tags
BR4.SRV.PWR.BSR131.BC02.BACS | Mod8Imp | BSR131BC02BACSDAT1_Mod8Imp | BR4_Cluster1 | BPL131 | INT | %MW4046 | BSR131BC02 Battery Charger BACS Module 8 Impedance | 0 | 1000 | BS1_Tags
BR4.SRV.PWR.BSR131.BC02.BACS | Mod8EqPerc | BSR131BC02BACSDAT1_Mod8EqPerc | BR4_Cluster1 | BPL131 | INT | %MW4048 | BSR131BC02 Battery Charger BACS Module 8 Equalizing / Balancing | 0 | 100 | BS1_Tags
BR4.SRV.PWR.BSR131.BC02.BACS | Mod9Tmp | BSR131BC02BACSDAT1_Mod9Tmp | BR4_Cluster1 | BPL131 | INT | %MW4049 | BSR131BC02 Battery Charger BACS Module 9 Temperature | 0 | 100 | BS1_Tags
BR4.SRV.PWR.BSR131.BC02.BACS | Mod9V | BSR131BC02BACSDAT1_Mod9V | BR4_Cluster1 | BPL131 | INT | %MW4050 | BSR131BC02 Battery Charger BACS Module 9 Voltage | 0 | 1000 | BS1_Tags
BR4.SRV.PWR.BSR131.BC02.BACS | Mod9Imp | BSR131BC02BACSDAT1_Mod9Imp | BR4_Cluster1 | BPL131 | INT | %MW4051 | BSR131BC02 Battery Charger BACS Module 9 Impedance | 0 | 1000 | BS1_Tags
BR4.SRV.PWR.BSR131.BC02.BACS | Mod9EqPerc | BSR131BC02BACSDAT1_Mod9EqPerc | BR4_Cluster1 | BPL131 | INT | %MW4053 | BSR131BC02 Battery Charger BACS Module 9 Equalizing / Balancing | 0 | 100 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.UPScale | AlmID1 | BSR131UP01DAT1_AlmID1 | BR4_Cluster1 | BPL131 | INT | %MW4201 | BSR131UP01 UPS Alarm ID 1 |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.UPScale | AlmID2 | BSR131UP01DAT1_AlmID2 | BR4_Cluster1 | BPL131 | INT | %MW4202 | BSR131UP01 UPS Alarm ID 2 |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.UPScale | InVPhs1 | BSR131UP01DAT1_InVPhs1 | BR4_Cluster1 | BPL131 | INT | %MW4207 | BSR131UP01 UPS Input Voltage Phase 1 (V) | 0 | 1000 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.UPScale | InVPhs2 | BSR131UP01DAT1_InVPhs2 | BR4_Cluster1 | BPL131 | INT | %MW4208 | BSR131UP01 UPS Input Voltage Phase 2 (V) | 0 | 1000 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.UPScale | InVPhs3 | BSR131UP01DAT1_InVPhs3 | BR4_Cluster1 | BPL131 | INT | %MW4209 | BSR131UP01 UPS Input Voltage Phase 3 (V) | 0 | 1000 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.UPScale | Tmp | BSR131UP01DAT1_Tmp | BR4_Cluster1 | BPL131 | INT | %MW4210 | BSR131UP01 UPS Temperature (C) | 0 | 100 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.UPScale | BatTmRemn | BSR131UP01DAT1_BatTmRemn | BR4_Cluster1 | BPL131 | INT | %MW4211 | BSR131UP01 UPS Battery Time Remaining (min) | 0 | 10000 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.UPScale | BatV | BSR131UP01DAT1_BatV | BR4_Cluster1 | BPL131 | INT | %MW4212 | BSR131UP01 UPS Battery Voltage (V) | 0 | 1000 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1I | BSR131UP01BACSDAT1_Str1I | BR4_Cluster1 | BPL131 | INT | %MW5005 | BSR131UP01 UPS BACS String 1 Current | 0 | 1000 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1AltI | BSR131UP01BACSDAT1_Str1AltI | BR4_Cluster1 | BPL131 | INT | %MW5006 | BSR131UP01 UPS BACS String 1 AC Current | 0 | 1000 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1SumV | BSR131UP01BACSDAT1_Str1SumV | BR4_Cluster1 | BPL131 | INT | %MW5007 | BSR131UP01 UPS BACS String 1 Overall Voltage | 0 | 1000 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1AvgV | BSR131UP01BACSDAT1_Str1AvgV | BR4_Cluster1 | BPL131 | INT | %MW5008 | BSR131UP01 UPS BACS String 1 Average Voltage | 0 | 1000 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod1Tmp | BSR131UP01BACSDAT1_Str1Mod1Tmp | BR4_Cluster1 | BPL131 | INT | %MW5009 | BSR131UP01 UPS BACS String 1 Module 1 Temperature | 0 | 100 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod1V | BSR131UP01BACSDAT1_Str1Mod1V | BR4_Cluster1 | BPL131 | INT | %MW5010 | BSR131UP01 UPS BACS String 1 Module 1 Voltage | 0 | 1000 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod1Imp | BSR131UP01BACSDAT1_Str1Mod1Imp | BR4_Cluster1 | BPL131 | INT | %MW5011 | BSR131UP01 UPS BACS String 1 Module 1 Impedance | 0 | 1000 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod1EqPerc | BSR131UP01BACSDAT1_Str1Mod1EqPerc | BR4_Cluster1 | BPL131 | INT | %MW5013 | BSR131UP01 UPS BACS String 1 Module 1 Equalizing / Balancing | 0 | 100 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod2Tmp | BSR131UP01BACSDAT1_Str1Mod2Tmp | BR4_Cluster1 | BPL131 | INT | %MW5014 | BSR131UP01 UPS BACS String 1 Module 2 Temperature | 0 | 100 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod2V | BSR131UP01BACSDAT1_Str1Mod2V | BR4_Cluster1 | BPL131 | INT | %MW5015 | BSR131UP01 UPS BACS String 1 Module 2 Voltage | 0 | 1000 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod2Imp | BSR131UP01BACSDAT1_Str1Mod2Imp | BR4_Cluster1 | BPL131 | INT | %MW5016 | BSR131UP01 UPS BACS String 1 Module 2 Impedance | 0 | 1000 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod2EqPerc | BSR131UP01BACSDAT1_Str1Mod2EqPerc | BR4_Cluster1 | BPL131 | INT | %MW5018 | BSR131UP01 UPS BACS String 1 Module 2 Equalizing / Balancing | 0 | 100 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod3Tmp | BSR131UP01BACSDAT1_Str1Mod3Tmp | BR4_Cluster1 | BPL131 | INT | %MW5019 | BSR131UP01 UPS BACS String 1 Module 3 Temperature | 0 | 100 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod3V | BSR131UP01BACSDAT1_Str1Mod3V | BR4_Cluster1 | BPL131 | INT | %MW5020 | BSR131UP01 UPS BACS String 1 Module 3 Voltage | 0 | 1000 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod3Imp | BSR131UP01BACSDAT1_Str1Mod3Imp | BR4_Cluster1 | BPL131 | INT | %MW5021 | BSR131UP01 UPS BACS String 1 Module 3 Impedance | 0 | 1000 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod3EqPerc | BSR131UP01BACSDAT1_Str1Mod3EqPerc | BR4_Cluster1 | BPL131 | INT | %MW5023 | BSR131UP01 UPS BACS String 1 Module 3 Equalizing / Balancing | 0 | 100 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod4Tmp | BSR131UP01BACSDAT1_Str1Mod4Tmp | BR4_Cluster1 | BPL131 | INT | %MW5024 | BSR131UP01 UPS BACS String 1 Module 4 Temperature | 0 | 100 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod4V | BSR131UP01BACSDAT1_Str1Mod4V | BR4_Cluster1 | BPL131 | INT | %MW5025 | BSR131UP01 UPS BACS String 1 Module 4 Voltage | 0 | 1000 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod4Imp | BSR131UP01BACSDAT1_Str1Mod4Imp | BR4_Cluster1 | BPL131 | INT | %MW5026 | BSR131UP01 UPS BACS String 1 Module 4 Impedance | 0 | 1000 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod4EqPerc | BSR131UP01BACSDAT1_Str1Mod4EqPerc | BR4_Cluster1 | BPL131 | INT | %MW5028 | BSR131UP01 UPS BACS String 1 Module 4 Equalizing / Balancing | 0 | 100 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod5Tmp | BSR131UP01BACSDAT1_Str1Mod5Tmp | BR4_Cluster1 | BPL131 | INT | %MW5029 | BSR131UP01 UPS BACS String 1 Module 5 Temperature | 0 | 100 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod5V | BSR131UP01BACSDAT1_Str1Mod5V | BR4_Cluster1 | BPL131 | INT | %MW5030 | BSR131UP01 UPS BACS String 1 Module 5 Voltage | 0 | 1000 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod5Imp | BSR131UP01BACSDAT1_Str1Mod5Imp | BR4_Cluster1 | BPL131 | INT | %MW5031 | BSR131UP01 UPS BACS String 1 Module 5 Impedance | 0 | 1000 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod5EqPerc | BSR131UP01BACSDAT1_Str1Mod5EqPerc | BR4_Cluster1 | BPL131 | INT | %MW5033 | BSR131UP01 UPS BACS String 1 Module 5 Equalizing / Balancing | 0 | 100 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod6Tmp | BSR131UP01BACSDAT1_Str1Mod6Tmp | BR4_Cluster1 | BPL131 | INT | %MW5034 | BSR131UP01 UPS BACS String 1 Module 6 Temperature | 0 | 100 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod6V | BSR131UP01BACSDAT1_Str1Mod6V | BR4_Cluster1 | BPL131 | INT | %MW5035 | BSR131UP01 UPS BACS String 1 Module 6 Voltage | 0 | 1000 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod6Imp | BSR131UP01BACSDAT1_Str1Mod6Imp | BR4_Cluster1 | BPL131 | INT | %MW5036 | BSR131UP01 UPS BACS String 1 Module 6 Impedance | 0 | 1000 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod6EqPerc | BSR131UP01BACSDAT1_Str1Mod6EqPerc | BR4_Cluster1 | BPL131 | INT | %MW5038 | BSR131UP01 UPS BACS String 1 Module 6 Equalizing / Balancing | 0 | 100 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod7Tmp | BSR131UP01BACSDAT1_Str1Mod7Tmp | BR4_Cluster1 | BPL131 | INT | %MW5039 | BSR131UP01 UPS BACS String 1 Module 7 Temperature | 0 | 100 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod7V | BSR131UP01BACSDAT1_Str1Mod7V | BR4_Cluster1 | BPL131 | INT | %MW5040 | BSR131UP01 UPS BACS String 1 Module 7 Voltage | 0 | 1000 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod7Imp | BSR131UP01BACSDAT1_Str1Mod7Imp | BR4_Cluster1 | BPL131 | INT | %MW5041 | BSR131UP01 UPS BACS String 1 Module 7 Impedance | 0 | 1000 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod7EqPerc | BSR131UP01BACSDAT1_Str1Mod7EqPerc | BR4_Cluster1 | BPL131 | INT | %MW5043 | BSR131UP01 UPS BACS String 1 Module 7 Equalizing / Balancing | 0 | 100 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod8Tmp | BSR131UP01BACSDAT1_Str1Mod8Tmp | BR4_Cluster1 | BPL131 | INT | %MW5044 | BSR131UP01 UPS BACS String 1 Module 8 Temperature | 0 | 100 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod8V | BSR131UP01BACSDAT1_Str1Mod8V | BR4_Cluster1 | BPL131 | INT | %MW5045 | BSR131UP01 UPS BACS String 1 Module 8 Voltage | 0 | 1000 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod8Imp | BSR131UP01BACSDAT1_Str1Mod8Imp | BR4_Cluster1 | BPL131 | INT | %MW5046 | BSR131UP01 UPS BACS String 1 Module 8 Impedance | 0 | 1000 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod8EqPerc | BSR131UP01BACSDAT1_Str1Mod8EqPerc | BR4_Cluster1 | BPL131 | INT | %MW5048 | BSR131UP01 UPS BACS String 1 Module 8 Equalizing / Balancing | 0 | 100 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod9Tmp | BSR131UP01BACSDAT1_Str1Mod9Tmp | BR4_Cluster1 | BPL131 | INT | %MW5049 | BSR131UP01 UPS BACS String 1 Module 9 Temperature | 0 | 100 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod9V | BSR131UP01BACSDAT1_Str1Mod9V | BR4_Cluster1 | BPL131 | INT | %MW5050 | BSR131UP01 UPS BACS String 1 Module 9 Voltage | 0 | 1000 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod9Imp | BSR131UP01BACSDAT1_Str1Mod9Imp | BR4_Cluster1 | BPL131 | INT | %MW5051 | BSR131UP01 UPS BACS String 1 Module 9 Impedance | 0 | 1000 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod9EqPerc | BSR131UP01BACSDAT1_Str1Mod9EqPerc | BR4_Cluster1 | BPL131 | INT | %MW5053 | BSR131UP01 UPS BACS String 1 Module 9 Equalizing / Balancing | 0 | 100 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod10Tmp | BSR131UP01BACSDAT1_Str1Mod10Tmp | BR4_Cluster1 | BPL131 | INT | %MW5054 | BSR131UP01 UPS BACS String 1 Module 10 Temperature | 0 | 100 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod10V | BSR131UP01BACSDAT1_Str1Mod10V | BR4_Cluster1 | BPL131 | INT | %MW5055 | BSR131UP01 UPS BACS String 1 Module 10 Voltage | 0 | 1000 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod10Imp | BSR131UP01BACSDAT1_Str1Mod10Imp | BR4_Cluster1 | BPL131 | INT | %MW5056 | BSR131UP01 UPS BACS String 1 Module 10 Impedance | 0 | 1000 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod10EqPerc | BSR131UP01BACSDAT1_Str1Mod10EqPerc | BR4_Cluster1 | BPL131 | INT | %MW5058 | BSR131UP01 UPS BACS String 1 Module 10 Equalizing / Balancing | 0 | 100 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod11Tmp | BSR131UP01BACSDAT1_Str1Mod11Tmp | BR4_Cluster1 | BPL131 | INT | %MW5059 | BSR131UP01 UPS BACS String 1 Module 11 Temperature | 0 | 100 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod11V | BSR131UP01BACSDAT1_Str1Mod11V | BR4_Cluster1 | BPL131 | INT | %MW5060 | BSR131UP01 UPS BACS String 1 Module 11 Voltage | 0 | 1000 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod11Imp | BSR131UP01BACSDAT1_Str1Mod11Imp | BR4_Cluster1 | BPL131 | INT | %MW5061 | BSR131UP01 UPS BACS String 1 Module 11 Impedance | 0 | 1000 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod11EqPerc | BSR131UP01BACSDAT1_Str1Mod11EqPerc | BR4_Cluster1 | BPL131 | INT | %MW5063 | BSR131UP01 UPS BACS String 1 Module 11 Equalizing / Balancing | 0 | 100 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod12Tmp | BSR131UP01BACSDAT1_Str1Mod12Tmp | BR4_Cluster1 | BPL131 | INT | %MW5064 | BSR131UP01 UPS BACS String 1 Module 12 Temperature | 0 | 100 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod12V | BSR131UP01BACSDAT1_Str1Mod12V | BR4_Cluster1 | BPL131 | INT | %MW5065 | BSR131UP01 UPS BACS String 1 Module 12 Voltage | 0 | 1000 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod12Imp | BSR131UP01BACSDAT1_Str1Mod12Imp | BR4_Cluster1 | BPL131 | INT | %MW5066 | BSR131UP01 UPS BACS String 1 Module 12 Impedance | 0 | 1000 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod12EqPerc | BSR131UP01BACSDAT1_Str1Mod12EqPerc | BR4_Cluster1 | BPL131 | INT | %MW5068 | BSR131UP01 UPS BACS String 1 Module 12 Equalizing / Balancing | 0 | 100 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod13Tmp | BSR131UP01BACSDAT1_Str1Mod13Tmp | BR4_Cluster1 | BPL131 | INT | %MW5069 | BSR131UP01 UPS BACS String 1 Module 13 Temperature | 0 | 100 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod13V | BSR131UP01BACSDAT1_Str1Mod13V | BR4_Cluster1 | BPL131 | INT | %MW5070 | BSR131UP01 UPS BACS String 1 Module 13 Voltage | 0 | 1000 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod13Imp | BSR131UP01BACSDAT1_Str1Mod13Imp | BR4_Cluster1 | BPL131 | INT | %MW5071 | BSR131UP01 UPS BACS String 1 Module 13 Impedance | 0 | 1000 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod13EqPerc | BSR131UP01BACSDAT1_Str1Mod13EqPerc | BR4_Cluster1 | BPL131 | INT | %MW5073 | BSR131UP01 UPS BACS String 1 Module 13 Equalizing / Balancing | 0 | 100 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod14Tmp | BSR131UP01BACSDAT1_Str1Mod14Tmp | BR4_Cluster1 | BPL131 | INT | %MW5074 | BSR131UP01 UPS BACS String 1 Module 14 Temperature | 0 | 100 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod14V | BSR131UP01BACSDAT1_Str1Mod14V | BR4_Cluster1 | BPL131 | INT | %MW5075 | BSR131UP01 UPS BACS String 1 Module 14 Voltage | 0 | 1000 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod14Imp | BSR131UP01BACSDAT1_Str1Mod14Imp | BR4_Cluster1 | BPL131 | INT | %MW5076 | BSR131UP01 UPS BACS String 1 Module 14 Impedance | 0 | 1000 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod14EqPerc | BSR131UP01BACSDAT1_Str1Mod14EqPerc | BR4_Cluster1 | BPL131 | INT | %MW5078 | BSR131UP01 UPS BACS String 1 Module 14 Equalizing / Balancing | 0 | 100 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod15Tmp | BSR131UP01BACSDAT1_Str1Mod15Tmp | BR4_Cluster1 | BPL131 | INT | %MW5079 | BSR131UP01 UPS BACS String 1 Module 15 Temperature | 0 | 100 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod15V | BSR131UP01BACSDAT1_Str1Mod15V | BR4_Cluster1 | BPL131 | INT | %MW5080 | BSR131UP01 UPS BACS String 1 Module 15 Voltage | 0 | 1000 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod15Imp | BSR131UP01BACSDAT1_Str1Mod15Imp | BR4_Cluster1 | BPL131 | INT | %MW5081 | BSR131UP01 UPS BACS String 1 Module 15 Impedance | 0 | 1000 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod15EqPerc | BSR131UP01BACSDAT1_Str1Mod15EqPerc | BR4_Cluster1 | BPL131 | INT | %MW5083 | BSR131UP01 UPS BACS String 1 Module 15 Equalizing / Balancing | 0 | 100 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod16Tmp | BSR131UP01BACSDAT1_Str1Mod16Tmp | BR4_Cluster1 | BPL131 | INT | %MW5084 | BSR131UP01 UPS BACS String 1 Module 16 Temperature | 0 | 100 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod16V | BSR131UP01BACSDAT1_Str1Mod16V | BR4_Cluster1 | BPL131 | INT | %MW5085 | BSR131UP01 UPS BACS String 1 Module 16 Voltage | 0 | 1000 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod16Imp | BSR131UP01BACSDAT1_Str1Mod16Imp | BR4_Cluster1 | BPL131 | INT | %MW5086 | BSR131UP01 UPS BACS String 1 Module 16 Impedance | 0 | 1000 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod16EqPerc | BSR131UP01BACSDAT1_Str1Mod16EqPerc | BR4_Cluster1 | BPL131 | INT | %MW5088 | BSR131UP01 UPS BACS String 1 Module 16 Equalizing / Balancing | 0 | 100 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod17Tmp | BSR131UP01BACSDAT1_Str1Mod17Tmp | BR4_Cluster1 | BPL131 | INT | %MW5089 | BSR131UP01 UPS BACS String 1 Module 17 Temperature | 0 | 100 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod17V | BSR131UP01BACSDAT1_Str1Mod17V | BR4_Cluster1 | BPL131 | INT | %MW5090 | BSR131UP01 UPS BACS String 1 Module 17 Voltage | 0 | 1000 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod17Imp | BSR131UP01BACSDAT1_Str1Mod17Imp | BR4_Cluster1 | BPL131 | INT | %MW5091 | BSR131UP01 UPS BACS String 1 Module 17 Impedance | 0 | 1000 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod17EqPerc | BSR131UP01BACSDAT1_Str1Mod17EqPerc | BR4_Cluster1 | BPL131 | INT | %MW5093 | BSR131UP01 UPS BACS String 1 Module 17 Equalizing / Balancing | 0 | 100 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod18Tmp | BSR131UP01BACSDAT1_Str1Mod18Tmp | BR4_Cluster1 | BPL131 | INT | %MW5094 | BSR131UP01 UPS BACS String 1 Module 18 Temperature | 0 | 100 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod18V | BSR131UP01BACSDAT1_Str1Mod18V | BR4_Cluster1 | BPL131 | INT | %MW5095 | BSR131UP01 UPS BACS String 1 Module 18 Voltage | 0 | 1000 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod18Imp | BSR131UP01BACSDAT1_Str1Mod18Imp | BR4_Cluster1 | BPL131 | INT | %MW5096 | BSR131UP01 UPS BACS String 1 Module 18 Impedance | 0 | 1000 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod18EqPerc | BSR131UP01BACSDAT1_Str1Mod18EqPerc | BR4_Cluster1 | BPL131 | INT | %MW5098 | BSR131UP01 UPS BACS String 1 Module 18 Equalizing / Balancing | 0 | 100 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod19Tmp | BSR131UP01BACSDAT1_Str1Mod19Tmp | BR4_Cluster1 | BPL131 | INT | %MW5099 | BSR131UP01 UPS BACS String 1 Module 19 Temperature | 0 | 100 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod19V | BSR131UP01BACSDAT1_Str1Mod19V | BR4_Cluster1 | BPL131 | INT | %MW5100 | BSR131UP01 UPS BACS String 1 Module 19 Voltage | 0 | 1000 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod19Imp | BSR131UP01BACSDAT1_Str1Mod19Imp | BR4_Cluster1 | BPL131 | INT | %MW5101 | BSR131UP01 UPS BACS String 1 Module 19 Impedance | 0 | 1000 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod19EqPerc | BSR131UP01BACSDAT1_Str1Mod19EqPerc | BR4_Cluster1 | BPL131 | INT | %MW5103 | BSR131UP01 UPS BACS String 1 Module 19 Equalizing / Balancing | 0 | 100 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod20Tmp | BSR131UP01BACSDAT1_Str1Mod20Tmp | BR4_Cluster1 | BPL131 | INT | %MW5104 | BSR131UP01 UPS BACS String 1 Module 20 Temperature | 0 | 100 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod20V | BSR131UP01BACSDAT1_Str1Mod20V | BR4_Cluster1 | BPL131 | INT | %MW5105 | BSR131UP01 UPS BACS String 1 Module 20 Voltage | 0 | 1000 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod20Imp | BSR131UP01BACSDAT1_Str1Mod20Imp | BR4_Cluster1 | BPL131 | INT | %MW5106 | BSR131UP01 UPS BACS String 1 Module 20 Impedance | 0 | 1000 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod20EqPerc | BSR131UP01BACSDAT1_Str1Mod20EqPerc | BR4_Cluster1 | BPL131 | INT | %MW5108 | BSR131UP01 UPS BACS String 1 Module 20 Equalizing / Balancing | 0 | 100 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod21Tmp | BSR131UP01BACSDAT1_Str1Mod21Tmp | BR4_Cluster1 | BPL131 | INT | %MW5109 | BSR131UP01 UPS BACS String 1 Module 21 Temperature | 0 | 100 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod21V | BSR131UP01BACSDAT1_Str1Mod21V | BR4_Cluster1 | BPL131 | INT | %MW5110 | BSR131UP01 UPS BACS String 1 Module 21 Voltage | 0 | 1000 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod21Imp | BSR131UP01BACSDAT1_Str1Mod21Imp | BR4_Cluster1 | BPL131 | INT | %MW5111 | BSR131UP01 UPS BACS String 1 Module 21 Impedance | 0 | 1000 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod21EqPerc | BSR131UP01BACSDAT1_Str1Mod21EqPerc | BR4_Cluster1 | BPL131 | INT | %MW5113 | BSR131UP01 UPS BACS String 1 Module 21 Equalizing / Balancing | 0 | 100 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod22V | BSR131UP01BACSDAT1_Str2Mod22V | BR4_Cluster1 | BPL131 | INT | %MW5113 | BSR131UP01 UPS BACS String 2 Module 22 Voltage | 0 | 1000 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod22Tmp | BSR131UP01BACSDAT1_Str1Mod22Tmp | BR4_Cluster1 | BPL131 | INT | %MW5114 | BSR131UP01 UPS BACS String 1 Module 22 Temperature | 0 | 100 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod22Imp | BSR131UP01BACSDAT1_Str2Mod22Imp | BR4_Cluster1 | BPL131 | INT | %MW5114 | BSR131UP01 UPS BACS String 2 Module 22 Impedance | 0 | 1000 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod22V | BSR131UP01BACSDAT1_Str1Mod22V | BR4_Cluster1 | BPL131 | INT | %MW5115 | BSR131UP01 UPS BACS String 1 Module 22 Voltage | 0 | 1000 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod22Imp | BSR131UP01BACSDAT1_Str1Mod22Imp | BR4_Cluster1 | BPL131 | INT | %MW5116 | BSR131UP01 UPS BACS String 1 Module 22 Impedance | 0 | 1000 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod22EqPerc | BSR131UP01BACSDAT1_Str2Mod22EqPerc | BR4_Cluster1 | BPL131 | INT | %MW5116 | BSR131UP01 UPS BACS String 2 Module 22 Equalizing / Balancing | 0 | 100 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod23Tmp | BSR131UP01BACSDAT1_Str2Mod23Tmp | BR4_Cluster1 | BPL131 | INT | %MW5117 | BSR131UP01 UPS BACS String 2 Module 23 Temperature | 0 | 100 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod22EqPerc | BSR131UP01BACSDAT1_Str1Mod22EqPerc | BR4_Cluster1 | BPL131 | INT | %MW5118 | BSR131UP01 UPS BACS String 1 Module 22 Equalizing / Balancing | 0 | 100 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod23V | BSR131UP01BACSDAT1_Str2Mod23V | BR4_Cluster1 | BPL131 | INT | %MW5118 | BSR131UP01 UPS BACS String 2 Module 23 Voltage | 0 | 1000 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod23Tmp | BSR131UP01BACSDAT1_Str1Mod23Tmp | BR4_Cluster1 | BPL131 | INT | %MW5119 | BSR131UP01 UPS BACS String 1 Module 23 Temperature | 0 | 100 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod23Imp | BSR131UP01BACSDAT1_Str2Mod23Imp | BR4_Cluster1 | BPL131 | INT | %MW5119 | BSR131UP01 UPS BACS String 2 Module 23 Impedance | 0 | 1000 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod23V | BSR131UP01BACSDAT1_Str1Mod23V | BR4_Cluster1 | BPL131 | INT | %MW5120 | BSR131UP01 UPS BACS String 1 Module 23 Voltage | 0 | 1000 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod23Imp | BSR131UP01BACSDAT1_Str1Mod23Imp | BR4_Cluster1 | BPL131 | INT | %MW5121 | BSR131UP01 UPS BACS String 1 Module 23 Impedance | 0 | 1000 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod23EqPerc | BSR131UP01BACSDAT1_Str2Mod23EqPerc | BR4_Cluster1 | BPL131 | INT | %MW5121 | BSR131UP01 UPS BACS String 2 Module 23 Equalizing / Balancing | 0 | 100 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod24Tmp | BSR131UP01BACSDAT1_Str2Mod24Tmp | BR4_Cluster1 | BPL131 | INT | %MW5122 | BSR131UP01 UPS BACS String 2 Module 24 Temperature | 0 | 100 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod23EqPerc | BSR131UP01BACSDAT1_Str1Mod23EqPerc | BR4_Cluster1 | BPL131 | INT | %MW5123 | BSR131UP01 UPS BACS String 1 Module 23 Equalizing / Balancing | 0 | 100 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod24V | BSR131UP01BACSDAT1_Str2Mod24V | BR4_Cluster1 | BPL131 | INT | %MW5123 | BSR131UP01 UPS BACS String 2 Module 24 Voltage | 0 | 1000 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod24Tmp | BSR131UP01BACSDAT1_Str1Mod24Tmp | BR4_Cluster1 | BPL131 | INT | %MW5124 | BSR131UP01 UPS BACS String 1 Module 24 Temperature | 0 | 100 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod24Imp | BSR131UP01BACSDAT1_Str2Mod24Imp | BR4_Cluster1 | BPL131 | INT | %MW5124 | BSR131UP01 UPS BACS String 2 Module 24 Impedance | 0 | 1000 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod24V | BSR131UP01BACSDAT1_Str1Mod24V | BR4_Cluster1 | BPL131 | INT | %MW5125 | BSR131UP01 UPS BACS String 1 Module 24 Voltage | 0 | 1000 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod24Imp | BSR131UP01BACSDAT1_Str1Mod24Imp | BR4_Cluster1 | BPL131 | INT | %MW5126 | BSR131UP01 UPS BACS String 1 Module 24 Impedance | 0 | 1000 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod24EqPerc | BSR131UP01BACSDAT1_Str2Mod24EqPerc | BR4_Cluster1 | BPL131 | INT | %MW5126 | BSR131UP01 UPS BACS String 2 Module 24 Equalizing / Balancing | 0 | 100 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod25Tmp | BSR131UP01BACSDAT1_Str2Mod25Tmp | BR4_Cluster1 | BPL131 | INT | %MW5127 | BSR131UP01 UPS BACS String 2 Module 25 Temperature | 0 | 100 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod24EqPerc | BSR131UP01BACSDAT1_Str1Mod24EqPerc | BR4_Cluster1 | BPL131 | INT | %MW5128 | BSR131UP01 UPS BACS String 1 Module 24 Equalizing / Balancing | 0 | 100 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod25V | BSR131UP01BACSDAT1_Str2Mod25V | BR4_Cluster1 | BPL131 | INT | %MW5128 | BSR131UP01 UPS BACS String 2 Module 25 Voltage | 0 | 1000 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod25Tmp | BSR131UP01BACSDAT1_Str1Mod25Tmp | BR4_Cluster1 | BPL131 | INT | %MW5129 | BSR131UP01 UPS BACS String 1 Module 25 Temperature | 0 | 100 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod25Imp | BSR131UP01BACSDAT1_Str2Mod25Imp | BR4_Cluster1 | BPL131 | INT | %MW5129 | BSR131UP01 UPS BACS String 2 Module 25 Impedance | 0 | 1000 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod25V | BSR131UP01BACSDAT1_Str1Mod25V | BR4_Cluster1 | BPL131 | INT | %MW5130 | BSR131UP01 UPS BACS String 1 Module 25 Voltage | 0 | 1000 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod25Imp | BSR131UP01BACSDAT1_Str1Mod25Imp | BR4_Cluster1 | BPL131 | INT | %MW5131 | BSR131UP01 UPS BACS String 1 Module 25 Impedance | 0 | 1000 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod25EqPerc | BSR131UP01BACSDAT1_Str2Mod25EqPerc | BR4_Cluster1 | BPL131 | INT | %MW5131 | BSR131UP01 UPS BACS String 2 Module 25 Equalizing / Balancing | 0 | 100 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod26Tmp | BSR131UP01BACSDAT1_Str2Mod26Tmp | BR4_Cluster1 | BPL131 | INT | %MW5132 | BSR131UP01 UPS BACS String 2 Module 26 Temperature | 0 | 100 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod25EqPerc | BSR131UP01BACSDAT1_Str1Mod25EqPerc | BR4_Cluster1 | BPL131 | INT | %MW5133 | BSR131UP01 UPS BACS String 1 Module 25 Equalizing / Balancing | 0 | 100 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod26V | BSR131UP01BACSDAT1_Str2Mod26V | BR4_Cluster1 | BPL131 | INT | %MW5133 | BSR131UP01 UPS BACS String 2 Module 26 Voltage | 0 | 1000 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod26Tmp | BSR131UP01BACSDAT1_Str1Mod26Tmp | BR4_Cluster1 | BPL131 | INT | %MW5134 | BSR131UP01 UPS BACS String 1 Module 26 Temperature | 0 | 100 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod26Imp | BSR131UP01BACSDAT1_Str2Mod26Imp | BR4_Cluster1 | BPL131 | INT | %MW5134 | BSR131UP01 UPS BACS String 2 Module 26 Impedance | 0 | 1000 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod26V | BSR131UP01BACSDAT1_Str1Mod26V | BR4_Cluster1 | BPL131 | INT | %MW5135 | BSR131UP01 UPS BACS String 1 Module 26 Voltage | 0 | 1000 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod26Imp | BSR131UP01BACSDAT1_Str1Mod26Imp | BR4_Cluster1 | BPL131 | INT | %MW5136 | BSR131UP01 UPS BACS String 1 Module 26 Impedance | 0 | 1000 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod26EqPerc | BSR131UP01BACSDAT1_Str2Mod26EqPerc | BR4_Cluster1 | BPL131 | INT | %MW5136 | BSR131UP01 UPS BACS String 2 Module 26 Equalizing / Balancing | 0 | 100 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod27Tmp | BSR131UP01BACSDAT1_Str2Mod27Tmp | BR4_Cluster1 | BPL131 | INT | %MW5137 | BSR131UP01 UPS BACS String 2 Module 27 Temperature | 0 | 100 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod26EqPerc | BSR131UP01BACSDAT1_Str1Mod26EqPerc | BR4_Cluster1 | BPL131 | INT | %MW5138 | BSR131UP01 UPS BACS String 1 Module 26 Equalizing / Balancing | 0 | 100 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod27V | BSR131UP01BACSDAT1_Str2Mod27V | BR4_Cluster1 | BPL131 | INT | %MW5138 | BSR131UP01 UPS BACS String 2 Module 27 Voltage | 0 | 1000 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod27Tmp | BSR131UP01BACSDAT1_Str1Mod27Tmp | BR4_Cluster1 | BPL131 | INT | %MW5139 | BSR131UP01 UPS BACS String 1 Module 27 Temperature | 0 | 100 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod27Imp | BSR131UP01BACSDAT1_Str2Mod27Imp | BR4_Cluster1 | BPL131 | INT | %MW5139 | BSR131UP01 UPS BACS String 2 Module 27 Impedance | 0 | 1000 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod27V | BSR131UP01BACSDAT1_Str1Mod27V | BR4_Cluster1 | BPL131 | INT | %MW5140 | BSR131UP01 UPS BACS String 1 Module 27 Voltage | 0 | 1000 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod27Imp | BSR131UP01BACSDAT1_Str1Mod27Imp | BR4_Cluster1 | BPL131 | INT | %MW5141 | BSR131UP01 UPS BACS String 1 Module 27 Impedance | 0 | 1000 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod27EqPerc | BSR131UP01BACSDAT1_Str2Mod27EqPerc | BR4_Cluster1 | BPL131 | INT | %MW5141 | BSR131UP01 UPS BACS String 2 Module 27 Equalizing / Balancing | 0 | 100 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod28Tmp | BSR131UP01BACSDAT1_Str2Mod28Tmp | BR4_Cluster1 | BPL131 | INT | %MW5142 | BSR131UP01 UPS BACS String 2 Module 28 Temperature | 0 | 100 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod27EqPerc | BSR131UP01BACSDAT1_Str1Mod27EqPerc | BR4_Cluster1 | BPL131 | INT | %MW5143 | BSR131UP01 UPS BACS String 1 Module 27 Equalizing / Balancing | 0 | 100 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod28V | BSR131UP01BACSDAT1_Str2Mod28V | BR4_Cluster1 | BPL131 | INT | %MW5143 | BSR131UP01 UPS BACS String 2 Module 28 Voltage | 0 | 1000 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod28Tmp | BSR131UP01BACSDAT1_Str1Mod28Tmp | BR4_Cluster1 | BPL131 | INT | %MW5144 | BSR131UP01 UPS BACS String 1 Module 28 Temperature | 0 | 100 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod28Imp | BSR131UP01BACSDAT1_Str2Mod28Imp | BR4_Cluster1 | BPL131 | INT | %MW5144 | BSR131UP01 UPS BACS String 2 Module 28 Impedance | 0 | 1000 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod28V | BSR131UP01BACSDAT1_Str1Mod28V | BR4_Cluster1 | BPL131 | INT | %MW5145 | BSR131UP01 UPS BACS String 1 Module 28 Voltage | 0 | 1000 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod28Imp | BSR131UP01BACSDAT1_Str1Mod28Imp | BR4_Cluster1 | BPL131 | INT | %MW5146 | BSR131UP01 UPS BACS String 1 Module 28 Impedance | 0 | 1000 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod28EqPerc | BSR131UP01BACSDAT1_Str2Mod28EqPerc | BR4_Cluster1 | BPL131 | INT | %MW5146 | BSR131UP01 UPS BACS String 2 Module 28 Equalizing / Balancing | 0 | 100 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod29Tmp | BSR131UP01BACSDAT1_Str2Mod29Tmp | BR4_Cluster1 | BPL131 | INT | %MW5147 | BSR131UP01 UPS BACS String 2 Module 29 Temperature | 0 | 100 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod28EqPerc | BSR131UP01BACSDAT1_Str1Mod28EqPerc | BR4_Cluster1 | BPL131 | INT | %MW5148 | BSR131UP01 UPS BACS String 1 Module 28 Equalizing / Balancing | 0 | 100 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod29V | BSR131UP01BACSDAT1_Str2Mod29V | BR4_Cluster1 | BPL131 | INT | %MW5148 | BSR131UP01 UPS BACS String 2 Module 29 Voltage | 0 | 1000 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod29Tmp | BSR131UP01BACSDAT1_Str1Mod29Tmp | BR4_Cluster1 | BPL131 | INT | %MW5149 | BSR131UP01 UPS BACS String 1 Module 29 Temperature | 0 | 100 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod29Imp | BSR131UP01BACSDAT1_Str2Mod29Imp | BR4_Cluster1 | BPL131 | INT | %MW5149 | BSR131UP01 UPS BACS String 2 Module 29 Impedance | 0 | 1000 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod29V | BSR131UP01BACSDAT1_Str1Mod29V | BR4_Cluster1 | BPL131 | INT | %MW5150 | BSR131UP01 UPS BACS String 1 Module 29 Voltage | 0 | 1000 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod29Imp | BSR131UP01BACSDAT1_Str1Mod29Imp | BR4_Cluster1 | BPL131 | INT | %MW5151 | BSR131UP01 UPS BACS String 1 Module 29 Impedance | 0 | 1000 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod29EqPerc | BSR131UP01BACSDAT1_Str2Mod29EqPerc | BR4_Cluster1 | BPL131 | INT | %MW5151 | BSR131UP01 UPS BACS String 2 Module 29 Equalizing / Balancing | 0 | 100 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod30Tmp | BSR131UP01BACSDAT1_Str2Mod30Tmp | BR4_Cluster1 | BPL131 | INT | %MW5152 | BSR131UP01 UPS BACS String 2 Module 30 Temperature | 0 | 100 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod29EqPerc | BSR131UP01BACSDAT1_Str1Mod29EqPerc | BR4_Cluster1 | BPL131 | INT | %MW5153 | BSR131UP01 UPS BACS String 1 Module 29 Equalizing / Balancing | 0 | 100 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod30V | BSR131UP01BACSDAT1_Str2Mod30V | BR4_Cluster1 | BPL131 | INT | %MW5153 | BSR131UP01 UPS BACS String 2 Module 30 Voltage | 0 | 1000 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod30Tmp | BSR131UP01BACSDAT1_Str1Mod30Tmp | BR4_Cluster1 | BPL131 | INT | %MW5154 | BSR131UP01 UPS BACS String 1 Module 30 Temperature | 0 | 100 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod30Imp | BSR131UP01BACSDAT1_Str2Mod30Imp | BR4_Cluster1 | BPL131 | INT | %MW5154 | BSR131UP01 UPS BACS String 2 Module 30 Impedance | 0 | 1000 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod30V | BSR131UP01BACSDAT1_Str1Mod30V | BR4_Cluster1 | BPL131 | INT | %MW5155 | BSR131UP01 UPS BACS String 1 Module 30 Voltage | 0 | 1000 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod30Imp | BSR131UP01BACSDAT1_Str1Mod30Imp | BR4_Cluster1 | BPL131 | INT | %MW5156 | BSR131UP01 UPS BACS String 1 Module 30 Impedance | 0 | 1000 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod30EqPerc | BSR131UP01BACSDAT1_Str2Mod30EqPerc | BR4_Cluster1 | BPL131 | INT | %MW5156 | BSR131UP01 UPS BACS String 2 Module 30 Equalizing / Balancing | 0 | 100 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod31Tmp | BSR131UP01BACSDAT1_Str2Mod31Tmp | BR4_Cluster1 | BPL131 | INT | %MW5157 | BSR131UP01 UPS BACS String 2 Module 31 Temperature | 0 | 100 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod30EqPerc | BSR131UP01BACSDAT1_Str1Mod30EqPerc | BR4_Cluster1 | BPL131 | INT | %MW5158 | BSR131UP01 UPS BACS String 1 Module 30 Equalizing / Balancing | 0 | 100 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod31V | BSR131UP01BACSDAT1_Str2Mod31V | BR4_Cluster1 | BPL131 | INT | %MW5158 | BSR131UP01 UPS BACS String 2 Module 31 Voltage | 0 | 1000 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod31Tmp | BSR131UP01BACSDAT1_Str1Mod31Tmp | BR4_Cluster1 | BPL131 | INT | %MW5159 | BSR131UP01 UPS BACS String 1 Module 31 Temperature | 0 | 100 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod31Imp | BSR131UP01BACSDAT1_Str2Mod31Imp | BR4_Cluster1 | BPL131 | INT | %MW5159 | BSR131UP01 UPS BACS String 2 Module 31 Impedance | 0 | 1000 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod31V | BSR131UP01BACSDAT1_Str1Mod31V | BR4_Cluster1 | BPL131 | INT | %MW5160 | BSR131UP01 UPS BACS String 1 Module 31 Voltage | 0 | 1000 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod31Imp | BSR131UP01BACSDAT1_Str1Mod31Imp | BR4_Cluster1 | BPL131 | INT | %MW5161 | BSR131UP01 UPS BACS String 1 Module 31 Impedance | 0 | 1000 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod31EqPerc | BSR131UP01BACSDAT1_Str2Mod31EqPerc | BR4_Cluster1 | BPL131 | INT | %MW5161 | BSR131UP01 UPS BACS String 2 Module 31 Equalizing / Balancing | 0 | 100 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod32Tmp | BSR131UP01BACSDAT1_Str2Mod32Tmp | BR4_Cluster1 | BPL131 | INT | %MW5162 | BSR131UP01 UPS BACS String 2 Module 32 Temperature | 0 | 100 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod31EqPerc | BSR131UP01BACSDAT1_Str1Mod31EqPerc | BR4_Cluster1 | BPL131 | INT | %MW5163 | BSR131UP01 UPS BACS String 1 Module 31 Equalizing / Balancing | 0 | 100 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod32V | BSR131UP01BACSDAT1_Str2Mod32V | BR4_Cluster1 | BPL131 | INT | %MW5163 | BSR131UP01 UPS BACS String 2 Module 32 Voltage | 0 | 1000 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod32Tmp | BSR131UP01BACSDAT1_Str1Mod32Tmp | BR4_Cluster1 | BPL131 | INT | %MW5164 | BSR131UP01 UPS BACS String 1 Module 32 Temperature | 0 | 100 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod32Imp | BSR131UP01BACSDAT1_Str2Mod32Imp | BR4_Cluster1 | BPL131 | INT | %MW5164 | BSR131UP01 UPS BACS String 2 Module 32 Impedance | 0 | 1000 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod32V | BSR131UP01BACSDAT1_Str1Mod32V | BR4_Cluster1 | BPL131 | INT | %MW5165 | BSR131UP01 UPS BACS String 1 Module 32 Voltage | 0 | 1000 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod32Imp | BSR131UP01BACSDAT1_Str1Mod32Imp | BR4_Cluster1 | BPL131 | INT | %MW5166 | BSR131UP01 UPS BACS String 1 Module 32 Impedance | 0 | 1000 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod32EqPerc | BSR131UP01BACSDAT1_Str2Mod32EqPerc | BR4_Cluster1 | BPL131 | INT | %MW5166 | BSR131UP01 UPS BACS String 2 Module 32 Equalizing / Balancing | 0 | 100 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod33Tmp | BSR131UP01BACSDAT1_Str2Mod33Tmp | BR4_Cluster1 | BPL131 | INT | %MW5167 | BSR131UP01 UPS BACS String 2 Module 33 Temperature | 0 | 100 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod32EqPerc | BSR131UP01BACSDAT1_Str1Mod32EqPerc | BR4_Cluster1 | BPL131 | INT | %MW5168 | BSR131UP01 UPS BACS String 1 Module 32 Equalizing / Balancing | 0 | 100 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod33V | BSR131UP01BACSDAT1_Str2Mod33V | BR4_Cluster1 | BPL131 | INT | %MW5168 | BSR131UP01 UPS BACS String 2 Module 33 Voltage | 0 | 1000 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod33Tmp | BSR131UP01BACSDAT1_Str1Mod33Tmp | BR4_Cluster1 | BPL131 | INT | %MW5169 | BSR131UP01 UPS BACS String 1 Module 33 Temperature | 0 | 100 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod33Imp | BSR131UP01BACSDAT1_Str2Mod33Imp | BR4_Cluster1 | BPL131 | INT | %MW5169 | BSR131UP01 UPS BACS String 2 Module 33 Impedance | 0 | 1000 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod33V | BSR131UP01BACSDAT1_Str1Mod33V | BR4_Cluster1 | BPL131 | INT | %MW5170 | BSR131UP01 UPS BACS String 1 Module 33 Voltage | 0 | 1000 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod33Imp | BSR131UP01BACSDAT1_Str1Mod33Imp | BR4_Cluster1 | BPL131 | INT | %MW5171 | BSR131UP01 UPS BACS String 1 Module 33 Impedance | 0 | 1000 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod33EqPerc | BSR131UP01BACSDAT1_Str2Mod33EqPerc | BR4_Cluster1 | BPL131 | INT | %MW5171 | BSR131UP01 UPS BACS String 2 Module 33 Equalizing / Balancing | 0 | 100 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod34Tmp | BSR131UP01BACSDAT1_Str2Mod34Tmp | BR4_Cluster1 | BPL131 | INT | %MW5172 | BSR131UP01 UPS BACS String 2 Module 34 Temperature | 0 | 100 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod33EqPerc | BSR131UP01BACSDAT1_Str1Mod33EqPerc | BR4_Cluster1 | BPL131 | INT | %MW5173 | BSR131UP01 UPS BACS String 1 Module 33 Equalizing / Balancing | 0 | 100 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod34V | BSR131UP01BACSDAT1_Str2Mod34V | BR4_Cluster1 | BPL131 | INT | %MW5173 | BSR131UP01 UPS BACS String 2 Module 34 Voltage | 0 | 1000 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod34Tmp | BSR131UP01BACSDAT1_Str1Mod34Tmp | BR4_Cluster1 | BPL131 | INT | %MW5174 | BSR131UP01 UPS BACS String 1 Module 34 Temperature | 0 | 100 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod34Imp | BSR131UP01BACSDAT1_Str2Mod34Imp | BR4_Cluster1 | BPL131 | INT | %MW5174 | BSR131UP01 UPS BACS String 2 Module 34 Impedance | 0 | 1000 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod34V | BSR131UP01BACSDAT1_Str1Mod34V | BR4_Cluster1 | BPL131 | INT | %MW5175 | BSR131UP01 UPS BACS String 1 Module 34 Voltage | 0 | 1000 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod34Imp | BSR131UP01BACSDAT1_Str1Mod34Imp | BR4_Cluster1 | BPL131 | INT | %MW5176 | BSR131UP01 UPS BACS String 1 Module 34 Impedance | 0 | 1000 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod34EqPerc | BSR131UP01BACSDAT1_Str2Mod34EqPerc | BR4_Cluster1 | BPL131 | INT | %MW5176 | BSR131UP01 UPS BACS String 2 Module 34 Equalizing / Balancing | 0 | 100 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod35Tmp | BSR131UP01BACSDAT1_Str2Mod35Tmp | BR4_Cluster1 | BPL131 | INT | %MW5177 | BSR131UP01 UPS BACS String 2 Module 35 Temperature | 0 | 100 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod34EqPerc | BSR131UP01BACSDAT1_Str1Mod34EqPerc | BR4_Cluster1 | BPL131 | INT | %MW5178 | BSR131UP01 UPS BACS String 1 Module 34 Equalizing / Balancing | 0 | 100 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod35V | BSR131UP01BACSDAT1_Str2Mod35V | BR4_Cluster1 | BPL131 | INT | %MW5178 | BSR131UP01 UPS BACS String 2 Module 35 Voltage | 0 | 1000 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod35Tmp | BSR131UP01BACSDAT1_Str1Mod35Tmp | BR4_Cluster1 | BPL131 | INT | %MW5179 | BSR131UP01 UPS BACS String 1 Module 35 Temperature | 0 | 100 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod35Imp | BSR131UP01BACSDAT1_Str2Mod35Imp | BR4_Cluster1 | BPL131 | INT | %MW5179 | BSR131UP01 UPS BACS String 2 Module 35 Impedance | 0 | 1000 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod35V | BSR131UP01BACSDAT1_Str1Mod35V | BR4_Cluster1 | BPL131 | INT | %MW5180 | BSR131UP01 UPS BACS String 1 Module 35 Voltage | 0 | 1000 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod35Imp | BSR131UP01BACSDAT1_Str1Mod35Imp | BR4_Cluster1 | BPL131 | INT | %MW5181 | BSR131UP01 UPS BACS String 1 Module 35 Impedance | 0 | 1000 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod35EqPerc | BSR131UP01BACSDAT1_Str2Mod35EqPerc | BR4_Cluster1 | BPL131 | INT | %MW5181 | BSR131UP01 UPS BACS String 2 Module 35 Equalizing / Balancing | 0 | 100 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod36Tmp | BSR131UP01BACSDAT1_Str2Mod36Tmp | BR4_Cluster1 | BPL131 | INT | %MW5182 | BSR131UP01 UPS BACS String 2 Module 36 Temperature | 0 | 100 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod35EqPerc | BSR131UP01BACSDAT1_Str1Mod35EqPerc | BR4_Cluster1 | BPL131 | INT | %MW5183 | BSR131UP01 UPS BACS String 1 Module 35 Equalizing / Balancing | 0 | 100 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod36V | BSR131UP01BACSDAT1_Str2Mod36V | BR4_Cluster1 | BPL131 | INT | %MW5183 | BSR131UP01 UPS BACS String 2 Module 36 Voltage | 0 | 1000 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod36Tmp | BSR131UP01BACSDAT1_Str1Mod36Tmp | BR4_Cluster1 | BPL131 | INT | %MW5184 | BSR131UP01 UPS BACS String 1 Module 36 Temperature | 0 | 100 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod36Imp | BSR131UP01BACSDAT1_Str2Mod36Imp | BR4_Cluster1 | BPL131 | INT | %MW5184 | BSR131UP01 UPS BACS String 2 Module 36 Impedance | 0 | 1000 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod36V | BSR131UP01BACSDAT1_Str1Mod36V | BR4_Cluster1 | BPL131 | INT | %MW5185 | BSR131UP01 UPS BACS String 1 Module 36 Voltage | 0 | 1000 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod36Imp | BSR131UP01BACSDAT1_Str1Mod36Imp | BR4_Cluster1 | BPL131 | INT | %MW5186 | BSR131UP01 UPS BACS String 1 Module 36 Impedance | 0 | 1000 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod36EqPerc | BSR131UP01BACSDAT1_Str2Mod36EqPerc | BR4_Cluster1 | BPL131 | INT | %MW5186 | BSR131UP01 UPS BACS String 2 Module 36 Equalizing / Balancing | 0 | 100 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod37Tmp | BSR131UP01BACSDAT1_Str2Mod37Tmp | BR4_Cluster1 | BPL131 | INT | %MW5187 | BSR131UP01 UPS BACS String 2 Module 37 Temperature | 0 | 100 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod36EqPerc | BSR131UP01BACSDAT1_Str1Mod36EqPerc | BR4_Cluster1 | BPL131 | INT | %MW5188 | BSR131UP01 UPS BACS String 1 Module 36 Equalizing / Balancing | 0 | 100 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod37V | BSR131UP01BACSDAT1_Str2Mod37V | BR4_Cluster1 | BPL131 | INT | %MW5188 | BSR131UP01 UPS BACS String 2 Module 37 Voltage | 0 | 1000 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod37Tmp | BSR131UP01BACSDAT1_Str1Mod37Tmp | BR4_Cluster1 | BPL131 | INT | %MW5189 | BSR131UP01 UPS BACS String 1 Module 37 Temperature | 0 | 100 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod37Imp | BSR131UP01BACSDAT1_Str2Mod37Imp | BR4_Cluster1 | BPL131 | INT | %MW5189 | BSR131UP01 UPS BACS String 2 Module 37 Impedance | 0 | 1000 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod37V | BSR131UP01BACSDAT1_Str1Mod37V | BR4_Cluster1 | BPL131 | INT | %MW5190 | BSR131UP01 UPS BACS String 1 Module 37 Voltage | 0 | 1000 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod37Imp | BSR131UP01BACSDAT1_Str1Mod37Imp | BR4_Cluster1 | BPL131 | INT | %MW5191 | BSR131UP01 UPS BACS String 1 Module 37 Impedance | 0 | 1000 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod37EqPerc | BSR131UP01BACSDAT1_Str2Mod37EqPerc | BR4_Cluster1 | BPL131 | INT | %MW5191 | BSR131UP01 UPS BACS String 2 Module 37 Equalizing / Balancing | 0 | 100 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod38Tmp | BSR131UP01BACSDAT1_Str2Mod38Tmp | BR4_Cluster1 | BPL131 | INT | %MW5192 | BSR131UP01 UPS BACS String 2 Module 38 Temperature | 0 | 100 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod37EqPerc | BSR131UP01BACSDAT1_Str1Mod37EqPerc | BR4_Cluster1 | BPL131 | INT | %MW5193 | BSR131UP01 UPS BACS String 1 Module 37 Equalizing / Balancing | 0 | 100 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod38V | BSR131UP01BACSDAT1_Str2Mod38V | BR4_Cluster1 | BPL131 | INT | %MW5193 | BSR131UP01 UPS BACS String 2 Module 38 Voltage | 0 | 1000 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod38Tmp | BSR131UP01BACSDAT1_Str1Mod38Tmp | BR4_Cluster1 | BPL131 | INT | %MW5194 | BSR131UP01 UPS BACS String 1 Module 38 Temperature | 0 | 100 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod38Imp | BSR131UP01BACSDAT1_Str2Mod38Imp | BR4_Cluster1 | BPL131 | INT | %MW5194 | BSR131UP01 UPS BACS String 2 Module 38 Impedance | 0 | 1000 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod38V | BSR131UP01BACSDAT1_Str1Mod38V | BR4_Cluster1 | BPL131 | INT | %MW5195 | BSR131UP01 UPS BACS String 1 Module 38 Voltage | 0 | 1000 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod38Imp | BSR131UP01BACSDAT1_Str1Mod38Imp | BR4_Cluster1 | BPL131 | INT | %MW5196 | BSR131UP01 UPS BACS String 1 Module 38 Impedance | 0 | 1000 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod38EqPerc | BSR131UP01BACSDAT1_Str2Mod38EqPerc | BR4_Cluster1 | BPL131 | INT | %MW5196 | BSR131UP01 UPS BACS String 2 Module 38 Equalizing / Balancing | 0 | 100 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod39Tmp | BSR131UP01BACSDAT1_Str2Mod39Tmp | BR4_Cluster1 | BPL131 | INT | %MW5197 | BSR131UP01 UPS BACS String 2 Module 39 Temperature | 0 | 100 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod38EqPerc | BSR131UP01BACSDAT1_Str1Mod38EqPerc | BR4_Cluster1 | BPL131 | INT | %MW5198 | BSR131UP01 UPS BACS String 1 Module 38 Equalizing / Balancing | 0 | 100 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod39V | BSR131UP01BACSDAT1_Str2Mod39V | BR4_Cluster1 | BPL131 | INT | %MW5198 | BSR131UP01 UPS BACS String 2 Module 39 Voltage | 0 | 1000 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod39Tmp | BSR131UP01BACSDAT1_Str1Mod39Tmp | BR4_Cluster1 | BPL131 | INT | %MW5199 | BSR131UP01 UPS BACS String 1 Module 39 Temperature | 0 | 100 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod39Imp | BSR131UP01BACSDAT1_Str2Mod39Imp | BR4_Cluster1 | BPL131 | INT | %MW5199 | BSR131UP01 UPS BACS String 2 Module 39 Impedance | 0 | 1000 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod39V | BSR131UP01BACSDAT1_Str1Mod39V | BR4_Cluster1 | BPL131 | INT | %MW5200 | BSR131UP01 UPS BACS String 1 Module 39 Voltage | 0 | 1000 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod39Imp | BSR131UP01BACSDAT1_Str1Mod39Imp | BR4_Cluster1 | BPL131 | INT | %MW5201 | BSR131UP01 UPS BACS String 1 Module 39 Impedance | 0 | 1000 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod39EqPerc | BSR131UP01BACSDAT1_Str2Mod39EqPerc | BR4_Cluster1 | BPL131 | INT | %MW5201 | BSR131UP01 UPS BACS String 2 Module 39 Equalizing / Balancing | 0 | 100 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod40Tmp | BSR131UP01BACSDAT1_Str2Mod40Tmp | BR4_Cluster1 | BPL131 | INT | %MW5202 | BSR131UP01 UPS BACS String 2 Module 40 Temperature | 0 | 100 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod39EqPerc | BSR131UP01BACSDAT1_Str1Mod39EqPerc | BR4_Cluster1 | BPL131 | INT | %MW5203 | BSR131UP01 UPS BACS String 1 Module 39 Equalizing / Balancing | 0 | 100 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod40V | BSR131UP01BACSDAT1_Str2Mod40V | BR4_Cluster1 | BPL131 | INT | %MW5203 | BSR131UP01 UPS BACS String 2 Module 40 Voltage | 0 | 1000 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod40Tmp | BSR131UP01BACSDAT1_Str1Mod40Tmp | BR4_Cluster1 | BPL131 | INT | %MW5204 | BSR131UP01 UPS BACS String 1 Module 40 Temperature | 0 | 100 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod40Imp | BSR131UP01BACSDAT1_Str2Mod40Imp | BR4_Cluster1 | BPL131 | INT | %MW5204 | BSR131UP01 UPS BACS String 2 Module 40 Impedance | 0 | 1000 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod40V | BSR131UP01BACSDAT1_Str1Mod40V | BR4_Cluster1 | BPL131 | INT | %MW5205 | BSR131UP01 UPS BACS String 1 Module 40 Voltage | 0 | 1000 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod40Imp | BSR131UP01BACSDAT1_Str1Mod40Imp | BR4_Cluster1 | BPL131 | INT | %MW5206 | BSR131UP01 UPS BACS String 1 Module 40 Impedance | 0 | 1000 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod40EqPerc | BSR131UP01BACSDAT1_Str2Mod40EqPerc | BR4_Cluster1 | BPL131 | INT | %MW5206 | BSR131UP01 UPS BACS String 2 Module 40 Equalizing / Balancing | 0 | 100 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod40EqPerc | BSR131UP01BACSDAT1_Str1Mod40EqPerc | BR4_Cluster1 | BPL131 | INT | %MW5208 | BSR131UP01 UPS BACS String 1 Module 40 Equalizing / Balancing | 0 | 100 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2I | BSR131UP01BACSDAT1_Str2I | BR4_Cluster1 | BPL131 | INT | %MW5209 | BSR131UP01 UPS BACS String 2 Current | 0 | 1000 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2AltI | BSR131UP01BACSDAT1_Str2AltI | BR4_Cluster1 | BPL131 | INT | %MW5210 | BSR131UP01 UPS BACS String 2 AC Current | 0 | 1000 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2SumV | BSR131UP01BACSDAT1_Str2SumV | BR4_Cluster1 | BPL131 | INT | %MW5211 | BSR131UP01 UPS BACS String 2 Overall Voltage | 0 | 1000 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2AvgV | BSR131UP01BACSDAT1_Str2AvgV | BR4_Cluster1 | BPL131 | INT | %MW5212 | BSR131UP01 UPS BACS String 2 Average Voltage | 0 | 1000 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod1Tmp | BSR131UP01BACSDAT1_Str2Mod1Tmp | BR4_Cluster1 | BPL131 | INT | %MW5213 | BSR131UP01 UPS BACS String 2 Module 1 Temperature | 0 | 100 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod1V | BSR131UP01BACSDAT1_Str2Mod1V | BR4_Cluster1 | BPL131 | INT | %MW5214 | BSR131UP01 UPS BACS String 2 Module 1 Voltage | 0 | 1000 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod1Imp | BSR131UP01BACSDAT1_Str2Mod1Imp | BR4_Cluster1 | BPL131 | INT | %MW5215 | BSR131UP01 UPS BACS String 2 Module 1 Impedance | 0 | 1000 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod1EqPerc | BSR131UP01BACSDAT1_Str2Mod1EqPerc | BR4_Cluster1 | BPL131 | INT | %MW5217 | BSR131UP01 UPS BACS String 2 Module 1 Equalizing / Balancing | 0 | 100 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod2Tmp | BSR131UP01BACSDAT1_Str2Mod2Tmp | BR4_Cluster1 | BPL131 | INT | %MW5218 | BSR131UP01 UPS BACS String 2 Module 2 Temperature | 0 | 100 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod2V | BSR131UP01BACSDAT1_Str2Mod2V | BR4_Cluster1 | BPL131 | INT | %MW5219 | BSR131UP01 UPS BACS String 2 Module 2 Voltage | 0 | 1000 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod2Imp | BSR131UP01BACSDAT1_Str2Mod2Imp | BR4_Cluster1 | BPL131 | INT | %MW5220 | BSR131UP01 UPS BACS String 2 Module 2 Impedance | 0 | 1000 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod2EqPerc | BSR131UP01BACSDAT1_Str2Mod2EqPerc | BR4_Cluster1 | BPL131 | INT | %MW5222 | BSR131UP01 UPS BACS String 2 Module 2 Equalizing / Balancing | 0 | 100 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod3Tmp | BSR131UP01BACSDAT1_Str2Mod3Tmp | BR4_Cluster1 | BPL131 | INT | %MW5223 | BSR131UP01 UPS BACS String 2 Module 3 Temperature | 0 | 100 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod3V | BSR131UP01BACSDAT1_Str2Mod3V | BR4_Cluster1 | BPL131 | INT | %MW5224 | BSR131UP01 UPS BACS String 2 Module 3 Voltage | 0 | 1000 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod3Imp | BSR131UP01BACSDAT1_Str2Mod3Imp | BR4_Cluster1 | BPL131 | INT | %MW5225 | BSR131UP01 UPS BACS String 2 Module 3 Impedance | 0 | 1000 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod3EqPerc | BSR131UP01BACSDAT1_Str2Mod3EqPerc | BR4_Cluster1 | BPL131 | INT | %MW5227 | BSR131UP01 UPS BACS String 2 Module 3 Equalizing / Balancing | 0 | 100 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod4Tmp | BSR131UP01BACSDAT1_Str2Mod4Tmp | BR4_Cluster1 | BPL131 | INT | %MW5228 | BSR131UP01 UPS BACS String 2 Module 4 Temperature | 0 | 100 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod4V | BSR131UP01BACSDAT1_Str2Mod4V | BR4_Cluster1 | BPL131 | INT | %MW5229 | BSR131UP01 UPS BACS String 2 Module 4 Voltage | 0 | 1000 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod4Imp | BSR131UP01BACSDAT1_Str2Mod4Imp | BR4_Cluster1 | BPL131 | INT | %MW5230 | BSR131UP01 UPS BACS String 2 Module 4 Impedance | 0 | 1000 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod4EqPerc | BSR131UP01BACSDAT1_Str2Mod4EqPerc | BR4_Cluster1 | BPL131 | INT | %MW5232 | BSR131UP01 UPS BACS String 2 Module 4 Equalizing / Balancing | 0 | 100 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod5Tmp | BSR131UP01BACSDAT1_Str2Mod5Tmp | BR4_Cluster1 | BPL131 | INT | %MW5233 | BSR131UP01 UPS BACS String 2 Module 5 Temperature | 0 | 100 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod5V | BSR131UP01BACSDAT1_Str2Mod5V | BR4_Cluster1 | BPL131 | INT | %MW5234 | BSR131UP01 UPS BACS String 2 Module 5 Voltage | 0 | 1000 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod5Imp | BSR131UP01BACSDAT1_Str2Mod5Imp | BR4_Cluster1 | BPL131 | INT | %MW5235 | BSR131UP01 UPS BACS String 2 Module 5 Impedance | 0 | 1000 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod5EqPerc | BSR131UP01BACSDAT1_Str2Mod5EqPerc | BR4_Cluster1 | BPL131 | INT | %MW5237 | BSR131UP01 UPS BACS String 2 Module 5 Equalizing / Balancing | 0 | 100 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod6Tmp | BSR131UP01BACSDAT1_Str2Mod6Tmp | BR4_Cluster1 | BPL131 | INT | %MW5238 | BSR131UP01 UPS BACS String 2 Module 6 Temperature | 0 | 100 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod6V | BSR131UP01BACSDAT1_Str2Mod6V | BR4_Cluster1 | BPL131 | INT | %MW5239 | BSR131UP01 UPS BACS String 2 Module 6 Voltage | 0 | 1000 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod6Imp | BSR131UP01BACSDAT1_Str2Mod6Imp | BR4_Cluster1 | BPL131 | INT | %MW5240 | BSR131UP01 UPS BACS String 2 Module 6 Impedance | 0 | 1000 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod6EqPerc | BSR131UP01BACSDAT1_Str2Mod6EqPerc | BR4_Cluster1 | BPL131 | INT | %MW5242 | BSR131UP01 UPS BACS String 2 Module 6 Equalizing / Balancing | 0 | 100 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod7Tmp | BSR131UP01BACSDAT1_Str2Mod7Tmp | BR4_Cluster1 | BPL131 | INT | %MW5243 | BSR131UP01 UPS BACS String 2 Module 7 Temperature | 0 | 100 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod7V | BSR131UP01BACSDAT1_Str2Mod7V | BR4_Cluster1 | BPL131 | INT | %MW5244 | BSR131UP01 UPS BACS String 2 Module 7 Voltage | 0 | 1000 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod7Imp | BSR131UP01BACSDAT1_Str2Mod7Imp | BR4_Cluster1 | BPL131 | INT | %MW5245 | BSR131UP01 UPS BACS String 2 Module 7 Impedance | 0 | 1000 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod7EqPerc | BSR131UP01BACSDAT1_Str2Mod7EqPerc | BR4_Cluster1 | BPL131 | INT | %MW5247 | BSR131UP01 UPS BACS String 2 Module 7 Equalizing / Balancing | 0 | 100 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod8Tmp | BSR131UP01BACSDAT1_Str2Mod8Tmp | BR4_Cluster1 | BPL131 | INT | %MW5248 | BSR131UP01 UPS BACS String 2 Module 8 Temperature | 0 | 100 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod8V | BSR131UP01BACSDAT1_Str2Mod8V | BR4_Cluster1 | BPL131 | INT | %MW5249 | BSR131UP01 UPS BACS String 2 Module 8 Voltage | 0 | 1000 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod8Imp | BSR131UP01BACSDAT1_Str2Mod8Imp | BR4_Cluster1 | BPL131 | INT | %MW5250 | BSR131UP01 UPS BACS String 2 Module 8 Impedance | 0 | 1000 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod8EqPerc | BSR131UP01BACSDAT1_Str2Mod8EqPerc | BR4_Cluster1 | BPL131 | INT | %MW5252 | BSR131UP01 UPS BACS String 2 Module 8 Equalizing / Balancing | 0 | 100 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod9Tmp | BSR131UP01BACSDAT1_Str2Mod9Tmp | BR4_Cluster1 | BPL131 | INT | %MW5253 | BSR131UP01 UPS BACS String 2 Module 9 Temperature | 0 | 100 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod9V | BSR131UP01BACSDAT1_Str2Mod9V | BR4_Cluster1 | BPL131 | INT | %MW5254 | BSR131UP01 UPS BACS String 2 Module 9 Voltage | 0 | 1000 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod9Imp | BSR131UP01BACSDAT1_Str2Mod9Imp | BR4_Cluster1 | BPL131 | INT | %MW5255 | BSR131UP01 UPS BACS String 2 Module 9 Impedance | 0 | 1000 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod9EqPerc | BSR131UP01BACSDAT1_Str2Mod9EqPerc | BR4_Cluster1 | BPL131 | INT | %MW5257 | BSR131UP01 UPS BACS String 2 Module 9 Equalizing / Balancing | 0 | 100 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod10Tmp | BSR131UP01BACSDAT1_Str2Mod10Tmp | BR4_Cluster1 | BPL131 | INT | %MW5258 | BSR131UP01 UPS BACS String 2 Module 10 Temperature | 0 | 100 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod10V | BSR131UP01BACSDAT1_Str2Mod10V | BR4_Cluster1 | BPL131 | INT | %MW5259 | BSR131UP01 UPS BACS String 2 Module 10 Voltage | 0 | 1000 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod10Imp | BSR131UP01BACSDAT1_Str2Mod10Imp | BR4_Cluster1 | BPL131 | INT | %MW5260 | BSR131UP01 UPS BACS String 2 Module 10 Impedance | 0 | 1000 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod10EqPerc | BSR131UP01BACSDAT1_Str2Mod10EqPerc | BR4_Cluster1 | BPL131 | INT | %MW5262 | BSR131UP01 UPS BACS String 2 Module 10 Equalizing / Balancing | 0 | 100 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod11Tmp | BSR131UP01BACSDAT1_Str2Mod11Tmp | BR4_Cluster1 | BPL131 | INT | %MW5263 | BSR131UP01 UPS BACS String 2 Module 11 Temperature | 0 | 100 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod11V | BSR131UP01BACSDAT1_Str2Mod11V | BR4_Cluster1 | BPL131 | INT | %MW5264 | BSR131UP01 UPS BACS String 2 Module 11 Voltage | 0 | 1000 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod11Imp | BSR131UP01BACSDAT1_Str2Mod11Imp | BR4_Cluster1 | BPL131 | INT | %MW5265 | BSR131UP01 UPS BACS String 2 Module 11 Impedance | 0 | 1000 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod11EqPerc | BSR131UP01BACSDAT1_Str2Mod11EqPerc | BR4_Cluster1 | BPL131 | INT | %MW5267 | BSR131UP01 UPS BACS String 2 Module 11 Equalizing / Balancing | 0 | 100 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod12Tmp | BSR131UP01BACSDAT1_Str2Mod12Tmp | BR4_Cluster1 | BPL131 | INT | %MW5268 | BSR131UP01 UPS BACS String 2 Module 12 Temperature | 0 | 100 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod12V | BSR131UP01BACSDAT1_Str2Mod12V | BR4_Cluster1 | BPL131 | INT | %MW5269 | BSR131UP01 UPS BACS String 2 Module 12 Voltage | 0 | 1000 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod12Imp | BSR131UP01BACSDAT1_Str2Mod12Imp | BR4_Cluster1 | BPL131 | INT | %MW5270 | BSR131UP01 UPS BACS String 2 Module 12 Impedance | 0 | 1000 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod12EqPerc | BSR131UP01BACSDAT1_Str2Mod12EqPerc | BR4_Cluster1 | BPL131 | INT | %MW5272 | BSR131UP01 UPS BACS String 2 Module 12 Equalizing / Balancing | 0 | 100 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod13Tmp | BSR131UP01BACSDAT1_Str2Mod13Tmp | BR4_Cluster1 | BPL131 | INT | %MW5273 | BSR131UP01 UPS BACS String 2 Module 13 Temperature | 0 | 100 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod13V | BSR131UP01BACSDAT1_Str2Mod13V | BR4_Cluster1 | BPL131 | INT | %MW5274 | BSR131UP01 UPS BACS String 2 Module 13 Voltage | 0 | 1000 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod13Imp | BSR131UP01BACSDAT1_Str2Mod13Imp | BR4_Cluster1 | BPL131 | INT | %MW5275 | BSR131UP01 UPS BACS String 2 Module 13 Impedance | 0 | 1000 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod13EqPerc | BSR131UP01BACSDAT1_Str2Mod13EqPerc | BR4_Cluster1 | BPL131 | INT | %MW5277 | BSR131UP01 UPS BACS String 2 Module 13 Equalizing / Balancing | 0 | 100 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod14Tmp | BSR131UP01BACSDAT1_Str2Mod14Tmp | BR4_Cluster1 | BPL131 | INT | %MW5278 | BSR131UP01 UPS BACS String 2 Module 14 Temperature | 0 | 100 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod14V | BSR131UP01BACSDAT1_Str2Mod14V | BR4_Cluster1 | BPL131 | INT | %MW5279 | BSR131UP01 UPS BACS String 2 Module 14 Voltage | 0 | 1000 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod14Imp | BSR131UP01BACSDAT1_Str2Mod14Imp | BR4_Cluster1 | BPL131 | INT | %MW5280 | BSR131UP01 UPS BACS String 2 Module 14 Impedance | 0 | 1000 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod14EqPerc | BSR131UP01BACSDAT1_Str2Mod14EqPerc | BR4_Cluster1 | BPL131 | INT | %MW5282 | BSR131UP01 UPS BACS String 2 Module 14 Equalizing / Balancing | 0 | 100 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod15Tmp | BSR131UP01BACSDAT1_Str2Mod15Tmp | BR4_Cluster1 | BPL131 | INT | %MW5283 | BSR131UP01 UPS BACS String 2 Module 15 Temperature | 0 | 100 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod15V | BSR131UP01BACSDAT1_Str2Mod15V | BR4_Cluster1 | BPL131 | INT | %MW5284 | BSR131UP01 UPS BACS String 2 Module 15 Voltage | 0 | 1000 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod15Imp | BSR131UP01BACSDAT1_Str2Mod15Imp | BR4_Cluster1 | BPL131 | INT | %MW5285 | BSR131UP01 UPS BACS String 2 Module 15 Impedance | 0 | 1000 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod15EqPerc | BSR131UP01BACSDAT1_Str2Mod15EqPerc | BR4_Cluster1 | BPL131 | INT | %MW5287 | BSR131UP01 UPS BACS String 2 Module 15 Equalizing / Balancing | 0 | 100 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod16Tmp | BSR131UP01BACSDAT1_Str2Mod16Tmp | BR4_Cluster1 | BPL131 | INT | %MW5288 | BSR131UP01 UPS BACS String 2 Module 16 Temperature | 0 | 100 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod16V | BSR131UP01BACSDAT1_Str2Mod16V | BR4_Cluster1 | BPL131 | INT | %MW5289 | BSR131UP01 UPS BACS String 2 Module 16 Voltage | 0 | 1000 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod16Imp | BSR131UP01BACSDAT1_Str2Mod16Imp | BR4_Cluster1 | BPL131 | INT | %MW5290 | BSR131UP01 UPS BACS String 2 Module 16 Impedance | 0 | 1000 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod16EqPerc | BSR131UP01BACSDAT1_Str2Mod16EqPerc | BR4_Cluster1 | BPL131 | INT | %MW5292 | BSR131UP01 UPS BACS String 2 Module 16 Equalizing / Balancing | 0 | 100 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod17Tmp | BSR131UP01BACSDAT1_Str2Mod17Tmp | BR4_Cluster1 | BPL131 | INT | %MW5293 | BSR131UP01 UPS BACS String 2 Module 17 Temperature | 0 | 100 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod17V | BSR131UP01BACSDAT1_Str2Mod17V | BR4_Cluster1 | BPL131 | INT | %MW5294 | BSR131UP01 UPS BACS String 2 Module 17 Voltage | 0 | 1000 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod17Imp | BSR131UP01BACSDAT1_Str2Mod17Imp | BR4_Cluster1 | BPL131 | INT | %MW5295 | BSR131UP01 UPS BACS String 2 Module 17 Impedance | 0 | 1000 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod17EqPerc | BSR131UP01BACSDAT1_Str2Mod17EqPerc | BR4_Cluster1 | BPL131 | INT | %MW5297 | BSR131UP01 UPS BACS String 2 Module 17 Equalizing / Balancing | 0 | 100 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod18Tmp | BSR131UP01BACSDAT1_Str2Mod18Tmp | BR4_Cluster1 | BPL131 | INT | %MW5298 | BSR131UP01 UPS BACS String 2 Module 18 Temperature | 0 | 100 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod18V | BSR131UP01BACSDAT1_Str2Mod18V | BR4_Cluster1 | BPL131 | INT | %MW5299 | BSR131UP01 UPS BACS String 2 Module 18 Voltage | 0 | 1000 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod18Imp | BSR131UP01BACSDAT1_Str2Mod18Imp | BR4_Cluster1 | BPL131 | INT | %MW5300 | BSR131UP01 UPS BACS String 2 Module 18 Impedance | 0 | 1000 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod18EqPerc | BSR131UP01BACSDAT1_Str2Mod18EqPerc | BR4_Cluster1 | BPL131 | INT | %MW5302 | BSR131UP01 UPS BACS String 2 Module 18 Equalizing / Balancing | 0 | 100 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod19Tmp | BSR131UP01BACSDAT1_Str2Mod19Tmp | BR4_Cluster1 | BPL131 | INT | %MW5303 | BSR131UP01 UPS BACS String 2 Module 19 Temperature | 0 | 100 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod19V | BSR131UP01BACSDAT1_Str2Mod19V | BR4_Cluster1 | BPL131 | INT | %MW5304 | BSR131UP01 UPS BACS String 2 Module 19 Voltage | 0 | 1000 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod19Imp | BSR131UP01BACSDAT1_Str2Mod19Imp | BR4_Cluster1 | BPL131 | INT | %MW5305 | BSR131UP01 UPS BACS String 2 Module 19 Impedance | 0 | 1000 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod19EqPerc | BSR131UP01BACSDAT1_Str2Mod19EqPerc | BR4_Cluster1 | BPL131 | INT | %MW5307 | BSR131UP01 UPS BACS String 2 Module 19 Equalizing / Balancing | 0 | 100 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod20Tmp | BSR131UP01BACSDAT1_Str2Mod20Tmp | BR4_Cluster1 | BPL131 | INT | %MW5308 | BSR131UP01 UPS BACS String 2 Module 20 Temperature | 0 | 100 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod20V | BSR131UP01BACSDAT1_Str2Mod20V | BR4_Cluster1 | BPL131 | INT | %MW5309 | BSR131UP01 UPS BACS String 2 Module 20 Voltage | 0 | 1000 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod20Imp | BSR131UP01BACSDAT1_Str2Mod20Imp | BR4_Cluster1 | BPL131 | INT | %MW5310 | BSR131UP01 UPS BACS String 2 Module 20 Impedance | 0 | 1000 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod20EqPerc | BSR131UP01BACSDAT1_Str2Mod20EqPerc | BR4_Cluster1 | BPL131 | INT | %MW5312 | BSR131UP01 UPS BACS String 2 Module 20 Equalizing / Balancing | 0 | 100 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod21Tmp | BSR131UP01BACSDAT1_Str2Mod21Tmp | BR4_Cluster1 | BPL131 | INT | %MW5313 | BSR131UP01 UPS BACS String 2 Module 21 Temperature | 0 | 100 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod21V | BSR131UP01BACSDAT1_Str2Mod21V | BR4_Cluster1 | BPL131 | INT | %MW5314 | BSR131UP01 UPS BACS String 2 Module 21 Voltage | 0 | 1000 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod21Imp | BSR131UP01BACSDAT1_Str2Mod21Imp | BR4_Cluster1 | BPL131 | INT | %MW5315 | BSR131UP01 UPS BACS String 2 Module 21 Impedance | 0 | 1000 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod21EqPerc | BSR131UP01BACSDAT1_Str2Mod21EqPerc | BR4_Cluster1 | BPL131 | INT | %MW5317 | BSR131UP01 UPS BACS String 2 Module 21 Equalizing / Balancing | 0 | 100 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod22Tmp | BSR131UP01BACSDAT1_Str2Mod22Tmp | BR4_Cluster1 | BPL131 | INT | %MW5318 | BSR131UP01 UPS BACS String 2 Module 22 Temperature | 0 | 100 | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1101 |  | BPP1101PIC01_Cmd | BR4_Cluster1 | BPL131 | INT | %MW7006 | BPP1101 Pressure Controller HMI Commands |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1103 |  | BPP1103LIC01_Cmd | BR4_Cluster1 | BPL131 | INT | %MW7030 | West Turkeys Nest Level Controller HMI Commands |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BSTD1106 |  | BSTD1106FIC01_Cmd | BR4_Cluster1 | BPL131 | INT | %MW7066 | West Turkeys Nest LME Standpipe Flow Controller HMI Commands |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BSTD1107 |  | BSTD1107FIC01_Cmd | BR4_Cluster1 | BPL131 | INT | %MW7078 | West Turkeys Nest HME Standpipe Flow Controller HMI Commands |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC01 |  | BMC131INC01PR1DAT1 | BR4_Cluster1 | BPL131 | INT | %MW900[74] | BMC131 Process Bus Incomer Protection Relay Status Data for HMI Display |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC02 |  | BMC131INC02PR1DAT1 | BR4_Cluster1 | BPL131 | INT | %MW976[74] | BMC131 Essential Bus Incomer Protection Relay Status Data for HMI Display |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1101 |  | BPP1101_RunTm | BR4_Cluster1 | BPL131 | LONG | %MD1180 | Production Plant and NPI Water Supply Pump 1 Running Time Totaliser (min) |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1102 |  | BPP1102_RunTm | BR4_Cluster1 | BPL131 | LONG | %MD1274 | Production Plant and NPI Water Supply Pump 2 Running Time Totaliser (min) |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1103 |  | BPP1103_RunTm | BR4_Cluster1 | BPL131 | LONG | %MD1304 | Water Transfer Pump 1 Running Time Totaliser (min) |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1104 |  | BPP1104_RunTm | BR4_Cluster1 | BPL131 | LONG | %MD1378 | Water Transfer Pump 2 Running Time Totaliser (min) |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1105 |  | BPP1105_RunTm | BR4_Cluster1 | BPL131 | LONG | %MD1426 | Water Transfer Pump 3 Running Time Totaliser (min) |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BPP1106 |  | BPP1106_RunTm | BR4_Cluster1 | BPL131 | LONG | %MD1474 | HME & LME Standpipe Pump 3 Running Time Totaliser (min) |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BPP1107 |  | BPP1107_RunTm | BR4_Cluster1 | BPL131 | LONG | %MD1504 | HME & LME Standpipe Pump 4 Running Time Totaliser (min) |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1101.VS01 | FltID | BPP1101VS01DAT1_FltID | BR4_Cluster1 | BPL131 | LONG | %MD6000 | BPP1101VS01 VVVF Drive Fault ID |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1102.VS01 | FltID | BPP1102VS01DAT1_FltID | BR4_Cluster1 | BPL131 | LONG | %MD6100 | BPP1102VS01 VVVF Drive Fault ID |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1103.VS01 | FltID | BPP1103VS01DAT1_FltID | BR4_Cluster1 | BPL131 | LONG | %MD6200 | BPP1103VS01 VVVF Drive Fault ID |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1104.VS01 | FltID | BPP1104VS01DAT1_FltID | BR4_Cluster1 | BPL131 | LONG | %MD6300 | BPP1104VS01 VVVF Drive Fault ID |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1105.VS01 | FltID | BPP1105VS01DAT1_FltID | BR4_Cluster1 | BPL131 | LONG | %MD6400 | BPP1105VS01 VVVF Drive Fault ID |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1106.VS01 | FltID | BPP1106VS01DAT1_FltID | BR4_Cluster1 | BPL131 | LONG | %MD6500 | BPP1106VS01 VVVF Drive Fault ID |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1107.VS01 | FltID | BPP1107VS01DAT1_FltID | BR4_Cluster1 | BPL131 | LONG | %MD6600 | BPP1107VS01 VVVF Drive Fault ID |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC02.MasterPact | In | BMC131INC02PR1DAT1_In | BR4_Cluster1 | BPL131 | REAL | %MF1000 | BMC131INC02 Process Incomer MasterPact RMS Current on Neutral | 0 | 1000 | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC02.MasterPact | Vab | BMC131INC02PR1DAT1_Vab | BR4_Cluster1 | BPL131 | REAL | %MF1002 | BMC131INC02 Process Incomer MasterPact RMS Phase A to B Voltage | 0 | 1000 | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC02.MasterPact | Vbc | BMC131INC02PR1DAT1_Vbc | BR4_Cluster1 | BPL131 | REAL | %MF1004 | BMC131INC02 Process Incomer MasterPact RMS Phase B to C Voltage | 0 | 1000 | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC02.MasterPact | Vca | BMC131INC02PR1DAT1_Vca | BR4_Cluster1 | BPL131 | REAL | %MF1006 | BMC131INC02 Process Incomer MasterPact RMS Phase C to A Voltage | 0 | 1000 | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC02.MasterPact | Van | BMC131INC02PR1DAT1_Van | BR4_Cluster1 | BPL131 | REAL | %MF1008 | BMC131INC02 Process Incomer MasterPact RMS Phase A Voltage | 0 | 1000 | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC02.MasterPact | Vbn | BMC131INC02PR1DAT1_Vbn | BR4_Cluster1 | BPL131 | REAL | %MF1010 | BMC131INC02 Process Incomer MasterPact RMS Phase B Voltage | 0 | 1000 | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC02.MasterPact | Vcn | BMC131INC02PR1DAT1_Vcn | BR4_Cluster1 | BPL131 | REAL | %MF1012 | BMC131INC02 Process Incomer MasterPact RMS Phase C Voltage | 0 | 1000 | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC02.MasterPact | Ig | BMC131INC02PR1DAT1_Ig | BR4_Cluster1 | BPL131 | REAL | %MF1022 | BMC131INC02 Process Incomer MasterPact Ground Fault Current | 0 | 1000 | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC02.MasterPact | PwrAct | BMC131INC02PR1DAT1_PwrAct | BR4_Cluster1 | BPL131 | REAL | %MF1024 | BMC131INC02 Process Incomer MasterPact Total Active Power | 0 | 10000 | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC02.MasterPact | PwrRct | BMC131INC02PR1DAT1_PwrRct | BR4_Cluster1 | BPL131 | REAL | %MF1026 | BMC131INC02 Process Incomer MasterPact Total Reactive Power | 0 | 10000 | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC02.MasterPact | PwrApr | BMC131INC02PR1DAT1_PwrApr | BR4_Cluster1 | BPL131 | REAL | %MF1028 | BMC131INC02 Process Incomer MasterPact Total Apparent Power | 0 | 10000 | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC02.MasterPact | PF | BMC131INC02PR1DAT1_PF | BR4_Cluster1 | BPL131 | REAL | %MF1030 | BMC131INC02 Process Incomer MasterPact Total Power Factor | 0 | 1 | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC02.MasterPact | VabTHD | BMC131INC02PR1DAT1_VabTHD | BR4_Cluster1 | BPL131 | REAL | %MF1032 | BMC131INC02 Process Incomer MasterPact RMS Phase A to B Voltage Total Harmonic Distortion | 0 | 100 | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC02.MasterPact | VbcTHD | BMC131INC02PR1DAT1_VbcTHD | BR4_Cluster1 | BPL131 | REAL | %MF1034 | BMC131INC02 Process Incomer MasterPact RMS Phase B to C Voltage Total Harmonic Distortion | 0 | 100 | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC02.MasterPact | VcaTHD | BMC131INC02PR1DAT1_VcaTHD | BR4_Cluster1 | BPL131 | REAL | %MF1036 | BMC131INC02 Process Incomer MasterPact RMS Phase C to A Voltage Total Harmonic Distortion | 0 | 100 | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC02.MasterPact | VanTHD | BMC131INC02PR1DAT1_VanTHD | BR4_Cluster1 | BPL131 | REAL | %MF1038 | BMC131INC02 Process Incomer MasterPact RMS Phase A Voltage Total Harmonic Distortion | 0 | 100 | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC02.MasterPact | VbnTHD | BMC131INC02PR1DAT1_VbnTHD | BR4_Cluster1 | BPL131 | REAL | %MF1040 | BMC131INC02 Process Incomer MasterPact RMS Phase B Voltage Total Harmonic Distortion | 0 | 100 | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC02.MasterPact | VcnTHD | BMC131INC02PR1DAT1_VcnTHD | BR4_Cluster1 | BPL131 | REAL | %MF1042 | BMC131INC02 Process Incomer MasterPact RMS Phase C Voltage Total Harmonic Distortion | 0 | 100 | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC02.MasterPact | IaTHD | BMC131INC02PR1DAT1_IaTHD | BR4_Cluster1 | BPL131 | REAL | %MF1044 | BMC131INC02 Process Incomer MasterPact RMS Current on Phase A Total Harmonic Distortion | 0 | 100 | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC02.MasterPact | IbTHD | BMC131INC02PR1DAT1_IbTHD | BR4_Cluster1 | BPL131 | REAL | %MF1046 | BMC131INC02 Process Incomer MasterPact RMS Current on Phase B Total Harmonic Distortion | 0 | 100 | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC02.MasterPact | IcTHD | BMC131INC02PR1DAT1_IcTHD | BR4_Cluster1 | BPL131 | REAL | %MF1048 | BMC131INC02 Process Incomer MasterPact RMS Current on Phase C Total Harmonic Distortion | 0 | 100 | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC03.MasterPact | Frq | BMC131INC03PR1DAT1_Frq | BR4_Cluster1 | BPL131 | REAL | %MF1065 | BMC131INC03 Process Incomer MasterPact Frequency | 0 | 70 | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC03.MasterPact | Ia | BMC131INC03PR1DAT1_Ia | BR4_Cluster1 | BPL131 | REAL | %MF1068 | BMC131INC03 Process Incomer MasterPact RMS Current on Phase A | 0 | 1000 | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC03.MasterPact | Ib | BMC131INC03PR1DAT1_Ib | BR4_Cluster1 | BPL131 | REAL | %MF1070 | BMC131INC03 Process Incomer MasterPact RMS Current on Phase B | 0 | 1000 | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC03.MasterPact | Ic | BMC131INC03PR1DAT1_Ic | BR4_Cluster1 | BPL131 | REAL | %MF1072 | BMC131INC03 Process Incomer MasterPact RMS Current on Phase C | 0 | 1000 | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC03.MasterPact | In | BMC131INC03PR1DAT1_In | BR4_Cluster1 | BPL131 | REAL | %MF1074 | BMC131INC03 Process Incomer MasterPact RMS Current on Neutral | 0 | 1000 | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC03.MasterPact | Vab | BMC131INC03PR1DAT1_Vab | BR4_Cluster1 | BPL131 | REAL | %MF1076 | BMC131INC03 Process Incomer MasterPact RMS Phase A to B Voltage | 0 | 1000 | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC03.MasterPact | Vbc | BMC131INC03PR1DAT1_Vbc | BR4_Cluster1 | BPL131 | REAL | %MF1078 | BMC131INC03 Process Incomer MasterPact RMS Phase B to C Voltage | 0 | 1000 | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC03.MasterPact | Vca | BMC131INC03PR1DAT1_Vca | BR4_Cluster1 | BPL131 | REAL | %MF1080 | BMC131INC03 Process Incomer MasterPact RMS Phase C to A Voltage | 0 | 1000 | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC03.MasterPact | Van | BMC131INC03PR1DAT1_Van | BR4_Cluster1 | BPL131 | REAL | %MF1082 | BMC131INC03 Process Incomer MasterPact RMS Phase A Voltage | 0 | 1000 | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC03.MasterPact | Vbn | BMC131INC03PR1DAT1_Vbn | BR4_Cluster1 | BPL131 | REAL | %MF1084 | BMC131INC03 Process Incomer MasterPact RMS Phase B Voltage | 0 | 1000 | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC03.MasterPact | Vcn | BMC131INC03PR1DAT1_Vcn | BR4_Cluster1 | BPL131 | REAL | %MF1086 | BMC131INC03 Process Incomer MasterPact RMS Phase C Voltage | 0 | 1000 | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC03.MasterPact | Ig | BMC131INC03PR1DAT1_Ig | BR4_Cluster1 | BPL131 | REAL | %MF1096 | BMC131INC03 Process Incomer MasterPact Ground Fault Current | 0 | 1000 | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC03.MasterPact | PwrAct | BMC131INC03PR1DAT1_PwrAct | BR4_Cluster1 | BPL131 | REAL | %MF1098 | BMC131INC03 Process Incomer MasterPact Total Active Power | 0 | 10000 | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC03.MasterPact | PwrRct | BMC131INC03PR1DAT1_PwrRct | BR4_Cluster1 | BPL131 | REAL | %MF1100 | BMC131INC03 Process Incomer MasterPact Total Reactive Power | 0 | 10000 | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC03.MasterPact | PwrApr | BMC131INC03PR1DAT1_PwrApr | BR4_Cluster1 | BPL131 | REAL | %MF1102 | BMC131INC03 Process Incomer MasterPact Total Apparent Power | 0 | 10000 | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC03.MasterPact | PF | BMC131INC03PR1DAT1_PF | BR4_Cluster1 | BPL131 | REAL | %MF1104 | BMC131INC03 Process Incomer MasterPact Total Power Factor | 0 | 1 | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC03.MasterPact | VabTHD | BMC131INC03PR1DAT1_VabTHD | BR4_Cluster1 | BPL131 | REAL | %MF1106 | BMC131INC03 Process Incomer MasterPact RMS Phase A to B Voltage Total Harmonic Distortion | 0 | 100 | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC03.MasterPact | VbcTHD | BMC131INC03PR1DAT1_VbcTHD | BR4_Cluster1 | BPL131 | REAL | %MF1108 | BMC131INC03 Process Incomer MasterPact RMS Phase B to C Voltage Total Harmonic Distortion | 0 | 100 | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC03.MasterPact | VcaTHD | BMC131INC03PR1DAT1_VcaTHD | BR4_Cluster1 | BPL131 | REAL | %MF1110 | BMC131INC03 Process Incomer MasterPact RMS Phase C to A Voltage Total Harmonic Distortion | 0 | 100 | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC03.MasterPact | VanTHD | BMC131INC03PR1DAT1_VanTHD | BR4_Cluster1 | BPL131 | REAL | %MF1112 | BMC131INC03 Process Incomer MasterPact RMS Phase A Voltage Total Harmonic Distortion | 0 | 100 | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC03.MasterPact | VbnTHD | BMC131INC03PR1DAT1_VbnTHD | BR4_Cluster1 | BPL131 | REAL | %MF1114 | BMC131INC03 Process Incomer MasterPact RMS Phase B Voltage Total Harmonic Distortion | 0 | 100 | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC03.MasterPact | VcnTHD | BMC131INC03PR1DAT1_VcnTHD | BR4_Cluster1 | BPL131 | REAL | %MF1116 | BMC131INC03 Process Incomer MasterPact RMS Phase C Voltage Total Harmonic Distortion | 0 | 100 | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC03.MasterPact | IaTHD | BMC131INC03PR1DAT1_IaTHD | BR4_Cluster1 | BPL131 | REAL | %MF1118 | BMC131INC03 Process Incomer MasterPact RMS Current on Phase A Total Harmonic Distortion | 0 | 100 | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC03.MasterPact | IbTHD | BMC131INC03PR1DAT1_IbTHD | BR4_Cluster1 | BPL131 | REAL | %MF1120 | BMC131INC03 Process Incomer MasterPact RMS Current on Phase B Total Harmonic Distortion | 0 | 100 | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC03.MasterPact | IcTHD | BMC131INC03PR1DAT1_IcTHD | BR4_Cluster1 | BPL131 | REAL | %MF1122 | BMC131INC03 Process Incomer MasterPact RMS Current on Phase C Total Harmonic Distortion | 0 | 100 | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC01.MasterPact | Frq | BMC131INC01PR1DAT1_Frq | BR4_Cluster1 | BPL131 | REAL | %MF915 | BMC131INC01 Process Incomer MasterPact Frequency | 0 | 70 | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC01.MasterPact | Ia | BMC131INC01PR1DAT1_Ia | BR4_Cluster1 | BPL131 | REAL | %MF918 | BMC131INC01 Process Incomer MasterPact RMS Current on Phase A | 0 | 1000 | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC01.MasterPact | Ib | BMC131INC01PR1DAT1_Ib | BR4_Cluster1 | BPL131 | REAL | %MF920 | BMC131INC01 Process Incomer MasterPact RMS Current on Phase B | 0 | 1000 | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC01.MasterPact | Ic | BMC131INC01PR1DAT1_Ic | BR4_Cluster1 | BPL131 | REAL | %MF922 | BMC131INC01 Process Incomer MasterPact RMS Current on Phase C | 0 | 1000 | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC01.MasterPact | In | BMC131INC01PR1DAT1_In | BR4_Cluster1 | BPL131 | REAL | %MF924 | BMC131INC01 Process Incomer MasterPact RMS Current on Neutral | 0 | 1000 | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC01.MasterPact | Vab | BMC131INC01PR1DAT1_Vab | BR4_Cluster1 | BPL131 | REAL | %MF926 | BMC131INC01 Process Incomer MasterPact RMS Phase A to B Voltage | 0 | 1000 | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC01.MasterPact | Vbc | BMC131INC01PR1DAT1_Vbc | BR4_Cluster1 | BPL131 | REAL | %MF928 | BMC131INC01 Process Incomer MasterPact RMS Phase B to C Voltage | 0 | 1000 | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC01.MasterPact | Vca | BMC131INC01PR1DAT1_Vca | BR4_Cluster1 | BPL131 | REAL | %MF930 | BMC131INC01 Process Incomer MasterPact RMS Phase C to A Voltage | 0 | 1000 | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC01.MasterPact | Van | BMC131INC01PR1DAT1_Van | BR4_Cluster1 | BPL131 | REAL | %MF932 | BMC131INC01 Process Incomer MasterPact RMS Phase A Voltage | 0 | 1000 | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC01.MasterPact | Vbn | BMC131INC01PR1DAT1_Vbn | BR4_Cluster1 | BPL131 | REAL | %MF934 | BMC131INC01 Process Incomer MasterPact RMS Phase B Voltage | 0 | 1000 | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC01.MasterPact | Vcn | BMC131INC01PR1DAT1_Vcn | BR4_Cluster1 | BPL131 | REAL | %MF936 | BMC131INC01 Process Incomer MasterPact RMS Phase C Voltage | 0 | 1000 | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC01.MasterPact | Ig | BMC131INC01PR1DAT1_Ig | BR4_Cluster1 | BPL131 | REAL | %MF946 | BMC131INC01 Process Incomer MasterPact Ground Fault Current | 0 | 1000 | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC01.MasterPact | PwrAct | BMC131INC01PR1DAT1_PwrAct | BR4_Cluster1 | BPL131 | REAL | %MF948 | BMC131INC01 Process Incomer MasterPact Total Active Power | 0 | 10000 | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC01.MasterPact | PwrRct | BMC131INC01PR1DAT1_PwrRct | BR4_Cluster1 | BPL131 | REAL | %MF950 | BMC131INC01 Process Incomer MasterPact Total Reactive Power | 0 | 10000 | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC01.MasterPact | PwrApr | BMC131INC01PR1DAT1_PwrApr | BR4_Cluster1 | BPL131 | REAL | %MF952 | BMC131INC01 Process Incomer MasterPact Total Apparent Power | 0 | 10000 | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC01.MasterPact | PF | BMC131INC01PR1DAT1_PF | BR4_Cluster1 | BPL131 | REAL | %MF954 | BMC131INC01 Process Incomer MasterPact Total Power Factor | 0 | 1 | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC01.MasterPact | VabTHD | BMC131INC01PR1DAT1_VabTHD | BR4_Cluster1 | BPL131 | REAL | %MF956 | BMC131INC01 Process Incomer MasterPact RMS Phase A to B Voltage Total Harmonic Distortion | 0 | 100 | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC01.MasterPact | VbcTHD | BMC131INC01PR1DAT1_VbcTHD | BR4_Cluster1 | BPL131 | REAL | %MF958 | BMC131INC01 Process Incomer MasterPact RMS Phase B to C Voltage Total Harmonic Distortion | 0 | 100 | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC01.MasterPact | VcaTHD | BMC131INC01PR1DAT1_VcaTHD | BR4_Cluster1 | BPL131 | REAL | %MF960 | BMC131INC01 Process Incomer MasterPact RMS Phase C to A Voltage Total Harmonic Distortion | 0 | 100 | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC01.MasterPact | VanTHD | BMC131INC01PR1DAT1_VanTHD | BR4_Cluster1 | BPL131 | REAL | %MF962 | BMC131INC01 Process Incomer MasterPact RMS Phase A Voltage Total Harmonic Distortion | 0 | 100 | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC01.MasterPact | VbnTHD | BMC131INC01PR1DAT1_VbnTHD | BR4_Cluster1 | BPL131 | REAL | %MF964 | BMC131INC01 Process Incomer MasterPact RMS Phase B Voltage Total Harmonic Distortion | 0 | 100 | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC01.MasterPact | VcnTHD | BMC131INC01PR1DAT1_VcnTHD | BR4_Cluster1 | BPL131 | REAL | %MF966 | BMC131INC01 Process Incomer MasterPact RMS Phase C Voltage Total Harmonic Distortion | 0 | 100 | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC01.MasterPact | IaTHD | BMC131INC01PR1DAT1_IaTHD | BR4_Cluster1 | BPL131 | REAL | %MF968 | BMC131INC01 Process Incomer MasterPact RMS Current on Phase A Total Harmonic Distortion | 0 | 100 | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC01.MasterPact | IbTHD | BMC131INC01PR1DAT1_IbTHD | BR4_Cluster1 | BPL131 | REAL | %MF970 | BMC131INC01 Process Incomer MasterPact RMS Current on Phase B Total Harmonic Distortion | 0 | 100 | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC01.MasterPact | IcTHD | BMC131INC01PR1DAT1_IcTHD | BR4_Cluster1 | BPL131 | REAL | %MF972 | BMC131INC01 Process Incomer MasterPact RMS Current on Phase C Total Harmonic Distortion | 0 | 100 | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC02.MasterPact | Frq | BMC131INC02PR1DAT1_Frq | BR4_Cluster1 | BPL131 | REAL | %MF991 | BMC131INC02 Process Incomer MasterPact Frequency | 0 | 70 | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC02.MasterPact | Ia | BMC131INC02PR1DAT1_Ia | BR4_Cluster1 | BPL131 | REAL | %MF994 | BMC131INC02 Process Incomer MasterPact RMS Current on Phase A | 0 | 1000 | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC02.MasterPact | Ib | BMC131INC02PR1DAT1_Ib | BR4_Cluster1 | BPL131 | REAL | %MF996 | BMC131INC02 Process Incomer MasterPact RMS Current on Phase B | 0 | 1000 | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC02.MasterPact | Ic | BMC131INC02PR1DAT1_Ic | BR4_Cluster1 | BPL131 | REAL | %MF998 | BMC131INC02 Process Incomer MasterPact RMS Current on Phase C | 0 | 1000 | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1101 |  | BPP1101PIC01_PV | BR4_Cluster1 | BPL131 | REAL | %MW1242 | BPP1101 Pressure Controller Process Variable |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1101 |  | BPP1101PIC01_SP | BR4_Cluster1 | BPL131 | REAL | %MW1244 | BPP1101 Pressure Controller Setpoint |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1103 |  | BPP1103LIC01_PV | BR4_Cluster1 | BPL131 | REAL | %MW1348 | West Turkeys Nest Level Controller Process Variable |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1103 |  | BPP1103LIC01_SP | BR4_Cluster1 | BPL131 | REAL | %MW1350 | West Turkeys Nest Level Controller Setpoint |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BSTD1106 |  | BSTD1106FIC01_PV | BR4_Cluster1 | BPL131 | REAL | %MW1596 | West Turkeys Nest LME Standpipe Flow Controller Process Variable |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BSTD1106 |  | BSTD1106FIC01_SP | BR4_Cluster1 | BPL131 | REAL | %MW1598 | West Turkeys Nest LME Standpipe Flow Controller Setpoint |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BSTD1107 |  | BSTD1107FIC01_PV | BR4_Cluster1 | BPL131 | REAL | %MW1622 | West Turkeys Nest HME Standpipe Flow Controller Process Variable |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BSTD1107 |  | BSTD1107FIC01_SP | BR4_Cluster1 | BPL131 | REAL | %MW1624 | West Turkeys Nest HME Standpipe Flow Controller Setpoint |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.BTY1502.FieldIO.FT01 |  | BTY1502FT01_PV | BR4_Cluster1 | BPL131 | REAL | %MW200 | West Turkeys Nest Flow Rate (m3/h) |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.BTY1502.FieldIO.FT03 |  | BTY1502FT03_PV | BR4_Cluster1 | BPL131 | REAL | %MW202 | West Turkeys Nest Flow Rate (m3/h) |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.BTY1502.FieldIO.PT01 |  | BTY1502PT01_PV | BR4_Cluster1 | BPL131 | REAL | %MW204 | West Turkeys Nest Pressure (kPa) |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.BTY1502.FieldIO.PT03 |  | BTY1502PT03_PV | BR4_Cluster1 | BPL131 | REAL | %MW206 | West Turkeys Nest Pressure (kPa) |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BSTD1106.FieldIO.FT03 |  | BSTD1106FT03_PV | BR4_Cluster1 | BPL131 | REAL | %MW208 | West Turkeys Nest LME Standpipe Flow Rate (m3/h) |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BSTD1107 |  | BSTD1107FT02_PV | BR4_Cluster1 | BPL131 | REAL | %MW210 | BSTD1107FT02 Flow Rate (m3/h) |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BSTD1106.FV03.FieldIO.ZT01 |  | BSTD1106FV03ZT01_PV | BR4_Cluster1 | BPL131 | REAL | %MW212 | West Turkeys Nest LME Standpipe Flow Valve Position (%) |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BSTD1107.FV02.FieldIO.ZT01 |  | BSTD1107FV02ZT01_PV | BR4_Cluster1 | BPL131 | REAL | %MW214 | West Turkeys Nest HME Standpipe Flow Valve Position (%) |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BPP1106.FieldIO.PT01 |  | BPP1106PT01_PV | BR4_Cluster1 | BPL131 | REAL | %MW216 | HME & LME Standpipe Pump 3 Pressure (kPa) |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BPP1107.FieldIO.PT02 |  | BPP1107PT02_PV | BR4_Cluster1 | BPL131 | REAL | %MW218 | HME & LME Standpipe Pump 4 Pressure (kPa) |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1101.FieldIO.PT03 |  | BPP1101PT03_PV | BR4_Cluster1 | BPL131 | REAL | %MW220 | Production Plant and NPI Water Supply Pump 1 Discharge Pressure (kPa) |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1102.FieldIO.PT04 |  | BPP1102PT04_PV | BR4_Cluster1 | BPL131 | REAL | %MW222 | Production Plant and NPI Water Supply Pump 2 Discharge Pressure (kPa) |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1101.FieldIO.FT01 |  | BPP1101FT01_PV | BR4_Cluster1 | BPL131 | REAL | %MW224 | Production Plant and NPI Water Supply Pump 1 Flow Rate (m3/h) |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.BTY1502.FieldIO.FT02 |  | BTY1502FT02_PV | BR4_Cluster1 | BPL131 | REAL | %MW226 | West Turkeys Nest Flow Rate (m3/h) |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.BTY1502.FV01.FieldIO.ZT01 |  | BTY1502FV01ZT01_PV | BR4_Cluster1 | BPL131 | REAL | %MW228 | West Turkeys Nest Flow Valve Position (%) |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1101.FieldIO.PT10 |  | BPP1101PT10_PV | BR4_Cluster1 | BPL131 | REAL | %MW230 | Production Plant and NPI Water Supply Pump 1 Discharge Pressure 1 (kPa) |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1101.FieldIO.PT11 |  | BPP1101PT11_PV | BR4_Cluster1 | BPL131 | REAL | %MW232 | Production Plant and NPI Water Supply Pump 1 Discharge Pressure 2 (kPa) |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1103.FieldIO.FT03 |  | BPP1103FT03_PV | BR4_Cluster1 | BPL131 | REAL | %MW234 | Water Transfer Pump 1 Flow Rate (m3/h) |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1103.FieldIO.PT05 |  | BPP1103PT05_PV | BR4_Cluster1 | BPL131 | REAL | %MW236 | Water Transfer Pump 1 Discharge Pressure (kPa) |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1104.FieldIO.FT04 |  | BPP1104FT04_PV | BR4_Cluster1 | BPL131 | REAL | %MW238 | Water Transfer Pump 2 Flow Rate (m3/h) |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1104.FieldIO.PT06 |  | BPP1104PT06_PV | BR4_Cluster1 | BPL131 | REAL | %MW240 | Water Transfer Pump 2 Discharge Pressure (kPa) |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1105.FieldIO.FT05 |  | BPP1105FT05_PV | BR4_Cluster1 | BPL131 | REAL | %MW242 | Water Transfer Pump 3 Flow Rate (m3/h) |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1105.FieldIO.PT07 |  | BPP1105PT07_PV | BR4_Cluster1 | BPL131 | REAL | %MW244 | Water Transfer Pump 3 Discharge Pressure (kPa) |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1103.FieldIO.FT06 |  | BPP1103FT06_PV | BR4_Cluster1 | BPL131 | REAL | %MW246 | Water Transfer Pump 1 Flow Rate (m3/h) |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1103.FieldIO.PT08 |  | BPP1103PT08_PV | BR4_Cluster1 | BPL131 | REAL | %MW248 | Water Transfer Pump 1 Discharge Pressure (kPa) |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.BTY1502.FieldIO.LT01 |  | BTY1502LT01_PV | BR4_Cluster1 | BPL131 | REAL | %MW250 | West Turkeys Nest Level 1 (mm) |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.BTY1502.FieldIO.LT02 |  | BTY1502LT02_PV | BR4_Cluster1 | BPL131 | REAL | %MW252 | West Turkeys Nest Level 2 (mm) |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.P3FIREWATER.BTK2101.FieldIO.LT01 |  | BTK2101LT01_PV | BR4_Cluster1 | BPL131 | REAL | %MW254 | NPI Fire Water Tank 1 Tank Level (%) |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.P3FIREWATER.BTK2102.FieldIO.LT01 |  | BTK2102LT01_PV | BR4_Cluster1 | BPL131 | REAL | %MW256 | NPI Fire Water Tank 2 Tank Level (%) |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1101.FieldIO.FT01 |  | BPP1101FT02_PV | BR4_Cluster1 | BPL131 | REAL | %MW260 | Production Plant and NPI Water Supply Pump 1 Flow Rate (m3/h) |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.BC02.Cordex | SysV | BSR131BC02CordexDAT1_SysV | BR4_Cluster1 | BPL131 | REAL | %MW4404 | BSR131BC02 Battery Charger Cordex System Voltage | 0 | 1000 | BS1_Tags
BR4.SRV.PWR.BSR131.BC02.Cordex | TotLdI | BSR131BC02CordexDAT1_TotLdI | BR4_Cluster1 | BPL131 | REAL | %MW4408 | BSR131BC02 Battery Charger Cordex Total Load Current | 0 | 1000 | BS1_Tags
BR4.SRV.PWR.BSR131.BC02.Cordex | BatV | BSR131BC02CordexDAT1_BatV | BR4_Cluster1 | BPL131 | REAL | %MW4412 | BSR131BC02 Battery Charger Cordex Battery Voltage | 0 | 1000 | BS1_Tags
BR4.SRV.PWR.BSR131.BC02.Cordex | BatI | BSR131BC02CordexDAT1_BatI | BR4_Cluster1 | BPL131 | REAL | %MW4414 | BSR131BC02 Battery Charger Cordex Battery Current | 0 | 1000 | BS1_Tags
BR4.SRV.PWR.BSR131.BC02.Cordex | TotRecOPI | BSR131BC02CordexDAT1_TotRecOPI | BR4_Cluster1 | BPL131 | REAL | %MW4416 | BSR131BC02 Battery Charger Cordex Total Rectifier O/P Current | 0 | 1000 | BS1_Tags
BR4.SRV.PWR.BSR131.BC02.Cordex | TotOPPwr | BSR131BC02CordexDAT1_TotOPPwr | BR4_Cluster1 | BPL131 | REAL | %MW4418 | BSR131BC02 Battery Charger Cordex Total Output Power | 0 | 1000 | BS1_Tags
BR4.SRV.PWR.BSR131.BC02.Cordex | TotCap1 | BSR131BC02CordexDAT1_TotCap1 | BR4_Cluster1 | BPL131 | REAL | %MW4420 | BSR131BC02 Battery Charger Cordex Total Capacity Installed | 0 | 1000 | BS1_Tags
BR4.SRV.PWR.BSR131.BC02.Cordex | TotCap2 | BSR131BC02CordexDAT1_TotCap2 | BR4_Cluster1 | BPL131 | REAL | %MW4422 | BSR131BC02 Battery Charger Cordex Total Capacity Installed | 0 | 1000 | BS1_Tags
BR4.SRV.PWR.BSR131.BC02.Cordex | CapRemn1 | BSR131BC02CordexDAT1_CapRemn1 | BR4_Cluster1 | BPL131 | REAL | %MW4424 | BSR131BC02 Battery Charger Cordex Estimated Capacity Remaining | 0 | 1000 | BS1_Tags
BR4.SRV.PWR.BSR131.BC02.Cordex | CapRemn2 | BSR131BC02CordexDAT1_CapRemn2 | BR4_Cluster1 | BPL131 | REAL | %MW4426 | BSR131BC02 Battery Charger Cordex Estimated Capacity Remaining | 0 | 1000 | BS1_Tags
BR4.SRV.PWR.BSR131.BC02.Cordex | AvgDCOPV | BSR131BC02CordexDAT1_AvgDCOPV | BR4_Cluster1 | BPL131 | REAL | %MW4428 | BSR131BC02 Battery Charger Cordex Average DC Bus Output Voltage | 0 | 1000 | BS1_Tags
BR4.SRV.PWR.BSR131.BC02.Cordex | Phs1V | BSR131BC02CordexDAT1_Phs1V | BR4_Cluster1 | BPL131 | REAL | %MW4430 | BSR131BC02 Battery Charger Cordex Estimated AC Phase 1 Voltage | 0 | 1000 | BS1_Tags
BR4.SRV.PWR.BSR131.BC02.Cordex | Phs2V | BSR131BC02CordexDAT1_Phs2V | BR4_Cluster1 | BPL131 | REAL | %MW4432 | BSR131BC02 Battery Charger Cordex Estimated AC Phase 2 Voltage | 0 | 1000 | BS1_Tags
BR4.SRV.PWR.BSR131.BC02.Cordex | Phs3V | BSR131BC02CordexDAT1_Phs3V | BR4_Cluster1 | BPL131 | REAL | %MW4434 | BSR131BC02 Battery Charger Cordex Estimated AC Phase 3 Voltage | 0 | 1000 | BS1_Tags
BR4.SRV.PWR.BSR131.BC02.Cordex | CapRqd | BSR131BC02CordexDAT1_CapRqd | BR4_Cluster1 | BPL131 | REAL | %MW4436 | BSR131BC02 Battery Charger Cordex Estimated Required Capacity | 0 | 100 | BS1_Tags
BR4.SRV.PWR.BSR131.BC02.Cordex | CapAvl | BSR131BC02CordexDAT1_CapAvl | BR4_Cluster1 | BPL131 | REAL | %MW4438 | BSR131BC02 Battery Charger Cordex Estimated Available Capacity | 0 | 100 | BS1_Tags
BR4.SRV.PWR.BSR131.BC02.Cordex | RedunCap | BSR131BC02CordexDAT1_RedunCap | BR4_Cluster1 | BPL131 | REAL | %MW4440 | BSR131BC02 Battery Charger Cordex Estimated Redundant Capacity | 0 | 100 | BS1_Tags
BR4.SRV.PWR.BSR131.BC02.Cordex | SbyCap | BSR131BC02CordexDAT1_SbyCap | BR4_Cluster1 | BPL131 | REAL | %MW4442 | BSR131BC02 Battery Charger Cordex Estimated Standby Capacity | 0 | 100 | BS1_Tags
BR4.SRV.PWR.BSR131.BC02.Cordex | BatTmp | BSR131BC02CordexDAT1_BatTmp | BR4_Cluster1 | BPL131 | REAL | %MW4466 | BSR131BC02 Battery Charger Cordex Battery Temperature | 0 | 100 | BS1_Tags
BR4.SRV.PWR.BSR131.BC02.Cordex | StgCharge | BSR131BC02CordexDAT1_StgCharge | BR4_Cluster1 | BPL131 | REAL | %MW4468 | BSR131BC02 Battery Charger Cordex Estimated State of Charge | 0 | 100 | BS1_Tags
BR4.SRV.PWR.BSR131.BC02.Cordex | BatRunTm | BSR131BC02CordexDAT1_BatRunTm | BR4_Cluster1 | BPL131 | REAL | %MW4470 | BSR131BC02 Battery Charger Cordex Estimated Battery Runtime | 0 | 10000 | BS1_Tags
BR4.SRV.PWR.BSR131.BC02.Cordex | MaxRecAmbTmp | BSR131BC02CordexDAT1_MaxRecAmbTmp | BR4_Cluster1 | BPL131 | REAL | %MW4478 | BSR131BC02 Battery Charger Cordex Maximum Rectifier Ambient Temperature | 0 | 100 | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1101.VS01 | Iavg | BPP1101VS01DAT1_Iavg | BR4_Cluster1 | BPL131 | REAL | %MW6002 | BPP1101VS01 VVVF Average Current (A) |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1101.VS01 | Spd | BPP1101VS01DAT1_Spd | BR4_Cluster1 | BPL131 | REAL | %MW6004 | BPP1101VS01 VVVF Speed (%) |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1101.VS01 | Trq | BPP1101VS01DAT1_Trq | BR4_Cluster1 | BPL131 | REAL | %MW6006 | BPP1101VS01 VVVF Torque (%) |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1101.VS01 | Frq | BPP1101VS01DAT1_Frq | BR4_Cluster1 | BPL131 | REAL | %MW6008 | BPP1101VS01 VVVF Frequency (Hz) |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1101.VS01 | Pwr | BPP1101VS01DAT1_Pwr | BR4_Cluster1 | BPL131 | REAL | %MW6010 | BPP1101VS01 VVVF Power (kW) |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1101.VS01 | Tmp | BPP1101VS01DAT1_Tmp | BR4_Cluster1 | BPL131 | REAL | %MW6012 | BPP1101VS01 VVVF Temperature (degC) |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1101.VS01 | SpdEng | BPP1101VS01DAT1_SpdEng | BR4_Cluster1 | BPL131 | REAL | %MW6014 | BPP1101VS01 VVVF Speed (rpm) |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1102.VS01 | Iavg | BPP1102VS01DAT1_Iavg | BR4_Cluster1 | BPL131 | REAL | %MW6102 | BPP1102VS01 VVVF Average Current (A) |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1102.VS01 | Spd | BPP1102VS01DAT1_Spd | BR4_Cluster1 | BPL131 | REAL | %MW6104 | BPP1102VS01 VVVF Speed (%) |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1102.VS01 | Trq | BPP1102VS01DAT1_Trq | BR4_Cluster1 | BPL131 | REAL | %MW6106 | BPP1102VS01 VVVF Torque (%) |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1102.VS01 | Frq | BPP1102VS01DAT1_Frq | BR4_Cluster1 | BPL131 | REAL | %MW6108 | BPP1102VS01 VVVF Frequency (Hz) |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1102.VS01 | Pwr | BPP1102VS01DAT1_Pwr | BR4_Cluster1 | BPL131 | REAL | %MW6110 | BPP1102VS01 VVVF Power (kW) |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1102.VS01 | Tmp | BPP1102VS01DAT1_Tmp | BR4_Cluster1 | BPL131 | REAL | %MW6112 | BPP1102VS01 VVVF Temperature (degC) |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1102.VS01 | SpdEng | BPP1102VS01DAT1_SpdEng | BR4_Cluster1 | BPL131 | REAL | %MW6114 | BPP1102VS01 VVVF Speed (rpm) |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1103.VS01 | Iavg | BPP1103VS01DAT1_Iavg | BR4_Cluster1 | BPL131 | REAL | %MW6202 | BPP1103VS01 VVVF Average Current (A) |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1103.VS01 | Spd | BPP1103VS01DAT1_Spd | BR4_Cluster1 | BPL131 | REAL | %MW6204 | BPP1103VS01 VVVF Speed (%) |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1103.VS01 | Trq | BPP1103VS01DAT1_Trq | BR4_Cluster1 | BPL131 | REAL | %MW6206 | BPP1103VS01 VVVF Torque (%) |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1103.VS01 | Frq | BPP1103VS01DAT1_Frq | BR4_Cluster1 | BPL131 | REAL | %MW6208 | BPP1103VS01 VVVF Frequency (Hz) |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1103.VS01 | Pwr | BPP1103VS01DAT1_Pwr | BR4_Cluster1 | BPL131 | REAL | %MW6210 | BPP1103VS01 VVVF Power (kW) |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1103.VS01 | Tmp | BPP1103VS01DAT1_Tmp | BR4_Cluster1 | BPL131 | REAL | %MW6212 | BPP1103VS01 VVVF Temperature (degC) |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1103.VS01 | SpdEng | BPP1103VS01DAT1_SpdEng | BR4_Cluster1 | BPL131 | REAL | %MW6214 | BPP1103VS01 VVVF Speed (rpm) |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1104.VS01 | Iavg | BPP1104VS01DAT1_Iavg | BR4_Cluster1 | BPL131 | REAL | %MW6302 | BPP1104VS01 VVVF Average Current (A) |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1104.VS01 | Spd | BPP1104VS01DAT1_Spd | BR4_Cluster1 | BPL131 | REAL | %MW6304 | BPP1104VS01 VVVF Speed (%) |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1104.VS01 | Trq | BPP1104VS01DAT1_Trq | BR4_Cluster1 | BPL131 | REAL | %MW6306 | BPP1104VS01 VVVF Torque (%) |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1104.VS01 | Frq | BPP1104VS01DAT1_Frq | BR4_Cluster1 | BPL131 | REAL | %MW6308 | BPP1104VS01 VVVF Frequency (Hz) |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1104.VS01 | Pwr | BPP1104VS01DAT1_Pwr | BR4_Cluster1 | BPL131 | REAL | %MW6310 | BPP1104VS01 VVVF Power (kW) |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1104.VS01 | Tmp | BPP1104VS01DAT1_Tmp | BR4_Cluster1 | BPL131 | REAL | %MW6312 | BPP1104VS01 VVVF Temperature (degC) |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1104.VS01 | SpdEng | BPP1104VS01DAT1_SpdEng | BR4_Cluster1 | BPL131 | REAL | %MW6314 | BPP1104VS01 VVVF Speed (rpm) |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1105.VS01 | Iavg | BPP1105VS01DAT1_Iavg | BR4_Cluster1 | BPL131 | REAL | %MW6402 | BPP1105VS01 VVVF Average Current (A) |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1105.VS01 | Spd | BPP1105VS01DAT1_Spd | BR4_Cluster1 | BPL131 | REAL | %MW6404 | BPP1105VS01 VVVF Speed (%) |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1105.VS01 | Trq | BPP1105VS01DAT1_Trq | BR4_Cluster1 | BPL131 | REAL | %MW6406 | BPP1105VS01 VVVF Torque (%) |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1105.VS01 | Frq | BPP1105VS01DAT1_Frq | BR4_Cluster1 | BPL131 | REAL | %MW6408 | BPP1105VS01 VVVF Frequency (Hz) |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1105.VS01 | Pwr | BPP1105VS01DAT1_Pwr | BR4_Cluster1 | BPL131 | REAL | %MW6410 | BPP1105VS01 VVVF Power (kW) |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1105.VS01 | Tmp | BPP1105VS01DAT1_Tmp | BR4_Cluster1 | BPL131 | REAL | %MW6412 | BPP1105VS01 VVVF Temperature (degC) |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1105.VS01 | SpdEng | BPP1105VS01DAT1_SpdEng | BR4_Cluster1 | BPL131 | REAL | %MW6414 | BPP1105VS01 VVVF Speed (rpm) |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1106.VS01 | Iavg | BPP1106VS01DAT1_Iavg | BR4_Cluster1 | BPL131 | REAL | %MW6502 | BPP1106VS01 VVVF Average Current (A) |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1106.VS01 | Spd | BPP1106VS01DAT1_Spd | BR4_Cluster1 | BPL131 | REAL | %MW6504 | BPP1106VS01 VVVF Speed (%) |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1106.VS01 | Trq | BPP1106VS01DAT1_Trq | BR4_Cluster1 | BPL131 | REAL | %MW6506 | BPP1106VS01 VVVF Torque (%) |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1106.VS01 | Frq | BPP1106VS01DAT1_Frq | BR4_Cluster1 | BPL131 | REAL | %MW6508 | BPP1106VS01 VVVF Frequency (Hz) |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1106.VS01 | Pwr | BPP1106VS01DAT1_Pwr | BR4_Cluster1 | BPL131 | REAL | %MW6510 | BPP1106VS01 VVVF Power (kW) |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1106.VS01 | Tmp | BPP1106VS01DAT1_Tmp | BR4_Cluster1 | BPL131 | REAL | %MW6512 | BPP1106VS01 VVVF Temperature (degC) |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1106.VS01 | SpdEng | BPP1106VS01DAT1_SpdEng | BR4_Cluster1 | BPL131 | REAL | %MW6514 | BPP1106VS01 VVVF Speed (rpm) |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1107.VS01 | Iavg | BPP1107VS01DAT1_Iavg | BR4_Cluster1 | BPL131 | REAL | %MW6602 | BPP1107VS01 VVVF Average Current (A) |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1107.VS01 | Spd | BPP1107VS01DAT1_Spd | BR4_Cluster1 | BPL131 | REAL | %MW6604 | BPP1107VS01 VVVF Speed (%) |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1107.VS01 | Trq | BPP1107VS01DAT1_Trq | BR4_Cluster1 | BPL131 | REAL | %MW6606 | BPP1107VS01 VVVF Torque (%) |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1107.VS01 | Frq | BPP1107VS01DAT1_Frq | BR4_Cluster1 | BPL131 | REAL | %MW6608 | BPP1107VS01 VVVF Frequency (Hz) |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1107.VS01 | Pwr | BPP1107VS01DAT1_Pwr | BR4_Cluster1 | BPL131 | REAL | %MW6610 | BPP1107VS01 VVVF Power (kW) |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1107.VS01 | Tmp | BPP1107VS01DAT1_Tmp | BR4_Cluster1 | BPL131 | REAL | %MW6612 | BPP1107VS01 VVVF Temperature (degC) |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1107.VS01 | SpdEng | BPP1107VS01DAT1_SpdEng | BR4_Cluster1 | BPL131 | REAL | %MW6614 | BPP1107VS01 VVVF Speed (rpm) |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1101 |  | BPP1101PIC01_KD | BR4_Cluster1 | BPL131 | REAL | %MW7008 | BPP1101 Pressure Controller Derivative Gain |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1101 |  | BPP1101PIC01_KI | BR4_Cluster1 | BPL131 | REAL | %MW7010 | BPP1101 Pressure Controller Integral Gain |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1101 |  | BPP1101PIC01_KP | BR4_Cluster1 | BPL131 | REAL | %MW7012 | BPP1101 Pressure Controller Proportional Gain |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1101 |  | BPP1101PIC01_OP | BR4_Cluster1 | BPL131 | REAL | %MW7014 | BPP1101 Pressure Controller Output Value |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1101 |  | BPP1101PIC01_OPMan | BR4_Cluster1 | BPL131 | REAL | %MW7016 | BPP1101 Pressure Controller Manual Setpoint |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1103 |  | BPP1103LIC01_KD | BR4_Cluster1 | BPL131 | REAL | %MW7032 | West Turkeys Nest Level Controller Derivative Gain |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1103 |  | BPP1103LIC01_KI | BR4_Cluster1 | BPL131 | REAL | %MW7034 | West Turkeys Nest Level Controller Integral Gain |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1103 |  | BPP1103LIC01_KP | BR4_Cluster1 | BPL131 | REAL | %MW7036 | West Turkeys Nest Level Controller Proportional Gain |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1103 |  | BPP1103LIC01_OP | BR4_Cluster1 | BPL131 | REAL | %MW7038 | West Turkeys Nest Level Controller Output Value |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1103 |  | BPP1103LIC01_OPMan | BR4_Cluster1 | BPL131 | REAL | %MW7040 | West Turkeys Nest Level Controller Manual Setpoint |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BSTD1106 |  | BSTD1106FIC01_KD | BR4_Cluster1 | BPL131 | REAL | %MW7068 | West Turkeys Nest LME Standpipe Flow Controller Derivative Gain |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BSTD1106 |  | BSTD1106FIC01_KI | BR4_Cluster1 | BPL131 | REAL | %MW7070 | West Turkeys Nest LME Standpipe Flow Controller Integral Gain |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BSTD1106 |  | BSTD1106FIC01_KP | BR4_Cluster1 | BPL131 | REAL | %MW7072 | West Turkeys Nest LME Standpipe Flow Controller Proportional Gain |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BSTD1106 |  | BSTD1106FIC01_OP | BR4_Cluster1 | BPL131 | REAL | %MW7074 | West Turkeys Nest LME Standpipe Flow Controller Output Value |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BSTD1106 |  | BSTD1106FIC01_OPMan | BR4_Cluster1 | BPL131 | REAL | %MW7076 | West Turkeys Nest LME Standpipe Flow Controller Manual Setpoint |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BSTD1107 |  | BSTD1107FIC01_KD | BR4_Cluster1 | BPL131 | REAL | %MW7080 | West Turkeys Nest HME Standpipe Flow Controller Derivative Gain |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BSTD1107 |  | BSTD1107FIC01_KI | BR4_Cluster1 | BPL131 | REAL | %MW7082 | West Turkeys Nest HME Standpipe Flow Controller Integral Gain |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BSTD1107 |  | BSTD1107FIC01_KP | BR4_Cluster1 | BPL131 | REAL | %MW7084 | West Turkeys Nest HME Standpipe Flow Controller Proportional Gain |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BSTD1107 |  | BSTD1107FIC01_OP | BR4_Cluster1 | BPL131 | REAL | %MW7086 | West Turkeys Nest HME Standpipe Flow Controller Output Value |  |  | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BSTD1107 |  | BSTD1107FIC01_OPMan | BR4_Cluster1 | BPL131 | REAL | %MW7088 | West Turkeys Nest HME Standpipe Flow Controller Manual Setpoint |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.BC02.BACS | AlmID1 | BSR131BC02BACSDAT1_AlmID1 | BR4_Cluster1 | BPL131 | UINT | %MW4000 | BSR131BC02 Battery Charger BACS Alarm ID 1 |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.BC02.BACS | AlmID2 | BSR131BC02BACSDAT1_AlmID2 | BR4_Cluster1 | BPL131 | UINT | %MW4001 | BSR131BC02 Battery Charger BACS Alarm ID 2 |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.BC02.BACS | AlmID3 | BSR131BC02BACSDAT1_AlmID3 | BR4_Cluster1 | BPL131 | UINT | %MW4002 | BSR131BC02 Battery Charger BACS Alarm ID 3 |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.BC02.BACS | NumStr | BSR131BC02BACSDAT1_NumStr | BR4_Cluster1 | BPL131 | UINT | %MW4003 | BSR131BC02 Battery Charger BACS Number of BACS Strings | 0 | 1 | BS1_Tags
BR4.SRV.PWR.BSR131.BC02.BACS | NumMod | BSR131BC02BACSDAT1_NumMod | BR4_Cluster1 | BPL131 | UINT | %MW4004 | BSR131BC02 Battery Charger BACS Number of BACS Modules | 0 | 9 | BS1_Tags
BR4.SRV.PWR.BSR131.BC02.BACS | Mod1AlmID | BSR131BC02BACSDAT1_Mod1AlmID | BR4_Cluster1 | BPL131 | UINT | %MW4012 | BSR131BC02 Battery Charger BACS Module 1 Alarm ID |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.BC02.BACS | Mod2AlmID | BSR131BC02BACSDAT1_Mod2AlmID | BR4_Cluster1 | BPL131 | UINT | %MW4017 | BSR131BC02 Battery Charger BACS Module 2 Alarm ID |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.BC02.BACS | Mod3AlmID | BSR131BC02BACSDAT1_Mod3AlmID | BR4_Cluster1 | BPL131 | UINT | %MW4022 | BSR131BC02 Battery Charger BACS Module 3 Alarm ID |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.BC02.BACS | Mod4AlmID | BSR131BC02BACSDAT1_Mod4AlmID | BR4_Cluster1 | BPL131 | UINT | %MW4027 | BSR131BC02 Battery Charger BACS Module 4 Alarm ID |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.BC02.BACS | Mod5AlmID | BSR131BC02BACSDAT1_Mod5AlmID | BR4_Cluster1 | BPL131 | UINT | %MW4032 | BSR131BC02 Battery Charger BACS Module 5 Alarm ID |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.BC02.BACS | Mod6AlmID | BSR131BC02BACSDAT1_Mod6AlmID | BR4_Cluster1 | BPL131 | UINT | %MW4037 | BSR131BC02 Battery Charger BACS Module 6 Alarm ID |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.BC02.BACS | Mod7AlmID | BSR131BC02BACSDAT1_Mod7AlmID | BR4_Cluster1 | BPL131 | UINT | %MW4042 | BSR131BC02 Battery Charger BACS Module 7 Alarm ID |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.BC02.BACS | Mod8AlmID | BSR131BC02BACSDAT1_Mod8AlmID | BR4_Cluster1 | BPL131 | UINT | %MW4047 | BSR131BC02 Battery Charger BACS Module 8 Alarm ID |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.BC02.BACS | Mod9AlmID | BSR131BC02BACSDAT1_Mod9AlmID | BR4_Cluster1 | BPL131 | UINT | %MW4052 | BSR131BC02 Battery Charger BACS Module 9 Alarm ID |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.UPScale | StsID | BSR131UP01DAT1_StsID | BR4_Cluster1 | BPL131 | UINT | %MW4200 | BSR131UP01 UPS Status ID |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.UPScale | OPPhs1Pwr | BSR131UP01DAT1_OPPhs1Pwr | BR4_Cluster1 | BPL131 | UINT | %MW4203 | BSR131UP01 UPS Output Power Phase 1 (%) | 0 | 100 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.UPScale | OPPhs2Pwr | BSR131UP01DAT1_OPPhs2Pwr | BR4_Cluster1 | BPL131 | UINT | %MW4204 | BSR131UP01 UPS Output Power Phase 2 (%) | 0 | 100 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.UPScale | OPPhs3Pwr | BSR131UP01DAT1_OPPhs3Pwr | BR4_Cluster1 | BPL131 | UINT | %MW4205 | BSR131UP01 UPS Output Power Phase 3 (%) | 0 | 100 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.UPScale | BatCap | BSR131UP01DAT1_BatCap | BR4_Cluster1 | BPL131 | UINT | %MW4206 | BSR131UP01 UPS Battery Capacity (%) | 0 | 100 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.UPScale | InFrqPhs1 | BSR131UP01DAT1_InFrqPhs1 | BR4_Cluster1 | BPL131 | UINT | %MW4213 | BSR131UP01 UPS Input Frequency Phase 1 (Hz) | 0 | 100 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.UPScale | InFrqPhs2 | BSR131UP01DAT1_InFrqPhs2 | BR4_Cluster1 | BPL131 | UINT | %MW4214 | BSR131UP01 UPS Input Frequency Phase 2 (Hz) | 0 | 100 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.UPScale | InFrqPhs3 | BSR131UP01DAT1_InFrqPhs3 | BR4_Cluster1 | BPL131 | UINT | %MW4215 | BSR131UP01 UPS Input Frequency Phase 3 (Hz) | 0 | 100 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.UPScale | PwrFltCnt | BSR131UP01DAT1_PwrFltCnt | BR4_Cluster1 | BPL131 | UINT | %MW4216 | BSR131UP01 UPS Power Fail Counter |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.UPScale | ManBypCls | BSR131UP01DAT1_ManBypCls | BR4_Cluster1 | BPL131 | UINT | %MW4217 | BSR131UP01 UPS Manual Bypass Switch Closed |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.UPScale | OPVPhs1 | BSR131UP01DAT1_OPVPhs1 | BR4_Cluster1 | BPL131 | UINT | %MW4218 | BSR131UP01 UPS Output Voltage Phase 1 (V) | 0 | 1000 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.UPScale | OPVPhs2 | BSR131UP01DAT1_OPVPhs2 | BR4_Cluster1 | BPL131 | UINT | %MW4219 | BSR131UP01 UPS Output Voltage Phase 2 (V) | 0 | 1000 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.UPScale | OPVPhs3 | BSR131UP01DAT1_OPVPhs3 | BR4_Cluster1 | BPL131 | UINT | %MW4220 | BSR131UP01 UPS Output Voltage Phase 3 (V) | 0 | 1000 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.UPScale | OPIPhs1 | BSR131UP01DAT1_OPIPhs1 | BR4_Cluster1 | BPL131 | UINT | %MW4221 | BSR131UP01 UPS Output Current Phase 1 (A) | 0 | 1000 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.UPScale | OPIPhs2 | BSR131UP01DAT1_OPIPhs2 | BR4_Cluster1 | BPL131 | UINT | %MW4222 | BSR131UP01 UPS Output Current Phase 2 (A) | 0 | 1000 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.UPScale | OPIPhs3 | BSR131UP01DAT1_OPIPhs3 | BR4_Cluster1 | BPL131 | UINT | %MW4223 | BSR131UP01 UPS Output Current Phase 3 (A) | 0 | 1000 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.UPScale | TrueOPPwrPhs1 | BSR131UP01DAT1_TrueOPPwrPhs1 | BR4_Cluster1 | BPL131 | UINT | %MW4224 | BSR131UP01 UPS True Output Power Phase 1 (kW) | 0 | 100 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.UPScale | TrueOPPwrPhs2 | BSR131UP01DAT1_TrueOPPwrPhs2 | BR4_Cluster1 | BPL131 | UINT | %MW4225 | BSR131UP01 UPS True Output Power Phase 2 (kW) | 0 | 100 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.UPScale | TrueOPPwrPhs3 | BSR131UP01DAT1_TrueOPPwrPhs3 | BR4_Cluster1 | BPL131 | UINT | %MW4226 | BSR131UP01 UPS True Output Power Phase 3 (kW) | 0 | 100 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.UPScale | BatI | BSR131UP01DAT1_BatI | BR4_Cluster1 | BPL131 | UINT | %MW4227 | BSR131UP01 UPS Battery Current (A) | 0 | 1000 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.UPScale | OFFrq | BSR131UP01DAT1_OFFrq | BR4_Cluster1 | BPL131 | UINT | %MW4228 | BSR131UP01 UPS Output Frequency (Hz) | 0 | 100 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.UPScale | BypFrq | BSR131UP01DAT1_BypFrq | BR4_Cluster1 | BPL131 | UINT | %MW4229 | BSR131UP01 UPS Bypass Frequency (Hz) | 0 | 100 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.UPScale | BypVPhs1 | BSR131UP01DAT1_BypVPhs1 | BR4_Cluster1 | BPL131 | UINT | %MW4230 | BSR131UP01 UPS Bypass Voltage Phase 1 (V) | 0 | 1000 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.UPScale | BypVPhs2 | BSR131UP01DAT1_BypVPhs2 | BR4_Cluster1 | BPL131 | UINT | %MW4231 | BSR131UP01 UPS Bypass Voltage Phase 2 (V) | 0 | 1000 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.UPScale | BypVPhs3 | BSR131UP01DAT1_BypVPhs3 | BR4_Cluster1 | BPL131 | UINT | %MW4232 | BSR131UP01 UPS Bypass Voltage Phase 3 (V) | 0 | 1000 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.UPScale | BatCnd | BSR131UP01DAT1_BatCnd | BR4_Cluster1 | BPL131 | UINT | %MW4233 | BSR131UP01 UPS Battery Condition (0 = good, 1 = weak, 2 = replace) | 0 | 3 | BS1_Tags
BR4.SRV.PWR.BSR131.BC02.Cordex | AlmID1 | BSR131BC02CordexDAT1_AlmID1 | BR4_Cluster1 | BPL131 | UINT | %MW4400 | BSR131BC02 Battery Charger Cordex Alarm ID 1 |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.BC02.Cordex | AlmID2 | BSR131BC02CordexDAT1_AlmID2 | BR4_Cluster1 | BPL131 | UINT | %MW4401 | BSR131BC02 Battery Charger Cordex Alarm ID 2 |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.BC02.Cordex | AlmID3 | BSR131BC02CordexDAT1_AlmID3 | BR4_Cluster1 | BPL131 | UINT | %MW4402 | BSR131BC02 Battery Charger Cordex Alarm ID 3 |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | AlmID1 | BSR131UP01BACSDAT1_AlmID1 | BR4_Cluster1 | BPL131 | UINT | %MW5000 | BSR131UP01 UPS BACS Alarm ID 1 |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | AlmID2 | BSR131UP01BACSDAT1_AlmID2 | BR4_Cluster1 | BPL131 | UINT | %MW5001 | BSR131UP01 UPS BACS Alarm ID 2 |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | AlmID3 | BSR131UP01BACSDAT1_AlmID3 | BR4_Cluster1 | BPL131 | UINT | %MW5002 | BSR131UP01 UPS BACS Alarm ID 3 |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | NumStr | BSR131UP01BACSDAT1_NumStr | BR4_Cluster1 | BPL131 | UINT | %MW5003 | BSR131UP01 UPS BACS Number of BACS Strings | 0 | 1 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | NumMod | BSR131UP01BACSDAT1_NumMod | BR4_Cluster1 | BPL131 | UINT | %MW5004 | BSR131UP01 UPS BACS Number of BACS String 1 Modules | 0 | 9 | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod1AlmID | BSR131UP01BACSDAT1_Str1Mod1AlmID | BR4_Cluster1 | BPL131 | UINT | %MW5012 | BSR131UP01 UPS BACS String 1 Module 1 Alarm ID |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod2AlmID | BSR131UP01BACSDAT1_Str1Mod2AlmID | BR4_Cluster1 | BPL131 | UINT | %MW5017 | BSR131UP01 UPS BACS String 1 Module 2 Alarm ID |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod3AlmID | BSR131UP01BACSDAT1_Str1Mod3AlmID | BR4_Cluster1 | BPL131 | UINT | %MW5022 | BSR131UP01 UPS BACS String 1 Module 3 Alarm ID |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod4AlmID | BSR131UP01BACSDAT1_Str1Mod4AlmID | BR4_Cluster1 | BPL131 | UINT | %MW5027 | BSR131UP01 UPS BACS String 1 Module 4 Alarm ID |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod5AlmID | BSR131UP01BACSDAT1_Str1Mod5AlmID | BR4_Cluster1 | BPL131 | UINT | %MW5032 | BSR131UP01 UPS BACS String 1 Module 5 Alarm ID |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod6AlmID | BSR131UP01BACSDAT1_Str1Mod6AlmID | BR4_Cluster1 | BPL131 | UINT | %MW5037 | BSR131UP01 UPS BACS String 1 Module 6 Alarm ID |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod7AlmID | BSR131UP01BACSDAT1_Str1Mod7AlmID | BR4_Cluster1 | BPL131 | UINT | %MW5042 | BSR131UP01 UPS BACS String 1 Module 7 Alarm ID |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod8AlmID | BSR131UP01BACSDAT1_Str1Mod8AlmID | BR4_Cluster1 | BPL131 | UINT | %MW5047 | BSR131UP01 UPS BACS String 1 Module 8 Alarm ID |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod9AlmID | BSR131UP01BACSDAT1_Str1Mod9AlmID | BR4_Cluster1 | BPL131 | UINT | %MW5052 | BSR131UP01 UPS BACS String 1 Module 9 Alarm ID |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod10AlmID | BSR131UP01BACSDAT1_Str1Mod10AlmID | BR4_Cluster1 | BPL131 | UINT | %MW5057 | BSR131UP01 UPS BACS String 1 Module 10 Alarm ID |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod11AlmID | BSR131UP01BACSDAT1_Str1Mod11AlmID | BR4_Cluster1 | BPL131 | UINT | %MW5062 | BSR131UP01 UPS BACS String 1 Module 11 Alarm ID |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod12AlmID | BSR131UP01BACSDAT1_Str1Mod12AlmID | BR4_Cluster1 | BPL131 | UINT | %MW5067 | BSR131UP01 UPS BACS String 1 Module 12 Alarm ID |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod13AlmID | BSR131UP01BACSDAT1_Str1Mod13AlmID | BR4_Cluster1 | BPL131 | UINT | %MW5072 | BSR131UP01 UPS BACS String 1 Module 13 Alarm ID |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod14AlmID | BSR131UP01BACSDAT1_Str1Mod14AlmID | BR4_Cluster1 | BPL131 | UINT | %MW5077 | BSR131UP01 UPS BACS String 1 Module 14 Alarm ID |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod15AlmID | BSR131UP01BACSDAT1_Str1Mod15AlmID | BR4_Cluster1 | BPL131 | UINT | %MW5082 | BSR131UP01 UPS BACS String 1 Module 15 Alarm ID |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod16AlmID | BSR131UP01BACSDAT1_Str1Mod16AlmID | BR4_Cluster1 | BPL131 | UINT | %MW5087 | BSR131UP01 UPS BACS String 1 Module 16 Alarm ID |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod17AlmID | BSR131UP01BACSDAT1_Str1Mod17AlmID | BR4_Cluster1 | BPL131 | UINT | %MW5092 | BSR131UP01 UPS BACS String 1 Module 17 Alarm ID |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod18AlmID | BSR131UP01BACSDAT1_Str1Mod18AlmID | BR4_Cluster1 | BPL131 | UINT | %MW5097 | BSR131UP01 UPS BACS String 1 Module 18 Alarm ID |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod19AlmID | BSR131UP01BACSDAT1_Str1Mod19AlmID | BR4_Cluster1 | BPL131 | UINT | %MW5102 | BSR131UP01 UPS BACS String 1 Module 19 Alarm ID |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod20AlmID | BSR131UP01BACSDAT1_Str1Mod20AlmID | BR4_Cluster1 | BPL131 | UINT | %MW5107 | BSR131UP01 UPS BACS String 1 Module 20 Alarm ID |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod21AlmID | BSR131UP01BACSDAT1_Str1Mod21AlmID | BR4_Cluster1 | BPL131 | UINT | %MW5112 | BSR131UP01 UPS BACS String 1 Module 21 Alarm ID |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod22AlmID | BSR131UP01BACSDAT1_Str2Mod22AlmID | BR4_Cluster1 | BPL131 | UINT | %MW5115 | BSR131UP01 UPS BACS String 2 Module 22 Alarm ID |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod22AlmID | BSR131UP01BACSDAT1_Str1Mod22AlmID | BR4_Cluster1 | BPL131 | UINT | %MW5117 | BSR131UP01 UPS BACS String 1 Module 22 Alarm ID |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod23AlmID | BSR131UP01BACSDAT1_Str2Mod23AlmID | BR4_Cluster1 | BPL131 | UINT | %MW5120 | BSR131UP01 UPS BACS String 2 Module 23 Alarm ID |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod23AlmID | BSR131UP01BACSDAT1_Str1Mod23AlmID | BR4_Cluster1 | BPL131 | UINT | %MW5122 | BSR131UP01 UPS BACS String 1 Module 23 Alarm ID |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod24AlmID | BSR131UP01BACSDAT1_Str2Mod24AlmID | BR4_Cluster1 | BPL131 | UINT | %MW5125 | BSR131UP01 UPS BACS String 2 Module 24 Alarm ID |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod24AlmID | BSR131UP01BACSDAT1_Str1Mod24AlmID | BR4_Cluster1 | BPL131 | UINT | %MW5127 | BSR131UP01 UPS BACS String 1 Module 24 Alarm ID |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod25AlmID | BSR131UP01BACSDAT1_Str2Mod25AlmID | BR4_Cluster1 | BPL131 | UINT | %MW5130 | BSR131UP01 UPS BACS String 2 Module 25 Alarm ID |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod25AlmID | BSR131UP01BACSDAT1_Str1Mod25AlmID | BR4_Cluster1 | BPL131 | UINT | %MW5132 | BSR131UP01 UPS BACS String 1 Module 25 Alarm ID |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod26AlmID | BSR131UP01BACSDAT1_Str2Mod26AlmID | BR4_Cluster1 | BPL131 | UINT | %MW5135 | BSR131UP01 UPS BACS String 2 Module 26 Alarm ID |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod26AlmID | BSR131UP01BACSDAT1_Str1Mod26AlmID | BR4_Cluster1 | BPL131 | UINT | %MW5137 | BSR131UP01 UPS BACS String 1 Module 26 Alarm ID |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod27AlmID | BSR131UP01BACSDAT1_Str2Mod27AlmID | BR4_Cluster1 | BPL131 | UINT | %MW5140 | BSR131UP01 UPS BACS String 2 Module 27 Alarm ID |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod27AlmID | BSR131UP01BACSDAT1_Str1Mod27AlmID | BR4_Cluster1 | BPL131 | UINT | %MW5142 | BSR131UP01 UPS BACS String 1 Module 27 Alarm ID |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod28AlmID | BSR131UP01BACSDAT1_Str2Mod28AlmID | BR4_Cluster1 | BPL131 | UINT | %MW5145 | BSR131UP01 UPS BACS String 2 Module 28 Alarm ID |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod28AlmID | BSR131UP01BACSDAT1_Str1Mod28AlmID | BR4_Cluster1 | BPL131 | UINT | %MW5147 | BSR131UP01 UPS BACS String 1 Module 28 Alarm ID |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod29AlmID | BSR131UP01BACSDAT1_Str2Mod29AlmID | BR4_Cluster1 | BPL131 | UINT | %MW5150 | BSR131UP01 UPS BACS String 2 Module 29 Alarm ID |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod29AlmID | BSR131UP01BACSDAT1_Str1Mod29AlmID | BR4_Cluster1 | BPL131 | UINT | %MW5152 | BSR131UP01 UPS BACS String 1 Module 29 Alarm ID |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod30AlmID | BSR131UP01BACSDAT1_Str2Mod30AlmID | BR4_Cluster1 | BPL131 | UINT | %MW5155 | BSR131UP01 UPS BACS String 2 Module 30 Alarm ID |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod30AlmID | BSR131UP01BACSDAT1_Str1Mod30AlmID | BR4_Cluster1 | BPL131 | UINT | %MW5157 | BSR131UP01 UPS BACS String 1 Module 30 Alarm ID |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod31AlmID | BSR131UP01BACSDAT1_Str2Mod31AlmID | BR4_Cluster1 | BPL131 | UINT | %MW5160 | BSR131UP01 UPS BACS String 2 Module 31 Alarm ID |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod31AlmID | BSR131UP01BACSDAT1_Str1Mod31AlmID | BR4_Cluster1 | BPL131 | UINT | %MW5162 | BSR131UP01 UPS BACS String 1 Module 31 Alarm ID |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod32AlmID | BSR131UP01BACSDAT1_Str2Mod32AlmID | BR4_Cluster1 | BPL131 | UINT | %MW5165 | BSR131UP01 UPS BACS String 2 Module 32 Alarm ID |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod32AlmID | BSR131UP01BACSDAT1_Str1Mod32AlmID | BR4_Cluster1 | BPL131 | UINT | %MW5167 | BSR131UP01 UPS BACS String 1 Module 32 Alarm ID |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod33AlmID | BSR131UP01BACSDAT1_Str2Mod33AlmID | BR4_Cluster1 | BPL131 | UINT | %MW5170 | BSR131UP01 UPS BACS String 2 Module 33 Alarm ID |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod33AlmID | BSR131UP01BACSDAT1_Str1Mod33AlmID | BR4_Cluster1 | BPL131 | UINT | %MW5172 | BSR131UP01 UPS BACS String 1 Module 33 Alarm ID |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod34AlmID | BSR131UP01BACSDAT1_Str2Mod34AlmID | BR4_Cluster1 | BPL131 | UINT | %MW5175 | BSR131UP01 UPS BACS String 2 Module 34 Alarm ID |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod34AlmID | BSR131UP01BACSDAT1_Str1Mod34AlmID | BR4_Cluster1 | BPL131 | UINT | %MW5177 | BSR131UP01 UPS BACS String 1 Module 34 Alarm ID |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod35AlmID | BSR131UP01BACSDAT1_Str2Mod35AlmID | BR4_Cluster1 | BPL131 | UINT | %MW5180 | BSR131UP01 UPS BACS String 2 Module 35 Alarm ID |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod35AlmID | BSR131UP01BACSDAT1_Str1Mod35AlmID | BR4_Cluster1 | BPL131 | UINT | %MW5182 | BSR131UP01 UPS BACS String 1 Module 35 Alarm ID |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod36AlmID | BSR131UP01BACSDAT1_Str2Mod36AlmID | BR4_Cluster1 | BPL131 | UINT | %MW5185 | BSR131UP01 UPS BACS String 2 Module 36 Alarm ID |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod36AlmID | BSR131UP01BACSDAT1_Str1Mod36AlmID | BR4_Cluster1 | BPL131 | UINT | %MW5187 | BSR131UP01 UPS BACS String 1 Module 36 Alarm ID |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod37AlmID | BSR131UP01BACSDAT1_Str2Mod37AlmID | BR4_Cluster1 | BPL131 | UINT | %MW5190 | BSR131UP01 UPS BACS String 2 Module 37 Alarm ID |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod37AlmID | BSR131UP01BACSDAT1_Str1Mod37AlmID | BR4_Cluster1 | BPL131 | UINT | %MW5192 | BSR131UP01 UPS BACS String 1 Module 37 Alarm ID |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod38AlmID | BSR131UP01BACSDAT1_Str2Mod38AlmID | BR4_Cluster1 | BPL131 | UINT | %MW5195 | BSR131UP01 UPS BACS String 2 Module 38 Alarm ID |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod38AlmID | BSR131UP01BACSDAT1_Str1Mod38AlmID | BR4_Cluster1 | BPL131 | UINT | %MW5197 | BSR131UP01 UPS BACS String 1 Module 38 Alarm ID |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod39AlmID | BSR131UP01BACSDAT1_Str2Mod39AlmID | BR4_Cluster1 | BPL131 | UINT | %MW5200 | BSR131UP01 UPS BACS String 2 Module 39 Alarm ID |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod39AlmID | BSR131UP01BACSDAT1_Str1Mod39AlmID | BR4_Cluster1 | BPL131 | UINT | %MW5202 | BSR131UP01 UPS BACS String 1 Module 39 Alarm ID |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod40AlmID | BSR131UP01BACSDAT1_Str2Mod40AlmID | BR4_Cluster1 | BPL131 | UINT | %MW5205 | BSR131UP01 UPS BACS String 2 Module 40 Alarm ID |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod40AlmID | BSR131UP01BACSDAT1_Str1Mod40AlmID | BR4_Cluster1 | BPL131 | UINT | %MW5207 | BSR131UP01 UPS BACS String 1 Module 40 Alarm ID |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod1AlmID | BSR131UP01BACSDAT1_Str2Mod1AlmID | BR4_Cluster1 | BPL131 | UINT | %MW5216 | BSR131UP01 UPS BACS String 2 Module 1 Alarm ID |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod2AlmID | BSR131UP01BACSDAT1_Str2Mod2AlmID | BR4_Cluster1 | BPL131 | UINT | %MW5221 | BSR131UP01 UPS BACS String 2 Module 2 Alarm ID |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod3AlmID | BSR131UP01BACSDAT1_Str2Mod3AlmID | BR4_Cluster1 | BPL131 | UINT | %MW5226 | BSR131UP01 UPS BACS String 2 Module 3 Alarm ID |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod4AlmID | BSR131UP01BACSDAT1_Str2Mod4AlmID | BR4_Cluster1 | BPL131 | UINT | %MW5231 | BSR131UP01 UPS BACS String 2 Module 4 Alarm ID |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod5AlmID | BSR131UP01BACSDAT1_Str2Mod5AlmID | BR4_Cluster1 | BPL131 | UINT | %MW5236 | BSR131UP01 UPS BACS String 2 Module 5 Alarm ID |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod6AlmID | BSR131UP01BACSDAT1_Str2Mod6AlmID | BR4_Cluster1 | BPL131 | UINT | %MW5241 | BSR131UP01 UPS BACS String 2 Module 6 Alarm ID |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod7AlmID | BSR131UP01BACSDAT1_Str2Mod7AlmID | BR4_Cluster1 | BPL131 | UINT | %MW5246 | BSR131UP01 UPS BACS String 2 Module 7 Alarm ID |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod8AlmID | BSR131UP01BACSDAT1_Str2Mod8AlmID | BR4_Cluster1 | BPL131 | UINT | %MW5251 | BSR131UP01 UPS BACS String 2 Module 8 Alarm ID |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod9AlmID | BSR131UP01BACSDAT1_Str2Mod9AlmID | BR4_Cluster1 | BPL131 | UINT | %MW5256 | BSR131UP01 UPS BACS String 2 Module 9 Alarm ID |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod10AlmID | BSR131UP01BACSDAT1_Str2Mod10AlmID | BR4_Cluster1 | BPL131 | UINT | %MW5261 | BSR131UP01 UPS BACS String 2 Module 10 Alarm ID |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod11AlmID | BSR131UP01BACSDAT1_Str2Mod11AlmID | BR4_Cluster1 | BPL131 | UINT | %MW5266 | BSR131UP01 UPS BACS String 2 Module 11 Alarm ID |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod12AlmID | BSR131UP01BACSDAT1_Str2Mod12AlmID | BR4_Cluster1 | BPL131 | UINT | %MW5271 | BSR131UP01 UPS BACS String 2 Module 12 Alarm ID |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod13AlmID | BSR131UP01BACSDAT1_Str2Mod13AlmID | BR4_Cluster1 | BPL131 | UINT | %MW5276 | BSR131UP01 UPS BACS String 2 Module 13 Alarm ID |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod14AlmID | BSR131UP01BACSDAT1_Str2Mod14AlmID | BR4_Cluster1 | BPL131 | UINT | %MW5281 | BSR131UP01 UPS BACS String 2 Module 14 Alarm ID |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod15AlmID | BSR131UP01BACSDAT1_Str2Mod15AlmID | BR4_Cluster1 | BPL131 | UINT | %MW5286 | BSR131UP01 UPS BACS String 2 Module 15 Alarm ID |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod16AlmID | BSR131UP01BACSDAT1_Str2Mod16AlmID | BR4_Cluster1 | BPL131 | UINT | %MW5291 | BSR131UP01 UPS BACS String 2 Module 16 Alarm ID |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod17AlmID | BSR131UP01BACSDAT1_Str2Mod17AlmID | BR4_Cluster1 | BPL131 | UINT | %MW5296 | BSR131UP01 UPS BACS String 2 Module 17 Alarm ID |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod18AlmID | BSR131UP01BACSDAT1_Str2Mod18AlmID | BR4_Cluster1 | BPL131 | UINT | %MW5301 | BSR131UP01 UPS BACS String 2 Module 18 Alarm ID |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod19AlmID | BSR131UP01BACSDAT1_Str2Mod19AlmID | BR4_Cluster1 | BPL131 | UINT | %MW5306 | BSR131UP01 UPS BACS String 2 Module 19 Alarm ID |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod20AlmID | BSR131UP01BACSDAT1_Str2Mod20AlmID | BR4_Cluster1 | BPL131 | UINT | %MW5311 | BSR131UP01 UPS BACS String 2 Module 20 Alarm ID |  |  | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod21AlmID | BSR131UP01BACSDAT1_Str2Mod21AlmID | BR4_Cluster1 | BPL131 | UINT | %MW5316 | BSR131UP01 UPS BACS String 2 Module 21 Alarm ID |  |  | BS1_Tags

## Alarms
BR4.SRV.CTRLSYS.PLC.BPL131.Drop02 | BTY1502DX02DIO1PLM6_Ch01Flt_A | BPL131 Drop 2 - BTY1502DX02 | BR4_Cluster1 | CAT_P3 | Slot 6 AHI Module Channel 1 Fault | BPL131 | BTY1502DX02 AHI Module 6 Channel 1 Fault Alarm | BTY1502DX02DIO1PLM6_Ch01Flt_A | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC01 | BMC131INC01CB02_A | BMC131 Motor Control Centre - Incomer 1 | BR4_Cluster1 |  |  | BPL131 | BMC131 Process Bus Incomer Arc Flash Supply (Q204) Open | BMC131INC01CB02_A | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC01 | BMC131INC01CB03_A | BMC131 Motor Control Centre - Incomer 1 | BR4_Cluster1 |  |  | BPL131 | BMC131 Process Bus Incomer Incomer Circuit Breaker Spring Charge Supply (Q212) Open | BMC131INC01CB03_A | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC01 | BMC131INC01CB04_A | BMC131 Motor Control Centre - Incomer 1 | BR4_Cluster1 |  |  | BPL131 | BMC131 Process Bus Incomer Incomer Circuit Breaker Trip Supply (Q220) Open | BMC131INC01CB04_A | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC01 | BMC131INC01CB05_A | BMC131 Motor Control Centre - Incomer 1 | BR4_Cluster1 |  |  | BPL131 | BMC131 Process Bus Incomer Incomer Circuit Breaker 24VDC Cubicle Bus Supply (Q256) Open | BMC131INC01CB05_A | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC01 | BMC131INC01CB06_A | BMC131 Motor Control Centre - Incomer 1 | BR4_Cluster1 |  |  | BPL131 | BMC131 Process Bus Incomer 110VDC/24VDC Power Supply (Q215) Open | BMC131INC01CB06_A | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC01 | BMC131INC01PR1_CBCls_A | BMC131 Motor Control Centre - Incomer 1 | BR4_Cluster1 |  |  | BPL131 | BMC131 Process Bus Incomer Protection Relay Circuit Breaker Alarm Alarm | BMC131INC01PR1_CBCls_A | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC01 | BMC131INC01PR1_CBFlt_A | BMC131 Motor Control Centre - Incomer 1 | BR4_Cluster1 |  |  | BPL131 | BMC131 Process Bus Incomer Protection Relay Fault Alarm | BMC131INC01PR1_CBFlt_A | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC01 | BMC131INC01PR1_ComFlt_A | BMC131 Motor Control Centre - Incomer 1 | BR4_Cluster1 |  |  | BPL131 | BMC131 Process Bus Incomer Protection Relay Communications Fault Alarm Alarm | BMC131INC01PR1_ComFlt_A | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC01 | BMC131INC01PR1_Flt_A | BMC131 Motor Control Centre - Incomer 1 | BR4_Cluster1 |  |  | BPL131 | BMC131 Process Bus Incomer Protection Relay Fault Alarm Alarm | BMC131INC01PR1_Flt_A | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC01 | BMC131INC01PR1_MntRqd_A | BMC131 Motor Control Centre - Incomer 1 | BR4_Cluster1 |  |  | BPL131 | BMC131 Process Bus Incomer Protection Relay Contactor Replacement Required Alarm Alarm | BMC131INC01PR1_MntRqd_A | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC01 | BMC131INC01TRP02_A | BMC131 Motor Control Centre - Incomer 1 | BR4_Cluster1 |  |  | BPL131 | BMC131 Process Bus Incomer Arc Flash Tripped | BMC131INC01TRP02_A | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC01 | BMC131INC01VDC01_A | BMC131 Motor Control Centre - Incomer 1 | BR4_Cluster1 |  |  | BPL131 | BMC131 Process Bus Incomer 24VDC Control Supply (Q267) Failure | BMC131INC01VDC01_A | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC01 | BMC131INC01XS02_A | BMC131 Motor Control Centre - Incomer 1 | BR4_Cluster1 |  |  | BPL131 | BMC131 Process Bus Incomer Vamp Self Supervision Alarm | BMC131INC01XS02_A | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC01 | BMC131INC01XS03_A | BMC131 Motor Control Centre - Incomer 1 | BR4_Cluster1 |  |  | BPL131 | BMC131 Process Bus Incomer Surge Protection Unhealthy Alarm | BMC131INC01XS03_A | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC02 | BMC131INC02CB03_A | BMC131 Motor Control Centre - Incomer 2 | BR4_Cluster1 |  |  | BPL131 | BMC131 Essential Bus Incomer Incomer Circuit Breaker Spring Charge Supply (Q212) Open | BMC131INC02CB03_A | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC02 | BMC131INC02CB04_A | BMC131 Motor Control Centre - Incomer 2 | BR4_Cluster1 |  |  | BPL131 | BMC131 Essential Bus Incomer Incomer Circuit Breaker Trip Supply (Q220) Open | BMC131INC02CB04_A | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC02 | BMC131INC02CB05_A | BMC131 Motor Control Centre - Incomer 2 | BR4_Cluster1 |  |  | BPL131 | BMC131 Essential Bus Incomer Incomer Circuit Breaker 24VDC Cubicle Bus Supply (Q256) Open | BMC131INC02CB05_A | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC02 | BMC131INC02CB06_A | BMC131 Motor Control Centre - Incomer 2 | BR4_Cluster1 |  |  | BPL131 | BMC131 Essential Bus Incomer 110VDC/24VDC Power Supply (Q215) Open | BMC131INC02CB06_A | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC02 | BMC131INC02PR1_CBCls_A | BMC131 Motor Control Centre - Incomer 2 | BR4_Cluster1 |  |  | BPL131 | BMC131 Essential Bus Incomer Protection Relay Circuit Breaker Alarm Alarm | BMC131INC02PR1_CBCls_A | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC02 | BMC131INC02PR1_CBFlt_A | BMC131 Motor Control Centre - Incomer 2 | BR4_Cluster1 |  |  | BPL131 | BMC131 Essential Bus Incomer Protection Relay Fault Alarm | BMC131INC02PR1_CBFlt_A | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC02 | BMC131INC02PR1_ComFlt_A | BMC131 Motor Control Centre - Incomer 2 | BR4_Cluster1 |  |  | BPL131 | BMC131 Essential Bus Incomer Protection Relay Communications Fault Alarm Alarm | BMC131INC02PR1_ComFlt_A | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC02 | BMC131INC02PR1_Flt_A | BMC131 Motor Control Centre - Incomer 2 | BR4_Cluster1 |  |  | BPL131 | BMC131 Essential Bus Incomer Protection Relay Fault Alarm Alarm | BMC131INC02PR1_Flt_A | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC02 | BMC131INC02PR1_MntRqd_A | BMC131 Motor Control Centre - Incomer 2 | BR4_Cluster1 |  |  | BPL131 | BMC131 Essential Bus Incomer Protection Relay Contactor Replacement Required Alarm Alarm | BMC131INC02PR1_MntRqd_A | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC02 | BMC131INC02VDC01_A | BMC131 Motor Control Centre - Incomer 2 | BR4_Cluster1 |  |  | BPL131 | BMC131 Essential Bus Incomer 24VDC Control Supply (Q267) Failure | BMC131INC02VDC01_A | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC02 | BMC131INC02XS03_A | BMC131 Motor Control Centre - Incomer 2 | BR4_Cluster1 |  |  | BPL131 | BMC131 Essential Bus Incomer Surge Protection Unhealthy Alarm | BMC131INC02XS03_A | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC03 | BMC131INC03PR1_CBCls_A | BMC131 Motor Control Centre - Incomer 3 | BR4_Cluster1 |  |  | BPL131 | BMC131 Generator Bus Incomer Protection Relay Circuit Breaker Alarm Alarm | BMC131INC03PR1_CBCls_A | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC03 | BMC131INC03PR1_CBFlt_A | BMC131 Motor Control Centre - Incomer 3 | BR4_Cluster1 |  |  | BPL131 | BMC131 Generator Bus Incomer Protection Relay Fault Alarm | BMC131INC03PR1_CBFlt_A | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC03 | BMC131INC03PR1_ComFlt_A | BMC131 Motor Control Centre - Incomer 3 | BR4_Cluster1 |  |  | BPL131 | BMC131 Generator Bus Incomer Protection Relay Communications Fault Alarm Alarm | BMC131INC03PR1_ComFlt_A | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC03 | BMC131INC03PR1_Flt_A | BMC131 Motor Control Centre - Incomer 3 | BR4_Cluster1 |  |  | BPL131 | BMC131 Generator Bus Incomer Protection Relay Fault Alarm Alarm | BMC131INC03PR1_Flt_A | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC03 | BMC131INC03PR1_MntRqd_A | BMC131 Motor Control Centre - Incomer 3 | BR4_Cluster1 |  |  | BPL131 | BMC131 Generator Bus Incomer Protection Relay Contactor Replacement Required Alarm Alarm | BMC131INC03PR1_MntRqd_A | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC03 | BMC131INC03VDC01_A | BMC131 Motor Control Centre - Incomer 3 | BR4_Cluster1 |  |  | BPL131 | BMC131 Generator Bus Incomer 24VDC Control Supply (Q267) Failure | BMC131INC03VDC01_A | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC01.VAMP | BMC131VAMPPR1_ComFlt_A | BMC131 Motor Control Centre - Incomer 1 VAMP Arc Flash | BR4_Cluster1 |  |  | BPL131 | BMC131 Incomer Vamp Relay Communications Fault Alarm | BMC131VAMPPR1_ComFlt_A | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC01.VAMP | BMC131VAMPPR1_ProFlt_A | BMC131 Motor Control Centre - Incomer 1 VAMP Arc Flash | BR4_Cluster1 |  |  | BPL131 | BMC131VAMPPR1 Vamp Arc Flash Protection Fault | BMC131VAMPPR1_ProFlt_A | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC01.VAMP | BMC131VAMPPR1_SysFlt_A | BMC131 Motor Control Centre - Incomer 1 VAMP Arc Flash | BR4_Cluster1 |  |  | BPL131 | BMC131VAMPPR1 Vamp Arc Flash Protection Fault Alarm | BMC131VAMPPR1_SysFlt_A | BS1_Tags
BR4.SRV.PWR.BSR131.BMC1311.Sub.CB01 | BMC1311CB01_A | BMC1311 HME Refuelling Feeder Main Circuit Breaker | BR4_Cluster1 |  |  | BPL131 | HME Refuelling MCC Main Circuit Breaker (Q103) Open | BMC1311CB01_A | BS1_Tags
BR4.SRV.PWR.BSR131.BMC1311.Sub.CB01 | BMC1311TRP01_A | BMC1311 HME Refuelling Feeder Main Circuit Breaker | BR4_Cluster1 |  |  | BPL131 | HME Refuelling MCC Main Circuit Breaker Tripped | BMC1311TRP01_A | BS1_Tags
BR4.SRV.PWR.BSR131.BMC1311 | BMC1311VDC01_A | BMC1311 HME Refuelling Feeder | BR4_Cluster1 |  |  | BPL131 | HME Refuelling MCC 24VDC Control Supply (Q155) Failure | BMC1311VDC01_A | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131 | BPL131_Def_A | BPL131 PLC | BR4_Cluster1 |  |  | BPL131 | NPI Hub BPL131 Default Values Loaded Alarm | BPL131_Def_A | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131 | BPL131_MemFlt_A | BPL131 PLC | BR4_Cluster1 |  |  | BPL131 | NPI Hub PLC CPU Memory Card Error Alarm | BPL131_MemFlt_A | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131 | BPL131_Sys1Flt_A | BPL131 PLC | BR4_Cluster1 |  |  | BPL131 | NPI Hub PLC CPU Arithmetic Fault Alarm | BPL131_Sys1Flt_A | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131 | BPL131_Sys2Flt_A | BPL131 PLC | BR4_Cluster1 |  |  | BPL131 | NPI Hub PLC CPU Index Overflow Fault Alarm | BPL131_Sys2Flt_A | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131 | BPL131IPC2_Flt_A | BPL131 PLC | BR4_Cluster1 |  |  | BPL131 | BPL131 Communications From BPL130 Fault Alarm | BPL131IPC2_Flt_A | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131 | BPL131IPC2_PriFlt_A | BPL131 PLC | BR4_Cluster1 |  |  | BPL131 | BPL131 Communications From BPL130 Primary Path Fault Alarm | BPL131IPC2_PriFlt_A | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131 | BPL131IPC2_SecFlt_A | BPL131 PLC | BR4_Cluster1 |  |  | BPL131 | BPL131 Communications From BPL130 Secondary Path Fault Alarm | BPL131IPC2_SecFlt_A | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131 | BPL131IPC3_Flt_A | BPL131 PLC | BR4_Cluster1 |  |  | BPL131 | BPL131 Communications From BPL132 Fault Alarm | BPL131IPC3_Flt_A | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131 | BPL131IPC3_PriFlt_A | BPL131 PLC | BR4_Cluster1 |  |  | BPL131 | BPL131 Communications From BPL132 Primary Path Fault Alarm | BPL131IPC3_PriFlt_A | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131 | BPL131IPC3_SecFlt_A | BPL131 PLC | BR4_Cluster1 |  |  | BPL131 | BPL131 Communications From BPL132 Secondary Path Fault Alarm | BPL131IPC3_SecFlt_A | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131 | BPL131PLM0_Flt_A | BPL131 PLC | BR4_Cluster1 |  |  | BPL131 | NPI Hub PLC CPU RIO Network Fault Alarm | BPL131PLM0_Flt_A | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131 | BPL131PLM3_Flt_A | BPL131 PLC | BR4_Cluster1 |  |  | BPL131 | NPI Hub PLC Ethernet Module Slot 3 Fault Alarm Alarm | BPL131PLM3_Flt_A | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131 | BPL131PLM4_Flt_A | BPL131 PLC | BR4_Cluster1 |  |  | BPL131 | NPI Hub PLC Ethernet Module Slot 4 Fault Alarm Alarm | BPL131PLM4_Flt_A | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131 | BPL131PLM5_Flt_A | BPL131 PLC | BR4_Cluster1 |  |  | BPL131 | NPI Hub PLC Ethernet Module Slot 5 Fault Alarm Alarm | BPL131PLM5_Flt_A | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1 | BPP1101_2_EqpAvlFlt_A | West Turkeys Nest Raw Water Distribution Pumps | BR4_Cluster1 |  |  | BPL131 | No NPI and Process Water Pumps Available Fault Alarm | BPP1101_2_EqpAvlFlt_A | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1101.Sub.CB01 | BPP1101CB01_A | BPP1101 - Feeder Main Cicuit Breaker | BR4_Cluster1 |  |  | BPL131 | Production Plant and NPI Water Supply Pump 1 Main Circuit Breaker (Q103) Open | BPP1101CB01_A | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1101 | BPP1101FS09_A | BPP1101 - Raw Water Distribution Pump | BR4_Cluster1 |  |  | BPL131 | BPP1101FS09 Pump Flow Switch Low Alarm | BPP1101FS09_A | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1101 | BPP1101FS09_FailStp_A | BPP1101 - Raw Water Distribution Pump | BR4_Cluster1 |  |  | BPL131 | BPP1101FS09 Fail to Stop Alarm | BPP1101FS09_FailStp_A | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1101.FieldIO.FT03 | BPP1101FT03_Frz_A | BPP1101 - FT03 NPI/PC3 Supply Flowmeter | BR4_Cluster1 |  |  | BPL131 | BPP1101FT03 Flow Transmitter Frozen Alarm | BPP1101FT03_Frz_A | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1101.FieldIO.FT03 | BPP1101FT03_Hi_A | BPP1101 - FT03 NPI/PC3 Supply Flowmeter | BR4_Cluster1 |  |  | BPL131 | BPP1101FT03 Pump Flow High Alarm | BPP1101FT03_Hi_A | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1101.FieldIO.FT03 | BPP1101FT03_HiHi_A | BPP1101 - FT03 NPI/PC3 Supply Flowmeter | BR4_Cluster1 |  |  | BPL131 | BPP1101FT03 NPI and Process Water Supply Flow High High Healthy | BPP1101FT03_HiHi_A | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1101.FieldIO.FT03 | BPP1101FT03_Lo_A | BPP1101 - FT03 NPI/PC3 Supply Flowmeter | BR4_Cluster1 |  |  | BPL131 | BPP1101FT03 Flow Low Alarm | BPP1101FT03_Lo_A | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1101.VS01 | BPP1101IS01_A | BPP1101 - Raw Water Distribution Pump VSD | BR4_Cluster1 |  |  | BPL131 | BPP1101 Isolator Open Alarm | BPP1101IS01_A | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1101.FieldIO.PT03 | BPP1101PT03_Frz_A | BPP1101 - PT03 Pump Discharge Pressure | BR4_Cluster1 |  |  | BPL131 | BPP1101PT03 Pump Discharge Pressure Transmitter Frozen Alarm | BPP1101PT03_Frz_A | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1101.FieldIO.PT03 | BPP1101PT03_HiHi_A | BPP1101 - PT03 Pump Discharge Pressure | BR4_Cluster1 |  |  | BPL131 | BPP1101PT03 System Pressure High High Alarm | BPP1101PT03_HiHi_A | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1101.FieldIO.PT03 | BPP1101PT03_LoLo_A | BPP1101 - PT03 Pump Discharge Pressure | BR4_Cluster1 |  |  | BPL131 | BPP1101PT03 Pump Discharge Pressure Low Low Alarm | BPP1101PT03_LoLo_A | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1101.FieldIO.PT10 | BPP1101PT10_Diff_A | BPP1101 - PT10 BS1 Raw Water Distribution Pressure 1 | BR4_Cluster1 |  |  | BPL131 | NPI and Process Water Network Pressure Variance (PT10/PT11) Alarm | BPP1101PT10_Diff_A | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1101.FieldIO.PT10 | BPP1101PT10_Frz_A | BPP1101 - PT10 BS1 Raw Water Distribution Pressure 1 | BR4_Cluster1 |  |  | BPL131 | BPP1101PT10 System Pressure Frozen Alarm | BPP1101PT10_Frz_A | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1101.FieldIO.PT10 | BPP1101PT10_Hi_A | BPP1101 - PT10 BS1 Raw Water Distribution Pressure 1 | BR4_Cluster1 |  |  | BPL131 | BPP1101PT10 Discharge Header Pressure High Alarm | BPP1101PT10_Hi_A | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1101.FieldIO.PT10 | BPP1101PT10_Lo_A | BPP1101 - PT10 BS1 Raw Water Distribution Pressure 1 | BR4_Cluster1 |  |  | BPL131 | BPP1101PT10 Discharge Header Pressure Low Akarn | BPP1101PT10_Lo_A | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1101.FieldIO.PT11 | BPP1101PT11_Frz_A | BPP1101 - PT11 BS1 Raw Water Distribution Pressure 2 | BR4_Cluster1 |  |  | BPL131 | BPP1101PT11 Discharge Header Pressure Transmitter Frozen Alarm | BPP1101PT11_Frz_A | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1101.FieldIO.PT11 | BPP1101PT11_Hi_A | BPP1101 - PT11 BS1 Raw Water Distribution Pressure 2 | BR4_Cluster1 |  |  | BPL131 | BPP1101PT11 System Pressure High Alarm | BPP1101PT11_Hi_A | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1101.FieldIO.PT11 | BPP1101PT11_Lo_A | BPP1101 - PT11 BS1 Raw Water Distribution Pressure 2 | BR4_Cluster1 |  |  | BPL131 | BPP1101PT11 Discharge Header Pressure Low Alarm | BPP1101PT11_Lo_A | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1101 | BPP1101THR01_A | BPP1101 - Raw Water Distribution Pump | BR4_Cluster1 |  |  | BPL131 | Production Plant and NPI Water Supply Pump 1 Production Plant & NPI Water Supply Pump 1 (Duty) (K190) | BPP1101THR01_A | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1101.Sub.CB01 | BPP1101TRP01_A | BPP1101 - Feeder Main Cicuit Breaker | BR4_Cluster1 |  |  | BPL131 | BPP1101 Main Circuit Breaker Tripped Alarm | BPP1101TRP01_A | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1101 | BPP1101VDC01_A | BPP1101 - Raw Water Distribution Pump | BR4_Cluster1 |  |  | BPL131 | Production Plant and NPI Water Supply Pump 1 24VDC Control Supply (Q155) Failure | BPP1101VDC01_A | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1101.VS01 | BPP1101VS01_ComFlt_A | BPP1101 - Raw Water Distribution Pump VSD | BR4_Cluster1 |  |  | BPL131 | BPP1101VS01 VSD Communications Fault Alarm | BPP1101VS01_ComFlt_A | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1101.VS01 | BPP1101VS01_Flt_A | BPP1101 - Raw Water Distribution Pump VSD | BR4_Cluster1 |  |  | BPL131 | BPP1101VS01 VSD Fault Alarm | BPP1101VS01_Flt_A | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1101.VS01 | BPP1101VS01SY01_Flt_A | BPP1101 - Raw Water Distribution Pump VSD | BR4_Cluster1 |  |  | BPL131 | BPP1101VS01 Safety Relay Fault Healthy | BPP1101VS01SY01_Flt_A | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1101.VS01 | BPP1101VS01VDC01_A | BPP1101 - Raw Water Distribution Pump VSD | BR4_Cluster1 |  |  | BPL131 | BPP1101VS01 VVVF Drive BPP1101VS01 Control Supply (Q204) Failure | BPP1101VS01VDC01_A | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1102.Sub.CB01 | BPP1102CB01_A | BPP1102 - Feeder Main Cicuit Breaker | BR4_Cluster1 |  |  | BPL131 | Production Plant and NPI Water Supply Pump 2 Main Circuit Breaker (Q103) Open | BPP1102CB01_A | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1102 | BPP1102FS10_A | BPP1102 - Raw Water Distribution Pump | BR4_Cluster1 |  |  | BPL131 | BPP1102FS10 Pump Flow Switch Low Alarm | BPP1102FS10_A | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1102 | BPP1102FS10_FailStp_A | BPP1102 - Raw Water Distribution Pump | BR4_Cluster1 |  |  | BPL131 | BPP1102FS10 Pump Fail to Stop Alarm | BPP1102FS10_FailStp_A | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1102 | BPP1102IS01_A | BPP1102 - Raw Water Distribution Pump | BR4_Cluster1 |  |  | BPL131 | BPP1102 Isolator Open Alarm | BPP1102IS01_A | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1102.FieldIO.PT04 | BPP1102PT04_Frz_A | BPP1102 - PT04 Pump Discharge Pressure | BR4_Cluster1 |  |  | BPL131 | BPP1102PT04 Pump Discharge Pressure Transmitter Frozen Alarm | BPP1102PT04_Frz_A | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1102.FieldIO.PT04 | BPP1102PT04_HiHi_A | BPP1102 - PT04 Pump Discharge Pressure | BR4_Cluster1 |  |  | BPL131 | BPP1102PT04 Pump Discharge Pressure High High Alarm | BPP1102PT04_HiHi_A | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1102.FieldIO.PT04 | BPP1102PT04_LoLo_A | BPP1102 - PT04 Pump Discharge Pressure | BR4_Cluster1 |  |  | BPL131 | BPP1102PT04 Pump Discharge Pressure Low Low Alarm | BPP1102PT04_LoLo_A | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1102 | BPP1102THR01_A | BPP1102 - Raw Water Distribution Pump | BR4_Cluster1 |  |  | BPL131 | Production Plant and NPI Water Supply Pump 2 Production Plant & NPI Water Supply Pump 2 (Standby) (K190) | BPP1102THR01_A | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1102.Sub.CB01 | BPP1102TRP01_A | BPP1102 - Feeder Main Cicuit Breaker | BR4_Cluster1 |  |  | BPL131 | BPP1102 Main Circuit Breaker Tripped Alarm | BPP1102TRP01_A | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1102 | BPP1102VDC01_A | BPP1102 - Raw Water Distribution Pump | BR4_Cluster1 |  |  | BPL131 | Production Plant and NPI Water Supply Pump 2 24VDC Control Supply (Q155) Failure | BPP1102VDC01_A | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1102.VS01 | BPP1102VS01_ComFlt_A | BPP1102 - Raw Water Distribution Pump VSD | BR4_Cluster1 |  |  | BPL131 | BPP1107VS01 VSD Communications Fault Alarm | BPP1102VS01_ComFlt_A | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1102.VS01 | BPP1102VS01_Flt_A | BPP1102 - Raw Water Distribution Pump VSD | BR4_Cluster1 |  |  | BPL131 | BPP1102VS01 VSD Fault Alarm | BPP1102VS01_Flt_A | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1102.VS01 | BPP1102VS01SY01_Flt_A | BPP1102 - Raw Water Distribution Pump VSD | BR4_Cluster1 |  |  | BPL131 | BPP1102VS01 Safety Relay Fault Healthy | BPP1102VS01SY01_Flt_A | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1102.VS01 | BPP1102VS01VDC01_A | BPP1102 - Raw Water Distribution Pump VSD | BR4_Cluster1 |  |  | BPL131 | BPP1101VS01 VVVF Drive BPP1102VS01 Control Supply (Q207) Failure | BPP1102VS01VDC01_A | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT | BPP1103_4_5_EqpAvlFlt_A | West Turkeys Nest Raw Water Transfer Pumps | BR4_Cluster1 |  |  | BPL131 | No Transfer Pumps Available Fault Alarm | BPP1103_4_5_EqpAvlFlt_A | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1103 | BPP1103_FailStp_A | BPP1103 - Raw Water Transfer Pump | BR4_Cluster1 |  |  | BPL131 | Water Transfer Pump 1 Fail to Stop Alarm | BPP1103_FailStp_A | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1103.Sub.CB01 | BPP1103CB01_A | BPP1103 - Feeder Main Cicuit Breaker | BR4_Cluster1 |  |  | BPL131 | Water Transfer Pump 1 Main Circuit Breaker (Q103) Open | BPP1103CB01_A | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1103.FieldIO.FT03 | BPP1103FT03_Frz_A | BPP1103 - FT03 Pump Flowmeter | BR4_Cluster1 |  |  | BPL131 | BPP1103FT03 Pump Flow Transmitter Frozen Alarm | BPP1103FT03_Frz_A | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1103.FieldIO.FT03 | BPP1103FT03_LoLo_A | BPP1103 - FT03 Pump Flowmeter | BR4_Cluster1 |  |  | BPL131 | BPP1103FT03 Pump Flow Low Low Alarm | BPP1103FT03_LoLo_A | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1103.FieldIO.FT06 | BPP1103FT06_Frz_A | RWT - FT03 Transfer Pipeline Flowmeter | BR4_Cluster1 |  |  | BPL131 | BPP1103FT06 Transfer Flow Transmitter Frozen Alarm | BPP1103FT06_Frz_A | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1103.FieldIO.FT06 | BPP1103FT06_HiHi_A | RWT - FT03 Transfer Pipeline Flowmeter | BR4_Cluster1 |  |  | BPL131 | BPP1103FT06 Transfer Flow High High Alarm | BPP1103FT06_HiHi_A | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1103.FieldIO.FT06 | BPP1103FT06_LkFlt_A | RWT - FT03 Transfer Pipeline Flowmeter | BR4_Cluster1 |  |  | BPL131 | BPP1103FT06 Water Transfer Pipeline Leak Detected Alarm | BPP1103FT06_LkFlt_A | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1103.FieldIO.FT06 | BPP1103FT06_RevFlw_A | RWT - FT03 Transfer Pipeline Flowmeter | BR4_Cluster1 |  |  | BPL131 | BPP1103FT06 Water Transfer Pumps Reverse Flow Detected Alarm | BPP1103FT06_RevFlw_A | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1103 | BPP1103IS01_A | BPP1103 - Raw Water Transfer Pump | BR4_Cluster1 |  |  | BPL131 | BPP1103 Isolator Alarm | BPP1103IS01_A | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1103.FieldIO.PT05 | BPP1103PT05_Frz_A | BPP1103 - PT05 Pump Discharge Pressure | BR4_Cluster1 |  |  | BPL131 | BPP1103PT05 Pump Discharge Pressure Transmitter Frozen Alarm | BPP1103PT05_Frz_A | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1103.FieldIO.PT05 | BPP1103PT05_HiHi_A | BPP1103 - PT05 Pump Discharge Pressure | BR4_Cluster1 |  |  | BPL131 | BPP1103PT05 Pump Discharge Pressure High High Alarm | BPP1103PT05_HiHi_A | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1103.FieldIO.PT05 | BPP1103PT05_LoLo_A | BPP1103 - PT05 Pump Discharge Pressure | BR4_Cluster1 |  |  | BPL131 | BPP1103PT05 Pump Discharge Pressure Low Low Alarm | BPP1103PT05_LoLo_A | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1103.FieldIO.PT08 | BPP1103PT08_Frz_A | BPP1103 - PT08 Transfer Header Pressure | BR4_Cluster1 |  |  | BPL131 | BPP1103PT08 Water Transfer System Pressure Transmitter Frozen Alarm | BPP1103PT08_Frz_A | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1103.FieldIO.PT08 | BPP1103PT08_HiHi_A | BPP1103 - PT08 Transfer Header Pressure | BR4_Cluster1 |  |  | BPL131 | BPP1103PT08 Water Transfer System Pressure High High Alarm | BPP1103PT08_HiHi_A | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1103.FieldIO.PT08 | BPP1103PT08_Lo_A | BPP1103 - PT08 Transfer Header Pressure | BR4_Cluster1 |  |  | BPL131 | HME Standpipe Pump 1 PT08 Lo Alarm | BPP1103PT08_Lo_A | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1103 | BPP1103THR01_A | BPP1103 - Raw Water Transfer Pump | BR4_Cluster1 |  |  | BPL131 | Water Transfer Pump 1 Thermistor Relay (K190) | BPP1103THR01_A | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1103.Sub.CB01 | BPP1103TRP01_A | BPP1103 - Feeder Main Cicuit Breaker | BR4_Cluster1 |  |  | BPL131 | BPP1103 Main Circuit Breaker Tripped Alarm | BPP1103TRP01_A | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1103 | BPP1103VDC01_A | BPP1103 - Raw Water Transfer Pump | BR4_Cluster1 |  |  | BPL131 | Water Transfer Pump 1 24VDC Control Supply (Q155) Failure | BPP1103VDC01_A | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1103.VS01 | BPP1103VS01_ComFlt_A | BPP1103 - Raw Water Transfer Pump VSD | BR4_Cluster1 |  |  | BPL131 | BPP1103VS01 VSD Communications Fault Alarm | BPP1103VS01_ComFlt_A | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1103.VS01 | BPP1103VS01_Flt_A | BPP1103 - Raw Water Transfer Pump VSD | BR4_Cluster1 |  |  | BPL131 | BPP1103VS01 VSD Fault Alarm | BPP1103VS01_Flt_A | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1103.VS01 | BPP1103VS01SY01_Flt_A | BPP1103 - Raw Water Transfer Pump VSD | BR4_Cluster1 |  |  | BPL131 | BPP1103VS01 Safety Relay Fault Alarm | BPP1103VS01SY01_Flt_A | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1103.VS01 | BPP1103VS01VDC01_A | BPP1103 - Raw Water Transfer Pump VSD | BR4_Cluster1 |  |  | BPL131 | BPP1101VS01 VVVF Drive BPP1103VS01 Control Supply (Q210) Failure | BPP1103VS01VDC01_A | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1104 | BPP1104_FailStp_A | BPP1104 - Raw Water Transfer Pump | BR4_Cluster1 |  |  | BPL131 | Water Transfer Pump 2 Fail to Stop Alarm | BPP1104_FailStp_A | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1104.Sub.CB01 | BPP1104CB01_A | BPP1104 - Feeder Main Cicuit Breaker | BR4_Cluster1 |  |  | BPL131 | Water Transfer Pump 2 Main Circuit Breaker (Q103) Open | BPP1104CB01_A | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1104.FieldIO.FT04 | BPP1104FT04_Frz_A | BPP1104 - FT04 Pump Flowmeter | BR4_Cluster1 |  |  | BPL131 | BPP1104FT04 Pump Flow Transmitter Frozen Alarm | BPP1104FT04_Frz_A | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1104.FieldIO.FT04 | BPP1104FT04_LoLo_A | BPP1104 - FT04 Pump Flowmeter | BR4_Cluster1 |  |  | BPL131 | BPP1104FT04 Pump Flow Low Low Alarm | BPP1104FT04_LoLo_A | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1104 | BPP1104IS01_A | BPP1104 - Raw Water Transfer Pump | BR4_Cluster1 |  |  | BPL131 | BPP1104 Isolator Open Alarm | BPP1104IS01_A | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1104.FieldIO.PT06 | BPP1104PT06_Frz_A | BPP1104 - PT06 Pump Discharge Pressure | BR4_Cluster1 |  |  | BPL131 | BPP1104PT06 Pump Discharge Pressure Transmitter Frozen Alarm | BPP1104PT06_Frz_A | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1104.FieldIO.PT06 | BPP1104PT06_HiHi_A | BPP1104 - PT06 Pump Discharge Pressure | BR4_Cluster1 |  |  | BPL131 | BPP1104PT06 Pump Discharge Pressure High High Alarm | BPP1104PT06_HiHi_A | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1104.FieldIO.PT06 | BPP1104PT06_LoLo_A | BPP1104 - PT06 Pump Discharge Pressure | BR4_Cluster1 |  |  | BPL131 | BPP1104PT06 Pump Discharge Pressure Low Low Alarm | BPP1104PT06_LoLo_A | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1104 | BPP1104THR01_A | BPP1104 - Raw Water Transfer Pump | BR4_Cluster1 |  |  | BPL131 | Water Transfer Pump 2 Thermistor Relay (K190) | BPP1104THR01_A | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1104.Sub.CB01 | BPP1104TRP01_A | BPP1104 - Feeder Main Cicuit Breaker | BR4_Cluster1 |  |  | BPL131 | BPP1104 Main Circuit Breaker Tripped Alarm | BPP1104TRP01_A | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1104 | BPP1104VDC01_A | BPP1104 - Raw Water Transfer Pump | BR4_Cluster1 |  |  | BPL131 | Water Transfer Pump 2 24VDC Control Supply (Q155) Failure | BPP1104VDC01_A | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1104.VS01 | BPP1104VS01_ComFlt_A | BPP1104 - Raw Water Transfer Pump VSD | BR4_Cluster1 |  |  | BPL131 | BPP1104VS01 VSD Communications Fault Alarm | BPP1104VS01_ComFlt_A | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1104.VS01 | BPP1104VS01_Flt_A | BPP1104 - Raw Water Transfer Pump VSD | BR4_Cluster1 |  |  | BPL131 | BPP1104VS01 VSD Fault Alarm | BPP1104VS01_Flt_A | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1104.VS01 | BPP1104VS01SY01_Flt_A | BPP1104 - Raw Water Transfer Pump VSD | BR4_Cluster1 |  |  | BPL131 | BPP1104VS01 Safety Relay Fault Alarm | BPP1104VS01SY01_Flt_A | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1104.VS01 | BPP1104VS01VDC01_A | BPP1104 - Raw Water Transfer Pump VSD | BR4_Cluster1 |  |  | BPL131 | BPP1101VS01 VVVF Drive BPP1104VS01 Control Supply (Q213) Failure | BPP1104VS01VDC01_A | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1105 | BPP1105_FailStp_A | BPP1105 - Raw Water Transfer Pump | BR4_Cluster1 |  |  | BPL131 | Water Transfer Pump 3 Fail to Stop Alarm | BPP1105_FailStp_A | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1105 | BPP1105CB01_A | BPP1105 - Raw Water Transfer Pump | BR4_Cluster1 |  |  | BPL131 | Water Transfer Pump 3 Main Circuit Breaker (Q103) Open | BPP1105CB01_A | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1105.FieldIO.FT05 | BPP1105FT05_Frz_A | BPP1105 - FT04 Pump Flowmeter | BR4_Cluster1 |  |  | BPL131 | BPP1105FT05 Pump Flow Transmitter Frozen Alarm | BPP1105FT05_Frz_A | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1105.FieldIO.FT05 | BPP1105FT05_LoLo_A | BPP1105 - FT04 Pump Flowmeter | BR4_Cluster1 |  |  | BPL131 | BPP1105FT05 Pump Flow Low Low Alarm | BPP1105FT05_LoLo_A | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1105 | BPP1105IS01_A | BPP1105 - Raw Water Transfer Pump | BR4_Cluster1 |  |  | BPL131 | BPP1105 Isolator Open Alarm | BPP1105IS01_A | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1105.FieldIO.PT07 | BPP1105PT07_Frz_A | BPP1105 - PT06 Pump Discharge Pressure | BR4_Cluster1 |  |  | BPL131 | BPP1105PT07 Pump Discharge Pressure Transmitter Frozen Alarm | BPP1105PT07_Frz_A | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1105.FieldIO.PT07 | BPP1105PT07_HiHi_A | BPP1105 - PT06 Pump Discharge Pressure | BR4_Cluster1 |  |  | BPL131 | BPP1105PT07 Pump Discharge Pressure High High Alarm | BPP1105PT07_HiHi_A | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1105.FieldIO.PT07 | BPP1105PT07_LoLo_A | BPP1105 - PT06 Pump Discharge Pressure | BR4_Cluster1 |  |  | BPL131 | BPP1105PT07 Pump Discharge Pressure Low Low Alarm | BPP1105PT07_LoLo_A | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1105 | BPP1105THR01_A | BPP1105 - Raw Water Transfer Pump | BR4_Cluster1 |  |  | BPL131 | Water Transfer Pump 3 Thermistor Relay (K190) | BPP1105THR01_A | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1105.Sub.CB01 | BPP1105TRP01_A | BPP1105 - Feeder Main Cicuit Breaker | BR4_Cluster1 |  |  | BPL131 | BPP1105 Main Circuit Breaker Tripped Alarm | BPP1105TRP01_A | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1105 | BPP1105VDC01_A | BPP1105 - Raw Water Transfer Pump | BR4_Cluster1 |  |  | BPL131 | Water Transfer Pump 3 24VDC Control Supply (Q155) Failure | BPP1105VDC01_A | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1105.VS01 | BPP1105VS01_ComFlt_A | BPP1105 - Raw Water Transfer Pump VSD | BR4_Cluster1 |  |  | BPL131 | BPP1105VS01 VSD Communications Fault Alarm | BPP1105VS01_ComFlt_A | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1105.VS01 | BPP1105VS01_Flt_A | BPP1105 - Raw Water Transfer Pump VSD | BR4_Cluster1 |  |  | BPL131 | BPP1105VS01 VSD Fault Alarm | BPP1105VS01_Flt_A | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1105.VS01 | BPP1105VS01SY01_Flt_A | BPP1105 - Raw Water Transfer Pump VSD | BR4_Cluster1 |  |  | BPL131 | BPP1105VS01 Safety Relay Fault Alarm | BPP1105VS01SY01_Flt_A | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1105.VS01 | BPP1105VS01VDC01_A | BPP1105 - Raw Water Transfer Pump VSD | BR4_Cluster1 |  |  | BPL131 | BPP1101VS01 VVVF Drive BPP1105VS01 Control Supply (Q216) Failure | BPP1105VS01VDC01_A | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1 | BPP1106_7_EqpAvlFlt_A | West Turkeys Nest Standpipe Pumps | BR4_Cluster1 |  |  | BPL131 | No Standpipe Pumps Available Fault Alarm | BPP1106_7_EqpAvlFlt_A | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BPP1106 | BPP1106_RunNoVlv_A | BPP1106 - Standpipe Pump | BR4_Cluster1 |  |  | BPL131 | BPP1106 Pump Running with No Valve Open Alarm | BPP1106_RunNoVlv_A | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BPP1106.Sub.CB01 | BPP1106CB01_A | BPP1106 - Feeder Main Cicuit Breaker | BR4_Cluster1 |  |  | BPL131 | HME & LME Standpipe Pump 3 Main Circuit Breaker (Q103) Open | BPP1106CB01_A | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BPP1106 | BPP1106FS07_A | BPP1106 - Standpipe Pump | BR4_Cluster1 |  |  | BPL131 | BPP1106FS07 Pump Flow Switch Low Alarm | BPP1106FS07_A | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BPP1106 | BPP1106FS07_FailStp_A | BPP1106 - Standpipe Pump | BR4_Cluster1 |  |  | BPL131 | BPP1106FS07 Fail to Stop Alarm | BPP1106FS07_FailStp_A | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BPP1106 | BPP1106IS01_A | BPP1106 - Standpipe Pump | BR4_Cluster1 |  |  | BPL131 | BPP1106 Isolator Open Alarm | BPP1106IS01_A | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BPP1106.FieldIO.PT01 | BPP1106PT01_Frz_A | BPP1106 - PT01 Pump Discharge Pressure | BR4_Cluster1 |  |  | BPL131 | BPP1106PT01 Pump Discharge Pressure Transmitter Frozen Alarm | BPP1106PT01_Frz_A | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BPP1106.FieldIO.PT01 | BPP1106PT01_HiHi_A | BPP1106 - PT01 Pump Discharge Pressure | BR4_Cluster1 |  |  | BPL131 | BPP1106PT01 Pump Discharge Pressure High High Alarm | BPP1106PT01_HiHi_A | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BPP1106.FieldIO.PT01 | BPP1106PT01_LoLo_A | BPP1106 - PT01 Pump Discharge Pressure | BR4_Cluster1 |  |  | BPL131 | BPP1106PT01 Pump Discharge Pressure Low Low Alarm | BPP1106PT01_LoLo_A | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BPP1106 | BPP1106THR01_A | BPP1106 - Standpipe Pump | BR4_Cluster1 |  |  | BPL131 | HME & LME Standpipe Pump 3 HME And LME Standpipe Pump 3 (Duty) (K190) | BPP1106THR01_A | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BPP1106.Sub.CB01 | BPP1106TRP01_A | BPP1106 - Feeder Main Cicuit Breaker | BR4_Cluster1 |  |  | BPL131 | BPP1106 Main Circuit Breaker Tripped Alarm | BPP1106TRP01_A | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BPP1106 | BPP1106VDC01_A | BPP1106 - Standpipe Pump | BR4_Cluster1 |  |  | BPL131 | HME & LME Standpipe Pump 3 24VDC Control Supply (Q155) Failure | BPP1106VDC01_A | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BPP1106.VS01 | BPP1106VS01_ComFlt_A | BPP1106 - Raw Water Transfer Pump VSD | BR4_Cluster1 |  |  | BPL131 | BPP1106VS01 VSD Communications Fault Alarm | BPP1106VS01_ComFlt_A | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BPP1106.VS01 | BPP1106VS01_Flt_A | BPP1106 - Raw Water Transfer Pump VSD | BR4_Cluster1 |  |  | BPL131 | BPP1106VS01 VSD Fault Alarm | BPP1106VS01_Flt_A | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BPP1106.VS01 | BPP1106VS01SY01_Flt_A | BPP1106 - Raw Water Transfer Pump VSD | BR4_Cluster1 |  |  | BPL131 | BPP1106VS01 Safety Relay Fault Healthy | BPP1106VS01SY01_Flt_A | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BPP1106.VS01 | BPP1106VS01VDC01_A | BPP1106 - Raw Water Transfer Pump VSD | BR4_Cluster1 |  |  | BPL131 | BPP1101VS01 VVVF Drive BPP1106VS01 Control Supply (Q219) Failure | BPP1106VS01VDC01_A | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BPP1107.Sub.CB01 | BPP1107CB01_A | BPP1107 - Feeder Main Cicuit Breaker | BR4_Cluster1 |  |  | BPL131 | HME & LME Standpipe Pump 4 Main Circuit Breaker (Q103) Open | BPP1107CB01_A | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BPP1107 | BPP1107FS08_A | BPP1107 - Standpipe Pump | BR4_Cluster1 |  |  | BPL131 | BPP1107FS08 Pump Flow Switch Low Alarm | BPP1107FS08_A | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BPP1107 | BPP1107FS08_FailStp_A | BPP1107 - Standpipe Pump | BR4_Cluster1 |  |  | BPL131 | BPP1107FS08 Fail to Stop Alarm | BPP1107FS08_FailStp_A | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BPP1107 | BPP1107IS01_A | BPP1107 - Standpipe Pump | BR4_Cluster1 |  |  | BPL131 | BPP1107 Isolator Open Alarm | BPP1107IS01_A | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BPP1107.FieldIO.PT02 | BPP1107PT02_Frz_A | BPP1107 - PT01 Pump Discharge Pressure | BR4_Cluster1 |  |  | BPL131 | BPP1107PT02 Pump Discharge Pressure Transmitter Frozen Alarm | BPP1107PT02_Frz_A | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BPP1107.FieldIO.PT02 | BPP1107PT02_HiHi_A | BPP1107 - PT01 Pump Discharge Pressure | BR4_Cluster1 |  |  | BPL131 | BPP1107PT02 Pump Discharge Pressure High High Alarm | BPP1107PT02_HiHi_A | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BPP1107.FieldIO.PT02 | BPP1107PT02_LoLo_A | BPP1107 - PT01 Pump Discharge Pressure | BR4_Cluster1 |  |  | BPL131 | BPP1107PT02 Pump Discharge Pressure Low Low Alarm | BPP1107PT02_LoLo_A | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BPP1107 | BPP1107THR01_A | BPP1107 - Standpipe Pump | BR4_Cluster1 |  |  | BPL131 | HME & LME Standpipe Pump 4 HME And LME Standpipe Pump 4 (Standby) (K190) | BPP1107THR01_A | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BPP1107.Sub.CB01 | BPP1107TRP01_A | BPP1107 - Feeder Main Cicuit Breaker | BR4_Cluster1 |  |  | BPL131 | BPP1107 Main Circuit Breaker Tripped Alarm | BPP1107TRP01_A | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BPP1107 | BPP1107VDC01_A | BPP1107 - Standpipe Pump | BR4_Cluster1 |  |  | BPL131 | HME & LME Standpipe Pump 4 24VDC Control Supply (Q155) Failure | BPP1107VDC01_A | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BPP1107.VS01 | BPP1107VS01_ComFlt_A | BPP1107 - Raw Water Transfer Pump VSD | BR4_Cluster1 |  |  | BPL131 | BPP1107VS01 VSD Communications Fault Alarm | BPP1107VS01_ComFlt_A | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BPP1107.VS01 | BPP1107VS01_Flt_A | BPP1107 - Raw Water Transfer Pump VSD | BR4_Cluster1 |  |  | BPL131 | BPP1107VS01 VSD Fault Alarm | BPP1107VS01_Flt_A | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BPP1107.VS01 | BPP1107VS01SY01_Flt_A | BPP1107 - Raw Water Transfer Pump VSD | BR4_Cluster1 |  |  | BPL131 | BPP1107VS01 Safety Relay Fault Alarm | BPP1107VS01SY01_Flt_A | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BPP1107.VS01 | BPP1107VS01VDC01_A | BPP1107 - Raw Water Transfer Pump VSD | BR4_Cluster1 |  |  | BPL131 | BPP1101VS01 VVVF Drive BPP1107VS01 Control Supply (Q222) Failure | BPP1107VS01VDC01_A | BS1_Tags
BR4.UTILITIES.WATER.BS1.P3FIREWATER.BPQE2101.Sub.DB01.CB01 | BPQE2101DB01CB01_A | #N/A | BR4_Cluster1 |  |  | BPL131 | NPI & Primary Crusher Fire Water Pump Dist Board Main Circuit Breaker (Q103) Open | BPQE2101DB01CB01_A | BS1_Tags
BR4.UTILITIES.WATER.BS1.P3FIREWATER.BPQE2101.Sub.DB01.CB01 | BPQE2101DB01TRP01_A | #N/A | BR4_Cluster1 |  |  | BPL131 | NPI & Primary Crusher Fire Water Pump Dist Board Main Circuit Breaker Tripped | BPQE2101DB01TRP01_A | BS1_Tags
BR4.UTILITIES.WATER.BS1.P3FIREWATER.BPQE2101.Sub.DB01 | BPQE2101DB01VDC01_A | #N/A | BR4_Cluster1 |  |  | BPL131 | NPI & Primary Crusher Fire Water Pump Dist Board 24VDC Control Supply (Q155) Failure | BPQE2101DB01VDC01_A | BS1_Tags
BR4.UTILITIES.WATER.BS1.P3FIREWATER.BPQE2101.Sub.PN01 | BPQE2101PN01VDC01_A | #N/A | BR4_Cluster1 |  |  | BPL131 | NPI & Primary Crushing Fire Water Container Panel 24VDC Control Supply (Q155) Failure | BPQE2101PN01VDC01_A | BS1_Tags
BR4.UTILITIES.WATER.BS1.P3POTWATER.BPQE2115.Sub.DB01 | BPQE2115MC01VDC01_A | #N/A | BR4_Cluster1 |  |  | BPL131 | Potable Water MCC 24VDC Control Supply (PWTP) (Q155) Failure | BPQE2115MC01VDC01_A | BS1_Tags
BR4.SRV.PWR.BSR131.AC01.CB01 | BSR131AC01CB01_A | BSR131 Switchroom - Air Conditioner 1 Main Circuit Breaker | BR4_Cluster1 |  |  | BPL131 | BSR131 Aircon 1 Main Circuit Breaker (Q103) Open | BSR131AC01CB01_A | BS1_Tags
BR4.SRV.PWR.BSR131.AC01.CB01 | BSR131AC01TRP01_A | BSR131 Switchroom - Air Conditioner 1 Main Circuit Breaker | BR4_Cluster1 |  |  | BPL131 | BSR131 Aircon 1 Main Circuit Breaker Tripped | BSR131AC01TRP01_A | BS1_Tags
BR4.SRV.PWR.BSR131.AC01 | BSR131AC01VDC01_A | BSR131 Switchroom - Air Conditioner 1 | BR4_Cluster1 |  |  | BPL131 | BSR131 Aircon 1 24VDC Control Supply (Q155) Failure | BSR131AC01VDC01_A | BS1_Tags
BR4.SRV.PWR.BSR131.AC02.CB01 | BSR131AC02CB01_A | BSR131 Switchroom - Air Conditioner 2 Main Circuit Breaker | BR4_Cluster1 |  |  | BPL131 | BSR131 Aircon 2 Main Circuit Breaker (Q103) Open | BSR131AC02CB01_A | BS1_Tags
BR4.SRV.PWR.BSR131.AC02.CB01 | BSR131AC02TRP01_A | BSR131 Switchroom - Air Conditioner 2 Main Circuit Breaker | BR4_Cluster1 |  |  | BPL131 | BSR131 Aircon 2 Main Circuit Breaker Tripped | BSR131AC02TRP01_A | BS1_Tags
BR4.SRV.PWR.BSR131.AC02 | BSR131AC02VDC01_A | BSR131 Switchroom - Air Conditioner 2 | BR4_Cluster1 |  |  | BPL131 | BSR131 Aircon 2 24VDC Control Supply (Q155) Failure | BSR131AC02VDC01_A | BS1_Tags
BR4.SRV.PWR.BSR131.BC01.CB01 | BSR131BC01CB01_A | BSR131 Switchroom - Battery Charger 1 Main Circuit Breaker | BR4_Cluster1 |  |  | BPL131 | BSR131 Battery Charger 1 Main Circuit Breaker (Q103) Open | BSR131BC01CB01_A | BS1_Tags
BR4.SRV.PWR.BSR131.BC01.CB01 | BSR131BC01TRP01_A | BSR131 Switchroom - Battery Charger 1 Main Circuit Breaker | BR4_Cluster1 |  |  | BPL131 | BSR131 Battery Charger 1 Main Circuit Breaker Tripped | BSR131BC01TRP01_A | BS1_Tags
BR4.SRV.PWR.BSR131.BC01 | BSR131BC01VDC01_A | BSR131 Switchroom - Battery Charger 1 | BR4_Cluster1 |  |  | BPL131 | BSR131 Battery Charger 1 24VDC Control Supply (Q155) Failure | BSR131BC01VDC01_A | BS1_Tags
BR4.SRV.PWR.BSR131.BC02.BACS | BSR131BC02_BACSComFlt_A | BSR131 Switchroom - Battery Charger 2 Battery Management | BR4_Cluster1 |  |  | BPL131 | BSR131 Battery Charger BC02 BACSComFlt Alarm | BSR131BC02_BACSComFlt_A | BS1_Tags
BR4.SRV.PWR.BSR131.BC02.BACS | BSR131BC02_BACSFlt_A | BSR131 Switchroom - Battery Charger 2 Battery Management | BR4_Cluster1 |  |  | BPL131 | BSR131 Battery Charger BC02 BACSFlt Alarm | BSR131BC02_BACSFlt_A | BS1_Tags
BR4.SRV.PWR.BSR131.BC02.Cordex | BSR131BC02_CordexComFlt_A | BSR131 Switchroom - Battery Charger 2 Controller | BR4_Cluster1 |  |  | BPL131 | BSR131 Battery Charger BC02 CordexComFlt Alarm | BSR131BC02_CordexComFlt_A | BS1_Tags
BR4.SRV.PWR.BSR131.BC02.Cordex | BSR131BC02_CordexFlt_A | BSR131 Switchroom - Battery Charger 2 Controller | BR4_Cluster1 |  |  | BPL131 | BSR131 Battery Charger BC02 CordexFlt Alarm | BSR131BC02_CordexFlt_A | BS1_Tags
BR4.SRV.PWR.BSR131.BC02.CB01 | BSR131BC02CB01_A | BSR131 Switchroom - Battery Charger 2 Main Circuit Breaker | BR4_Cluster1 |  |  | BPL131 | BSR131 Battery Charger 2 Main Circuit Breaker (Q103) Open | BSR131BC02CB01_A | BS1_Tags
BR4.SRV.PWR.BSR131.BC02 | BSR131BC02CB02_A | BSR131 Switchroom - Battery Charger 2 | BR4_Cluster1 |  |  | BPL131 | BSR131 Battery Charger 2 BMC131INC01 110VDC INC01 Tripping Supply Circuit Breaker (Q114) Open | BSR131BC02CB02_A | BS1_Tags
BR4.SRV.PWR.BSR131.BC02 | BSR131BC02CB03_A | BSR131 Switchroom - Battery Charger 2 | BR4_Cluster1 |  |  | BPL131 | BSR131 Battery Charger 2 BMC131INC02 110VDC INC02 Tripping Supply Circuit Breaker (Q117) Open | BSR131BC02CB03_A | BS1_Tags
BR4.SRV.PWR.BSR131.BC02 | BSR131BC02CB04_A | BSR131 Switchroom - Battery Charger 2 | BR4_Cluster1 |  |  | BPL131 | BSR131 Battery Charger 2 BMC131INC03 110VDC INC03 Tripping Supply Circuit Breaker (Q120) Open | BSR131BC02CB04_A | BS1_Tags
BR4.SRV.PWR.BSR131.BC02 | BSR131BC02CB05_A | BSR131 Switchroom - Battery Charger 2 | BR4_Cluster1 |  |  | BPL131 | BSR131 Battery Charger 2 RSP01 110VDC Tripping Supply Circuit Breaker (Q123) Open | BSR131BC02CB05_A | BS1_Tags
BR4.SRV.PWR.BSR131.BC02.CB01 | BSR131BC02TRP01_A | BSR131 Switchroom - Battery Charger 2 Main Circuit Breaker | BR4_Cluster1 |  |  | BPL131 | BSR131 Battery Charger 2 Main Circuit Breaker Tripped | BSR131BC02TRP01_A | BS1_Tags
BR4.SRV.PWR.BSR131.BC02 | BSR131BC02VDC01_A | BSR131 Switchroom - Battery Charger 2 | BR4_Cluster1 |  |  | BPL131 | BSR131 Battery Charger 2 24VDC Control Supply (Q155) Failure | BSR131BC02VDC01_A | BS1_Tags
BR4.SRV.PWR.BSR131.BC02 | BSR131BC02VDC02_A | BSR131 Switchroom - Battery Charger 2 | BR4_Cluster1 |  |  | BPL131 | BSR131 Battery Charger 2 Battery Charger 110VDC Tripping Supply (K112) Failure | BSR131BC02VDC02_A | BS1_Tags
BR4.SRV.PWR.BSR131.DB01.CB01 | BSR131DB01CB01_A | DB01 - Small Power & Lighting Distribution Board Main Circuit Breaker | BR4_Cluster1 |  |  | BPL131 | BSR131 LSP Dist Board Main Circuit Breaker (Q103) Open | BSR131DB01CB01_A | BS1_Tags
BR4.SRV.PWR.BSR131.DB01.CB01 | BSR131DB01TRP01_A | DB01 - Small Power & Lighting Distribution Board Main Circuit Breaker | BR4_Cluster1 |  |  | BPL131 | BSR131 LSP Dist Board Main Circuit Breaker Tripped | BSR131DB01TRP01_A | BS1_Tags
BR4.SRV.PWR.BSR131.DB01 | BSR131DB01VDC01_A | DB01 - Small Power & Lighting Distribution Board | BR4_Cluster1 |  |  | BPL131 | BSR131 LSP Dist Board 24VDC Control Supply (Q155) Failure | BSR131DB01VDC01_A | BS1_Tags
BR4.SRV.PWR.BSR131.DB01 | BSR131DB01XS01_A | DB01 - Small Power & Lighting Distribution Board | BR4_Cluster1 |  |  | BPL131 | BSR131DB01 Surge Protection (SD107) Alarm | BSR131DB01XS01_A | BS1_Tags
BR4.SRV.PWR.BSR131.DB02.CB01 | BSR131DB02CB01_A | DB02 - Small Power & Lighting Distribution Board Main Circuit Breaker | BR4_Cluster1 |  |  | BPL131 | BSR131 415V Dewatering Laydown Lighting Dist Board Main Circuit Breaker (Q103) Open | BSR131DB02CB01_A | BS1_Tags
BR4.SRV.PWR.BSR131.DB02.CB01 | BSR131DB02TRP01_A | DB02 - Small Power & Lighting Distribution Board Main Circuit Breaker | BR4_Cluster1 |  |  | BPL131 | BSR131 415V Dewatering Laydown Lighting Dist Board Main Circuit Breaker Tripped | BSR131DB02TRP01_A | BS1_Tags
BR4.SRV.PWR.BSR131.DB02 | BSR131DB02VDC01_A | DB02 - Small Power & Lighting Distribution Board | BR4_Cluster1 |  |  | BPL131 | BSR131 415V Dewatering Laydown Lighting Dist Board 24VDC Control Supply (Q155) Failure | BSR131DB02VDC01_A | BS1_Tags
BR4.SRV.PWR.BSR131.DB03.CB01 | BSR131DB03CB01_A | DB03 - Small Power & Lighting Distribution Board Main Circuit Breaker | BR4_Cluster1 |  |  | BPL131 | BSR131 415V HME Refuel Water Recycle Dist Board Main Circuit Breaker (Q103) Open | BSR131DB03CB01_A | BS1_Tags
BR4.SRV.PWR.BSR131.DB03.CB01 | BSR131DB03TRP01_A | DB03 - Small Power & Lighting Distribution Board Main Circuit Breaker | BR4_Cluster1 |  |  | BPL131 | BSR131 415V HME Refuel Water Recycle Dist Board Main Circuit Breaker Tripped | BSR131DB03TRP01_A | BS1_Tags
BR4.SRV.PWR.BSR131.DB03 | BSR131DB03VDC01_A | DB03 - Small Power & Lighting Distribution Board | BR4_Cluster1 |  |  | BPL131 | BSR131 415V HME Refuel Water Recycle Dist Board 24VDC Control Supply (Q155) Failure | BSR131DB03VDC01_A | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop01 | BSR131DX01DIO1PLM0_ComFlt_A | BPL131 Drop 1 - BTY1502DX01 | BR4_Cluster1 |  |  | BPL131 | BSR131DX01 CRA Comms Module 0 Communications Fault Alarm | BSR131DX01DIO1PLM0_ComFlt_A | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop01 | BSR131DX01DIO1PLM0_Flt_A | BPL131 Drop 1 - BTY1502DX01 | BR4_Cluster1 |  |  | BPL131 | BSR131DX01 CRA Comms Module 0 Fault Alarm | BSR131DX01DIO1PLM0_Flt_A | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop01 | BSR131DX01DIO1PLM1_Flt_A | BPL131 Drop 1 - BTY1502DX01 | BR4_Cluster1 |  |  | BPL131 | BSR131DX01 DI Module 1 Fault Alarm | BSR131DX01DIO1PLM1_Flt_A | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop01 | BSR131DX01DIO1PLM1_Grp1Flt_A | BPL131 Drop 1 - BTY1502DX01 | BR4_Cluster1 |  |  | BPL131 | BSR131DX01 DI Module 1 Group 1 Fault Alarm | BSR131DX01DIO1PLM1_Grp1Flt_A | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop01 | BSR131DX01DIO1PLM1_Grp2Flt_A | BPL131 Drop 1 - BTY1502DX01 | BR4_Cluster1 |  |  | BPL131 | BSR131DX01 DI Module 1 Group 2 Fault Alarm | BSR131DX01DIO1PLM1_Grp2Flt_A | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop01 | BSR131DX01DIO1PLM2_Flt_A | BPL131 Drop 1 - BTY1502DX01 | BR4_Cluster1 |  |  | BPL131 | BSR131DX01 DI Module 2 Fault Alarm | BSR131DX01DIO1PLM2_Flt_A | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop01 | BSR131DX01DIO1PLM2_Grp1Flt_A | BPL131 Drop 1 - BTY1502DX01 | BR4_Cluster1 |  |  | BPL131 | BSR131DX01 DI Module 2 Group 1 Fault Alarm | BSR131DX01DIO1PLM2_Grp1Flt_A | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop01 | BSR131DX01DIO1PLM2_Grp2Flt_A | BPL131 Drop 1 - BTY1502DX01 | BR4_Cluster1 |  |  | BPL131 | BSR131DX01 DI Module 2 Group 2 Fault Alarm | BSR131DX01DIO1PLM2_Grp2Flt_A | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop01 | BSR131DX01DIO1PLM3_Flt_A | BPL131 Drop 1 - BTY1502DX01 | BR4_Cluster1 |  |  | BPL131 | BSR131DX01 DI Module 3 Fault Alarm | BSR131DX01DIO1PLM3_Flt_A | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop01 | BSR131DX01DIO1PLM3_Grp1Flt_A | BPL131 Drop 1 - BTY1502DX01 | BR4_Cluster1 |  |  | BPL131 | BSR131DX01 DI Module 3 Group 1 Fault Alarm | BSR131DX01DIO1PLM3_Grp1Flt_A | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop01 | BSR131DX01DIO1PLM3_Grp2Flt_A | BPL131 Drop 1 - BTY1502DX01 | BR4_Cluster1 |  |  | BPL131 | BSR131DX01 DI Module 3 Group 2 Fault Alarm | BSR131DX01DIO1PLM3_Grp2Flt_A | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop01 | BSR131DX01DIO1PLM4_Flt_A | BPL131 Drop 1 - BTY1502DX01 | BR4_Cluster1 |  |  | BPL131 | BSR131DX01 DI Module 4 Fault Alarm | BSR131DX01DIO1PLM4_Flt_A | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop01 | BSR131DX01DIO1PLM4_Grp1Flt_A | BPL131 Drop 1 - BTY1502DX01 | BR4_Cluster1 |  |  | BPL131 | BSR131DX01 DI Module 4 Group 1 Fault Alarm | BSR131DX01DIO1PLM4_Grp1Flt_A | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop01 | BSR131DX01DIO1PLM4_Grp2Flt_A | BPL131 Drop 1 - BTY1502DX01 | BR4_Cluster1 |  |  | BPL131 | BSR131DX01 DI Module 4 Group 2 Fault Alarm | BSR131DX01DIO1PLM4_Grp2Flt_A | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop01 | BSR131DX01DIO1PLM5_Flt_A | BPL131 Drop 1 - BTY1502DX01 | BR4_Cluster1 |  |  | BPL131 | BSR131DX01 DI Module 5 Fault Alarm | BSR131DX01DIO1PLM5_Flt_A | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop01 | BSR131DX01DIO1PLM5_Grp1Flt_A | BPL131 Drop 1 - BTY1502DX01 | BR4_Cluster1 |  |  | BPL131 | BSR131DX01 DI Module 5 Group 1 Fault Alarm | BSR131DX01DIO1PLM5_Grp1Flt_A | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop01 | BSR131DX01DIO1PLM5_Grp2Flt_A | BPL131 Drop 1 - BTY1502DX01 | BR4_Cluster1 |  |  | BPL131 | BSR131DX01 DI Module 5 Group 2 Fault Alarm | BSR131DX01DIO1PLM5_Grp2Flt_A | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop01 | BSR131DX01DIO1PLM6_Flt_A | BPL131 Drop 1 - BTY1502DX01 | BR4_Cluster1 |  |  | BPL131 | BSR131DX01 DI Module 6 Fault Alarm | BSR131DX01DIO1PLM6_Flt_A | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop01 | BSR131DX01DIO1PLM6_Grp1Flt_A | BPL131 Drop 1 - BTY1502DX01 | BR4_Cluster1 |  |  | BPL131 | BSR131DX01 DI Module 6 Group 1 Fault Alarm | BSR131DX01DIO1PLM6_Grp1Flt_A | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop01 | BSR131DX01DIO1PLM6_Grp2Flt_A | BPL131 Drop 1 - BTY1502DX01 | BR4_Cluster1 |  |  | BPL131 | BSR131DX01 DI Module 6 Group 2 Fault Alarm | BSR131DX01DIO1PLM6_Grp2Flt_A | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop01 | BSR131DX01DIO1PLM7_Flt_A | BPL131 Drop 1 - BTY1502DX01 | BR4_Cluster1 |  |  | BPL131 | BSR131DX01 DI Module 7 Fault Alarm | BSR131DX01DIO1PLM7_Flt_A | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop01 | BSR131DX01DIO1PLM7_Grp1Flt_A | BPL131 Drop 1 - BTY1502DX01 | BR4_Cluster1 |  |  | BPL131 | BSR131DX01 DI Module 7 Group 1 Fault Alarm | BSR131DX01DIO1PLM7_Grp1Flt_A | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop01 | BSR131DX01DIO1PLM7_Grp2Flt_A | BPL131 Drop 1 - BTY1502DX01 | BR4_Cluster1 |  |  | BPL131 | BSR131DX01 DI Module 7 Group 2 Fault Alarm | BSR131DX01DIO1PLM7_Grp2Flt_A | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop01 | BSR131DX01DIO1PLM8_Flt_A | BPL131 Drop 1 - BTY1502DX01 | BR4_Cluster1 |  |  | BPL131 | BSR131DX01 DO Module 8 Fault Alarm | BSR131DX01DIO1PLM8_Flt_A | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop01 | BSR131DX01VDC01_A | BPL131 Drop 1 - BTY1502DX01 | BR4_Cluster1 |  |  | BPL131 | BSR131 DIO Box 1 DX01 24VDC Control Supply Healthy (Q110) Failure | BSR131DX01VDC01_A | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop01 | BSR131DX01VDC02_A | BPL131 Drop 1 - BTY1502DX01 | BR4_Cluster1 |  |  | BPL131 | BSR131 DIO Box 1 DX01 24VDC Output Module Control Supply (Q170) Failure | BSR131DX01VDC02_A | BS1_Tags
BR4.SRV.PWR.BSR131.UP01 | BSR131DX01VDC03_A | UP01 - BSR131 Uninterruptable Power Supply 1 | BR4_Cluster1 |  |  | BPL131 | BSR131 DIO Box 1 BSR131UP01 24VDC Control Supply (Q254) Failure | BSR131DX01VDC03_A | BS1_Tags
BR4.SRV.PWR.BSR131.BC01 | BSR131DX01VDC04_A | BSR131 Switchroom - Battery Charger 1 | BR4_Cluster1 |  |  | BPL131 | BSR131 DIO Box 1 BSR131BC01DB01 24VDC Control Supply (Q257) Failure | BSR131DX01VDC04_A | BS1_Tags
BR4.SRV.PWR.BSR131.BC02 | BSR131DX01VDC05_A | BSR131 Switchroom - Battery Charger 2 | BR4_Cluster1 |  |  | BPL131 | BSR131 DIO Box 1 BSR131BC02DB01 24VDC Control Supply (Q260) Failure | BSR131DX01VDC05_A | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.DB01 | BSR131DX01VDC06_A | UP01 - BSR131 UPS Distribution Board 1 | BR4_Cluster1 |  |  | BPL131 | BSR131 DIO Box 1 BSR131UP01DB01 24VDC Control Supply (Q263) Failure | BSR131DX01VDC06_A | BS1_Tags
BR4.SRV.PWR.BSR131 | BSR131DX01VDC07_A | BSR131 Switchroom | BR4_Cluster1 |  |  | BPL131 | BSR131 DIO Box 1 Misc Switchroom Alarms 24VDC Control Supply (Q266) Failure | BSR131DX01VDC07_A | BS1_Tags
BR4.SRV.PWR.BSR131 | BSR131DX01XS01_A | BSR131 Switchroom | BR4_Cluster1 |  |  | BPL131 | BSR131DX01 24VDC Power Supply 1 Fail Alarm | BSR131DX01XS01_A | BS1_Tags
BR4.SRV.PWR.BSR131 | BSR131DX01XS02_A | BSR131 Switchroom | BR4_Cluster1 |  |  | BPL131 | BSR131DX01 24VDC Power Supply 2 Fail Alarm | BSR131DX01XS02_A | BS1_Tags
BR4.SRV.PWR.BSR131 | BSR131FIP01IS01_A | BSR131 Switchroom | BR4_Cluster1 |  |  | BPL131 | BSR131 Fire Panel Fire Panel Isolated Open | BSR131FIP01IS01_A | BS1_Tags
BR4.SRV.PWR.BSR131 | BSR131FIP01XS01_A | BSR131 Switchroom | BR4_Cluster1 |  |  | BPL131 | BSR131 Fire Panel Fault Alarm | BSR131FIP01XS01_A | BS1_Tags
BR4.SRV.PWR.BSR131 | BSR131FIP01XS02_A | BSR131 Switchroom | BR4_Cluster1 |  |  | BPL131 | BSR131 Fire Panel Unhealthy Alarm | BSR131FIP01XS02_A | BS1_Tags
BR4.SRV.PWR.BSR131 | BSR131FIP01XS03_A | BSR131 Switchroom | BR4_Cluster1 |  |  | BPL131 | BSR131 Fire Panel Gas Discharged Alarm | BSR131FIP01XS03_A | BS1_Tags
BR4.SRV.PWR.BSR131.NEP01 | BSR131NEP01CB01_A | NEP01 - BSR131 Network Equipment Panel 1 | BR4_Cluster1 |  |  | BPL131 | BSR131 Network Panel 1 NEP Primary PDU Circuit Breaker (Q130) Open | BSR131NEP01CB01_A | BS1_Tags
BR4.SRV.PWR.BSR131.NEP01 | BSR131NEP01CB02_A | NEP01 - BSR131 Network Equipment Panel 1 | BR4_Cluster1 |  |  | BPL131 | BSR131 Network Panel 1 NEP Secondary PDU Circuit Breaker (Q180) Open | BSR131NEP01CB02_A | BS1_Tags
BR4.SRV.PWR.BSR131 | BSR131PB01_A | BSR131 Switchroom | BR4_Cluster1 |  |  | BPL131 | NPI Hub Substation Shutdown Pushbutton (SESP) Activated Alarm | BSR131PB01_A | BS1_Tags
BR4.SRV.PWR.BSR131 | BSR131PN01PS01_A | BSR131 Switchroom | BR4_Cluster1 |  |  | BPL131 | BSR131PN01 Switchroom Pressurisation Fan Filter Blocked Alarm | BSR131PN01PS01_A | BS1_Tags
BR4.SRV.PWR.BSR131 | BSR131PN01TS01_A | BSR131 Switchroom | BR4_Cluster1 |  |  | BPL131 | Switchroom Control Panel Airlock High Temperature | BSR131PN01TS01_A | BS1_Tags
BR4.SRV.PWR.BSR131 | BSR131PN01XS01_A | BSR131 Switchroom | BR4_Cluster1 |  |  | BPL131 | BSR131PN01 Air Conditioner Fault Alarm | BSR131PN01XS01_A | BS1_Tags
BR4.SRV.PWR.BSR131 | BSR131PN01XS02_A | BSR131 Switchroom | BR4_Cluster1 |  |  | BPL131 | BSR131 Switchroom Control Panel Air Conditioner Filter Blocked Alarm | BSR131PN01XS02_A | BS1_Tags
BR4.SRV.PWR.BSR131 | BSR131PN01XS03_A | BSR131 Switchroom | BR4_Cluster1 |  |  | BPL131 | BSR131PN01 Air Con 1 Fault Alarm | BSR131PN01XS03_A | BS1_Tags
BR4.SRV.PWR.BSR131 | BSR131PN01XS04_A | BSR131 Switchroom | BR4_Cluster1 |  |  | BPL131 | BSR131 Switchroom Control Panel Air Con 2 Healthy | BSR131PN01XS04_A | BS1_Tags
BR4.SRV.PWR.BSR131 | BSR131PN01XS05_A | BSR131 Switchroom | BR4_Cluster1 |  |  | BPL131 | BSR131PN01 Switchroom Humidity Alarm | BSR131PN01XS05_A | BS1_Tags
BR4.SRV.PWR.BSR131 | BSR131PN01XS06_A | BSR131 Switchroom | BR4_Cluster1 |  |  | BPL131 | NPI Hub Switchroom Control Panel 1 Air Conditioner 6 - Airlock Fault Alarm | BSR131PN01XS06_A | BS1_Tags
BR4.SRV.PWR.BSR131 | BSR131PN01XS07_A | BSR131 Switchroom | BR4_Cluster1 |  |  | BPL131 | NPI Hub Switchroom Control Panel 1 Air Conditioner 7 - Airlock Fault Alarm | BSR131PN01XS07_A | BS1_Tags
BR4.SRV.PWR.BSR131.UP01 | BSR131UP01_ComFlt_A | UP01 - BSR131 Uninterruptable Power Supply 1 | BR4_Cluster1 |  |  | BPL131 | BSR131 UPS Communications Fault Alarm Alarm | BSR131UP01_ComFlt_A | BS1_Tags
BR4.SRV.PWR.BSR131.UP01 | BSR131UP01_Flt_A | UP01 - BSR131 Uninterruptable Power Supply 1 | BR4_Cluster1 |  |  | BPL131 | BSR131 UPS System Fault Alarm Alarm | BSR131UP01_Flt_A | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.CB01 | BSR131UP01CB01_A | #N/A | BR4_Cluster1 |  |  | BPL131 | BSR131 UPS Main Circuit Breaker (Q103) Open | BSR131UP01CB01_A | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.DB01 | BSR131UP01DB01B1_A | UP01 - BSR131 UPS Distribution Board 1 | BR4_Cluster1 |  |  | BPL131 | NEP130 240VAC Primary UPS Circuit Breaker Open Alarm | BSR131UP01DB01B1_A | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.DB01 | BSR131UP01DB01B2_A | UP01 - BSR131 UPS Distribution Board 1 | BR4_Cluster1 |  |  | BPL131 | DX03 240VAC UPS Circuit Breaker Open Alarm | BSR131UP01DB01B2_A | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.DB01 | BSR131UP01DB01B3_A | UP01 - BSR131 UPS Distribution Board 1 | BR4_Cluster1 |  |  | BPL131 | BSR131FIP01 Fire Panel 240VAC UPS Circuit Breaker Open Alarm | BSR131UP01DB01B3_A | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.DB01 | BSR131UP01DB01B4_A | UP01 - BSR131 UPS Distribution Board 1 | BR4_Cluster1 |  |  | BPL131 | BSR131FSS01PN01 Supression Control Panel Breaker Open Alarm | BSR131UP01DB01B4_A | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.DB01 | BSR131UP01DB01R1_A | UP01 - BSR131 UPS Distribution Board 1 | BR4_Cluster1 |  |  | BPL131 | DX01 Primary 240VAC UPS Circuit Breaker Open Alarm | BSR131UP01DB01R1_A | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.DB01 | BSR131UP01DB01R2_A | UP01 - BSR131 UPS Distribution Board 1 | BR4_Cluster1 |  |  | BPL131 | NEP130 240VAC Secondary UPS Circuit Breaker Open Alarm | BSR131UP01DB01R2_A | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.DB01 | BSR131UP01DB01R3_A | UP01 - BSR131 UPS Distribution Board 1 | BR4_Cluster1 |  |  | BPL131 | DX04 240VAC UPS Circuit Breaker Open Alarm | BSR131UP01DB01R3_A | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.DB01 | BSR131UP01DB01R4_A | UP01 - BSR131 UPS Distribution Board 1 | BR4_Cluster1 |  |  | BPL131 | BSR131VES01 VESDA Fire Detection Panel Breaker Open Alarm | BSR131UP01DB01R4_A | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.DB01 | BSR131UP01DB01R5_A | UP01 - BSR131 UPS Distribution Board 1 | BR4_Cluster1 |  |  | BPL131 | BTY1502AX01 240VAC UPS Circuit Breaker Open Alarm | BSR131UP01DB01R5_A | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.DB01 | BSR131UP01DB01W1_A | UP01 - BSR131 UPS Distribution Board 1 | BR4_Cluster1 |  |  | BPL131 | DX01 Secondary 240VAC UPS Circuit Breaker Open Alarm | BSR131UP01DB01W1_A | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.DB01 | BSR131UP01DB01W2_A | UP01 - BSR131 UPS Distribution Board 1 | BR4_Cluster1 |  |  | BPL131 | DX02 240VAC UPS Circuit Breaker Open Alarm | BSR131UP01DB01W2_A | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.DB01 | BSR131UP01DB01W3_A | UP01 - BSR131 UPS Distribution Board 1 | BR4_Cluster1 |  |  | BPL131 | HVAC Panel 240VAC UPS Circuit Breaker Open Alarm | BSR131UP01DB01W3_A | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.DB01 | BSR131UP01DB01W4_A | UP01 - BSR131 UPS Distribution Board 1 | BR4_Cluster1 |  |  | BPL131 | Cardax 240VAC UPS Circuit Breaker Open Alarm | BSR131UP01DB01W4_A | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.DB01 | BSR131UP01DB01W5_A | UP01 - BSR131 UPS Distribution Board 1 | BR4_Cluster1 |  |  | BPL131 | BPQE2115MC01 Potable Water 240VAC UPS Circuit Breaker Alarm | BSR131UP01DB01W5_A | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.DB01 | BSR131UP01DB01XS01_A | UP01 - BSR131 UPS Distribution Board 1 | BR4_Cluster1 |  |  | BPL131 | BSR131UP01DB01 Surge Protection (SD106) Alarm | BSR131UP01DB01XS01_A | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.CB01 | BSR131UP01TRP01_A | #N/A | BR4_Cluster1 |  |  | BPL131 | BSR131 UPS Main Circuit Breaker Tripped | BSR131UP01TRP01_A | BS1_Tags
BR4.SRV.PWR.BSR131.UP01 | BSR131UP01VDC01_A | UP01 - BSR131 Uninterruptable Power Supply 1 | BR4_Cluster1 |  |  | BPL131 | BSR131 UPS 24VDC Control Supply (Q155) Failure | BSR131UP01VDC01_A | BS1_Tags
BR4.SRV.PWR.BSR131.UP01 | BSR131UP01XS01_A | UP01 - BSR131 Uninterruptable Power Supply 1 | BR4_Cluster1 |  |  | BPL131 | BSR131 UPS Surge Filter Alarm | BSR131UP01XS01_A | BS1_Tags
BR4.SRV.PWR.BSR131.UP01 | BSR131UP01ZS01_A | UP01 - BSR131 Uninterruptable Power Supply 1 | BR4_Cluster1 |  |  | BPL131 | BSR131 UPS UPS in Normal Mode | BSR131UP01ZS01_A | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BSTD1106.FieldIO.FT03 | BSTD1106FT03_Frz_A | BSTD1106 - FT03 LME Standpipe Flowmeter | BR4_Cluster1 |  |  | BPL131 | BSTD1106FT03 Flow Transmitter Frozen Alarm | BSTD1106FT03_Frz_A | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BSTD1106.FieldIO.FT03 | BSTD1106FT03_Hi_A | BSTD1106 - FT03 LME Standpipe Flowmeter | BR4_Cluster1 |  |  | BPL131 | BSTD1106FT03 Flow High Alarm | BSTD1106FT03_Hi_A | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BSTD1106.FieldIO.FT03 | BSTD1106FT03_Rtn_A | BSTD1106 - FT03 LME Standpipe Flowmeter | BR4_Cluster1 |  |  | BPL131 | BPP1103FT03 Pump Flow Detected with Valve Closed Alarm | BSTD1106FT03_Rtn_A | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BSTD1106.FV03 | BSTD1106FV03_ExcRun_A | BSTD1106 - FV03 LME Standpipe Flow Valve | BR4_Cluster1 |  |  | BPL131 | West Turkeys Nest LME Standpipe Valve Excessive Open Alarm | BSTD1106FV03_ExcRun_A | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BSTD1106.FV03 | BSTD1106FV03_FTC_A | BSTD1106 - FV03 LME Standpipe Flow Valve | BR4_Cluster1 |  |  | BPL131 | West Turkeys Nest LME Standpipe Valve Fail to Close Alarm | BSTD1106FV03_FTC_A | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BSTD1106.FV03 | BSTD1106FV03_FTO_A | BSTD1106 - FV03 LME Standpipe Flow Valve | BR4_Cluster1 |  |  | BPL131 | West Turkeys Nest LME Standpipe Valve Fail to Open Alarm | BSTD1106FV03_FTO_A | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BSTD1106.FV03 | BSTD1106FV03_LmtFlt_A | BSTD1106 - FV03 LME Standpipe Flow Valve | BR4_Cluster1 |  |  | BPL131 | West Turkeys Nest LME Standpipe Valve Dual Limit Alarm | BSTD1106FV03_LmtFlt_A | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BSTD1106.FV03 | BSTD1106FV03_LocFlt_A | BSTD1106 - FV03 LME Standpipe Flow Valve | BR4_Cluster1 |  |  | BPL131 | West Turkeys Nest LME Standpipe Valve Left in Local Alarm | BSTD1106FV03_LocFlt_A | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BSTD1106.FV03.FieldIO.CB01 | BSTD1106FV03CB01_A | BSTD1106 - FV03 Cicuit Breaker | BR4_Cluster1 |  |  | BPL131 | West Turkeys Nest LME Standpipe 240VAC Flow Valve Power Circuit Breaker Open | BSTD1106FV03CB01_A | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BSTD1106.FV03 | BSTD1106FV03XS01_A | BSTD1106 - FV03 LME Standpipe Flow Valve | BR4_Cluster1 |  |  | BPL131 | West Turkeys Nest LME Standpipe Valve Unhealthy Alarm | BSTD1106FV03XS01_A | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BSTD1107 | BSTD1107FT02_Frz_A | BSTD1107 - HME Standpipe | BR4_Cluster1 |  |  | BPL131 | BSTD1107FT02 Flow Transmitter Frozen Alarm | BSTD1107FT02_Frz_A | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BSTD1107 | BSTD1107FT02_Hi_A | BSTD1107 - HME Standpipe | BR4_Cluster1 |  |  | BPL131 | BSTD1107FT02 Flow High Alarm | BSTD1107FT02_Hi_A | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BSTD1107 | BSTD1107FT02_Rtn_A | BSTD1107 - HME Standpipe | BR4_Cluster1 |  |  | BPL131 | BSTD1107FT02 Flow Detected with Valve Closed Alarm | BSTD1107FT02_Rtn_A | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BSTD1107.FV02 | BSTD1107FV02_ExcRun_A | BSTD1107 - FV02 HME Standpipe Flow Valve | BR4_Cluster1 |  |  | BPL131 | West Turkeys Nest HME Standpipe Valve Excessive Open Alarm | BSTD1107FV02_ExcRun_A | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BSTD1107.FV02 | BSTD1107FV02_FTC_A | BSTD1107 - FV02 HME Standpipe Flow Valve | BR4_Cluster1 |  |  | BPL131 | West Turkeys Nest HME Standpipe Valve Fail to Close Alarm | BSTD1107FV02_FTC_A | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BSTD1107.FV02 | BSTD1107FV02_FTO_A | BSTD1107 - FV02 HME Standpipe Flow Valve | BR4_Cluster1 |  |  | BPL131 | West Turkeys Nest HME Standpipe Valve Fail to Open Alarm | BSTD1107FV02_FTO_A | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BSTD1107.FV02 | BSTD1107FV02_LmtFlt_A | BSTD1107 - FV02 HME Standpipe Flow Valve | BR4_Cluster1 |  |  | BPL131 | West Turkeys Nest HME Standpipe Valve Dual Limit Alarm | BSTD1107FV02_LmtFlt_A | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BSTD1107.FV02 | BSTD1107FV02_LocFlt_A | BSTD1107 - FV02 HME Standpipe Flow Valve | BR4_Cluster1 |  |  | BPL131 | West Turkeys Nest HME Standpipe Valve Left in Local Alarm | BSTD1107FV02_LocFlt_A | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BSTD1107.FV02.FieldIO.CB01 | BSTD1107FV02CB01_A | BSTD1107 - FV02 Cicuit Breaker | BR4_Cluster1 |  |  | BPL131 | West Turkeys Nest HME Standpipe 240VAC Flow Valve Power Circuit Breaker Open | BSTD1107FV02CB01_A | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BSTD1107.FV02 | BSTD1107FV02XS01_A | BSTD1107 - FV02 HME Standpipe Flow Valve | BR4_Cluster1 |  |  | BPL131 | West Turkeys Nest HME Standpipe Valve Unhealthy Alarm | BSTD1107FV02XS01_A | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop04 | BTK2101DX04DIO1PLM0_ComFlt_A | BPL131 Drop 4 - BTK2101DX04 | BR4_Cluster1 |  |  | BPL131 | BTK2101DX04 CRA Comms Module 0 Communications Fault Alarm | BTK2101DX04DIO1PLM0_ComFlt_A | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop04 | BTK2101DX04DIO1PLM0_Flt_A | BPL131 Drop 4 - BTK2101DX04 | BR4_Cluster1 |  |  | BPL131 | BTK2101DX04 CRA Comms Module 0 Fault Alarm | BTK2101DX04DIO1PLM0_Flt_A | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop04 | BTK2101DX04DIO1PLM1_Flt_A | BPL131 Drop 4 - BTK2101DX04 | BR4_Cluster1 |  |  | BPL131 | BTK2101DX04 DI Module 1 Fault Alarm | BTK2101DX04DIO1PLM1_Flt_A | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop04 | BTK2101DX04DIO1PLM1_Grp1Flt_A | BPL131 Drop 4 - BTK2101DX04 | BR4_Cluster1 |  |  | BPL131 | BTK2101DX04 DI Module 1 Group 1 Fault Alarm | BTK2101DX04DIO1PLM1_Grp1Flt_A | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop04 | BTK2101DX04DIO1PLM1_Grp2Flt_A | BPL131 Drop 4 - BTK2101DX04 | BR4_Cluster1 |  |  | BPL131 | BTK2101DX04 DI Module 1 Group 2 Fault Alarm | BTK2101DX04DIO1PLM1_Grp2Flt_A | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop04 | BTK2101DX04DIO1PLM3_Ch00Flt_A | BPL131 Drop 4 - BTK2101DX04 | BR4_Cluster1 |  |  | BPL131 | BTK2101DX04 AHI Module 3 Channel 0 Fault Alarm | BTK2101DX04DIO1PLM3_Ch00Flt_A | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop04 | BTK2101DX04DIO1PLM3_Ch01Flt_A | BPL131 Drop 4 - BTK2101DX04 | BR4_Cluster1 |  |  | BPL131 | BTK2101DX04 AHI Module 3 Channel 1 Fault Alarm | BTK2101DX04DIO1PLM3_Ch01Flt_A | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop04 | BTK2101DX04DIO1PLM3_Ch02Flt_A | BPL131 Drop 4 - BTK2101DX04 | BR4_Cluster1 |  |  | BPL131 | BTK2101DX04 AHI Module 3 Channel 2 Fault Alarm | BTK2101DX04DIO1PLM3_Ch02Flt_A | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop04 | BTK2101DX04DIO1PLM3_Ch03Flt_A | BPL131 Drop 4 - BTK2101DX04 | BR4_Cluster1 |  |  | BPL131 | BTK2101DX04 AHI Module 3 Channel 3 Fault Alarm | BTK2101DX04DIO1PLM3_Ch03Flt_A | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop04 | BTK2101DX04DIO1PLM3_Ch04Flt_A | BPL131 Drop 4 - BTK2101DX04 | BR4_Cluster1 |  |  | BPL131 | BTK2101DX04 AHI Module 3 Channel 4 Fault Alarm | BTK2101DX04DIO1PLM3_Ch04Flt_A | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop04 | BTK2101DX04DIO1PLM3_Ch05Flt_A | BPL131 Drop 4 - BTK2101DX04 | BR4_Cluster1 |  |  | BPL131 | BTK2101DX04 AHI Module 3 Channel 5 Fault Alarm | BTK2101DX04DIO1PLM3_Ch05Flt_A | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop04 | BTK2101DX04DIO1PLM3_Ch06Flt_A | BPL131 Drop 4 - BTK2101DX04 | BR4_Cluster1 |  |  | BPL131 | BTK2101DX04 AHI Module 3 Channel 6 Fault Alarm | BTK2101DX04DIO1PLM3_Ch06Flt_A | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop04 | BTK2101DX04DIO1PLM3_Ch07Flt_A | BPL131 Drop 4 - BTK2101DX04 | BR4_Cluster1 |  |  | BPL131 | BTK2101DX04 AHI Module 3 Channel 7 Fault Alarm | BTK2101DX04DIO1PLM3_Ch07Flt_A | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop04 | BTK2101DX04DIO1PLM3_Flt_A | BPL131 Drop 4 - BTK2101DX04 | BR4_Cluster1 |  |  | BPL131 | BTK2101DX04 AHI Module 3 Fault Alarm | BTK2101DX04DIO1PLM3_Flt_A | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop04 | BTK2101DX04VDC01_A | BPL131 Drop 4 - BTK2101DX04 | BR4_Cluster1 |  |  | BPL131 | NPI Fire Water Tank DIO Box 1 24VDC Output Control Supply (Q143) Failure | BTK2101DX04VDC01_A | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop04 | BTK2101DX04VDC02_A | BPL131 Drop 4 - BTK2101DX04 | BR4_Cluster1 |  |  | BPL131 | NPI Fire Water Tank DIO Box 1 24VDC GW1 Control Supply (Q157) Failure | BTK2101DX04VDC02_A | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop04 | BTK2101DX04VDC03_A | BPL131 Drop 4 - BTK2101DX04 | BR4_Cluster1 |  |  | BPL131 | NPI Fire Water Tank DIO Box 1 24VDC Instrument Control Supply (Q164) Failure | BTK2101DX04VDC03_A | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop04 | BTK2101DX04VDC04_A | BPL131 Drop 4 - BTK2101DX04 | BR4_Cluster1 |  |  | BPL131 | NPI Fire Water Tank DIO Box 1 24VDC Transmitter Control Supply (Q168) Failure | BTK2101DX04VDC04_A | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop04 | BTK2101DX04VDC05_A | BPL131 Drop 4 - BTK2101DX04 | BR4_Cluster1 |  |  | BPL131 | NPI Fire Water Tank DIO Box 1 24VDC BTK2101DX04 Control Supply (Q172) Failure | BTK2101DX04VDC05_A | BS1_Tags
BR4.UTILITIES.WATER.BS1.P3FIREWATER.BTK2101.FieldIO.LT01 | BTK2101LT01_Hi_A | BTK2101 - LT01 BS1 NPI Firewater Tank 1 Level 1 | BR4_Cluster1 |  |  | BPL131 | BTK2101LT01 Hi Alarm | BTK2101LT01_Hi_A | BS1_Tags
BR4.UTILITIES.WATER.BS1.P3FIREWATER.BTK2101.FieldIO.LT01 | BTK2101LT01_HiHi_A | BTK2101 - LT01 BS1 NPI Firewater Tank 1 Level 1 | BR4_Cluster1 |  |  | BPL131 | BTK2101LT01 NPI Fire Water Tank Level High High Alarm | BTK2101LT01_HiHi_A | BS1_Tags
BR4.UTILITIES.WATER.BS1.P3FIREWATER.BTK2101.FieldIO.LT01 | BTK2101LT01_Lo_A | BTK2101 - LT01 BS1 NPI Firewater Tank 1 Level 1 | BR4_Cluster1 |  |  | BPL131 | NPI Fire Water Tank 1 LT01 Level Low Alarm | BTK2101LT01_Lo_A | BS1_Tags
BR4.UTILITIES.WATER.BS1.P3FIREWATER.BTK2101.FieldIO.LT01 | BTK2101LT01_LoLo_A | BTK2101 - LT01 BS1 NPI Firewater Tank 1 Level 1 | BR4_Cluster1 |  |  | BPL131 | BTK2101LT01 Level Low Low Alarm | BTK2101LT01_LoLo_A | BS1_Tags
BR4.UTILITIES.WATER.BS1.P3FIREWATER.BTK2102.FieldIO.LT01 | BTK2102LT01_Hi_A | BTK2102 - LT01 BS1 NPI Firewater Tank 2 Level 1 | BR4_Cluster1 |  |  | BPL131 | BTK2102LT01 Hi Alarm | BTK2102LT01_Hi_A | BS1_Tags
BR4.UTILITIES.WATER.BS1.P3FIREWATER.BTK2102.FieldIO.LT01 | BTK2102LT01_HiHi_A | BTK2102 - LT01 BS1 NPI Firewater Tank 2 Level 1 | BR4_Cluster1 |  |  | BPL131 | BTK2102LT01 NPI Fire Water Tank LT01 Level High High Alarm | BTK2102LT01_HiHi_A | BS1_Tags
BR4.UTILITIES.WATER.BS1.P3FIREWATER.BTK2102.FieldIO.LT01 | BTK2102LT01_Lo_A | BTK2102 - LT01 BS1 NPI Firewater Tank 2 Level 1 | BR4_Cluster1 |  |  | BPL131 | BTK2101LT01 Tank Level Low Healthy | BTK2102LT01_Lo_A | BS1_Tags
BR4.UTILITIES.WATER.BS1.P3FIREWATER.BTK2102.FieldIO.LT01 | BTK2102LT01_LoLo_A | BTK2102 - LT01 BS1 NPI Firewater Tank 2 Level 1 | BR4_Cluster1 |  |  | BPL131 | BTK2101LT01 Tank Level Low Low Alarm | BTK2102LT01_LoLo_A | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop02 | BTY1502DX02DIO1PLM0_ComFlt_A | BPL131 Drop 2 - BSR131DX01 | BR4_Cluster1 |  |  | BPL131 | BTY1502DX02 CRA Comms Module 0 Communications Fault Alarm | BTY1502DX02DIO1PLM0_ComFlt_A | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop02 | BTY1502DX02DIO1PLM0_Flt_A | BPL131 Drop 2 - BSR131DX01 | BR4_Cluster1 |  |  | BPL131 | BTY1502DX02 CRA Comms Module 0 Fault Alarm | BTY1502DX02DIO1PLM0_Flt_A | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop02 | BTY1502DX02DIO1PLM1_Flt_A | BPL131 Drop 2 - BSR131DX01 | BR4_Cluster1 |  |  | BPL131 | BTY1502DX02 DI Module 1 Fault Alarm | BTY1502DX02DIO1PLM1_Flt_A | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop02 | BTY1502DX02DIO1PLM1_Grp1Flt_A | BPL131 Drop 2 - BSR131DX01 | BR4_Cluster1 |  |  | BPL131 | BTY1502DX02 DI Module 1 Group 1 Fault Alarm | BTY1502DX02DIO1PLM1_Grp1Flt_A | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop02 | BTY1502DX02DIO1PLM1_Grp2Flt_A | BPL131 Drop 2 - BSR131DX01 | BR4_Cluster1 |  |  | BPL131 | BTY1502DX02 DI Module 1 Group 2 Fault Alarm | BTY1502DX02DIO1PLM1_Grp2Flt_A | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop02 | BTY1502DX02DIO1PLM2_Flt_A | BPL131 Drop 2 - BSR131DX01 | BR4_Cluster1 |  |  | BPL131 | BTY1502DX02 DI Module 2 Fault Alarm | BTY1502DX02DIO1PLM2_Flt_A | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop02 | BTY1502DX02DIO1PLM2_Grp1Flt_A | BPL131 Drop 2 - BSR131DX01 | BR4_Cluster1 |  |  | BPL131 | BTY1502DX02 DI Module 2 Group 1 Fault Alarm | BTY1502DX02DIO1PLM2_Grp1Flt_A | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop02 | BTY1502DX02DIO1PLM2_Grp2Flt_A | BPL131 Drop 2 - BSR131DX01 | BR4_Cluster1 |  |  | BPL131 | BTY1502DX02 DI Module 2 Group 2 Fault Alarm | BTY1502DX02DIO1PLM2_Grp2Flt_A | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop02 | BTY1502DX02DIO1PLM3_Flt_A | BPL131 Drop 2 - BSR131DX01 | BR4_Cluster1 |  |  | BPL131 | BTY1502DX02 DI Module 3 Fault Alarm | BTY1502DX02DIO1PLM3_Flt_A | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop02 | BTY1502DX02DIO1PLM3_Grp1Flt_A | BPL131 Drop 2 - BSR131DX01 | BR4_Cluster1 |  |  | BPL131 | BTY1502DX02 DI Module 3 Group 1 Fault Alarm | BTY1502DX02DIO1PLM3_Grp1Flt_A | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop02 | BTY1502DX02DIO1PLM3_Grp2Flt_A | BPL131 Drop 2 - BSR131DX01 | BR4_Cluster1 |  |  | BPL131 | BTY1502DX02 DI Module 3 Group 2 Fault Alarm | BTY1502DX02DIO1PLM3_Grp2Flt_A | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop02 | BTY1502DX02DIO1PLM4_Flt_A | BPL131 Drop 2 - BSR131DX01 | BR4_Cluster1 |  |  | BPL131 | BTY1502DX02 DO Module 4 Fault Alarm | BTY1502DX02DIO1PLM4_Flt_A | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop02 | BTY1502DX02DIO1PLM5_Ch00Flt_A | BPL131 Drop 2 - BSR131DX01 | BR4_Cluster1 |  |  | BPL131 | BTY1502DX02 AHI Module 5 Channel 0 Fault Alarm | BTY1502DX02DIO1PLM5_Ch00Flt_A | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop02 | BTY1502DX02DIO1PLM5_Ch01Flt_A | BPL131 Drop 2 - BSR131DX01 | BR4_Cluster1 |  |  | BPL131 | BTY1502DX02 AHI Module 5 Channel 1 Fault Alarm | BTY1502DX02DIO1PLM5_Ch01Flt_A | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop02 | BTY1502DX02DIO1PLM5_Ch02Flt_A | BPL131 Drop 2 - BSR131DX01 | BR4_Cluster1 |  |  | BPL131 | BTY1502DX02 AHI Module 5 Channel 2 Fault Alarm | BTY1502DX02DIO1PLM5_Ch02Flt_A | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop02 | BTY1502DX02DIO1PLM5_Ch03Flt_A | BPL131 Drop 2 - BSR131DX01 | BR4_Cluster1 |  |  | BPL131 | BTY1502DX02 AHI Module 5 Channel 3 Fault Alarm | BTY1502DX02DIO1PLM5_Ch03Flt_A | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop02 | BTY1502DX02DIO1PLM5_Ch04Flt_A | BPL131 Drop 2 - BSR131DX01 | BR4_Cluster1 |  |  | BPL131 | BTY1502DX02 AHI Module 5 Channel 4 Fault Alarm | BTY1502DX02DIO1PLM5_Ch04Flt_A | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop02 | BTY1502DX02DIO1PLM5_Ch05Flt_A | BPL131 Drop 2 - BSR131DX01 | BR4_Cluster1 |  |  | BPL131 | BTY1502DX02 AHI Module 5 Channel 5 Fault Alarm | BTY1502DX02DIO1PLM5_Ch05Flt_A | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop02 | BTY1502DX02DIO1PLM5_Ch06Flt_A | BPL131 Drop 2 - BSR131DX01 | BR4_Cluster1 |  |  | BPL131 | BTY1502DX02 AHI Module 5 Channel 6 Fault Alarm | BTY1502DX02DIO1PLM5_Ch06Flt_A | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop02 | BTY1502DX02DIO1PLM5_Ch07Flt_A | BPL131 Drop 2 - BSR131DX01 | BR4_Cluster1 |  |  | BPL131 | BTY1502DX02 AHI Module 5 Channel 7 Fault Alarm | BTY1502DX02DIO1PLM5_Ch07Flt_A | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop02 | BTY1502DX02DIO1PLM5_Flt_A | BPL131 Drop 2 - BSR131DX01 | BR4_Cluster1 |  |  | BPL131 | BTY1502DX02 AHI Module 5 Fault Alarm | BTY1502DX02DIO1PLM5_Flt_A | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop02 | BTY1502DX02DIO1PLM6_Ch00Flt_A | BPL131 Drop 2 - BSR131DX01 | BR4_Cluster1 |  |  | BPL131 | BTY1502DX02 AHI Module 6 Channel 0 Fault Alarm | BTY1502DX02DIO1PLM6_Ch00Flt_A | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop02 | BTY1502DX02DIO1PLM6_Ch01Flt_A | BPL131 Drop 2 - BSR131DX01 | BR4_Cluster1 |  |  | BPL131 | BTY1502DX02 AHI Module 6 Channel 1 Fault Alarm | BTY1502DX02DIO1PLM6_Ch01Flt_A | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop02 | BTY1502DX02DIO1PLM6_Ch02Flt_A | BPL131 Drop 2 - BSR131DX01 | BR4_Cluster1 |  |  | BPL131 | BTY1502DX02 AHI Module 6 Channel 2 Fault Alarm | BTY1502DX02DIO1PLM6_Ch02Flt_A | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop02 | BTY1502DX02DIO1PLM6_Ch03Flt_A | BPL131 Drop 2 - BSR131DX01 | BR4_Cluster1 |  |  | BPL131 | BTY1502DX02 AHI Module 6 Channel 3 Fault Alarm | BTY1502DX02DIO1PLM6_Ch03Flt_A | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop02 | BTY1502DX02DIO1PLM6_Ch04Flt_A | BPL131 Drop 2 - BSR131DX01 | BR4_Cluster1 |  |  | BPL131 | BTY1502DX02 AHI Module 6 Channel 4 Fault Alarm | BTY1502DX02DIO1PLM6_Ch04Flt_A | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop02 | BTY1502DX02DIO1PLM6_Ch05Flt_A | BPL131 Drop 2 - BSR131DX01 | BR4_Cluster1 |  |  | BPL131 | BTY1502DX02 AHI Module 6 Channel 5 Fault Alarm | BTY1502DX02DIO1PLM6_Ch05Flt_A | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop02 | BTY1502DX02DIO1PLM6_Ch06Flt_A | BPL131 Drop 2 - BSR131DX01 | BR4_Cluster1 |  |  | BPL131 | BTY1502DX02 AHI Module 6 Channel 6 Fault Alarm | BTY1502DX02DIO1PLM6_Ch06Flt_A | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop02 | BTY1502DX02DIO1PLM6_Ch07Flt_A | BPL131 Drop 2 - BSR131DX01 | BR4_Cluster1 |  |  | BPL131 | BTY1502DX02 AHI Module 6 Channel 7 Fault Alarm | BTY1502DX02DIO1PLM6_Ch07Flt_A | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop02 | BTY1502DX02DIO1PLM6_Flt_A | BPL131 Drop 2 - BSR131DX01 | BR4_Cluster1 |  |  | BPL131 | BTY1502DX02 AHI Module 6 Fault Alarm | BTY1502DX02DIO1PLM6_Flt_A | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop02 | BTY1502DX02DIO1PLM7_Ch00Flt_A | BPL131 Drop 2 - BSR131DX01 | BR4_Cluster1 |  |  | BPL131 | BTY1502DX02 AHI Module 7 Channel 0 Fault Alarm | BTY1502DX02DIO1PLM7_Ch00Flt_A | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop02 | BTY1502DX02DIO1PLM7_Ch01Flt_A | BPL131 Drop 2 - BSR131DX01 | BR4_Cluster1 |  |  | BPL131 | BTY1502DX02 AHI Module 7 Channel 1 Fault Alarm | BTY1502DX02DIO1PLM7_Ch01Flt_A | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop02 | BTY1502DX02DIO1PLM7_Ch02Flt_A | BPL131 Drop 2 - BSR131DX01 | BR4_Cluster1 |  |  | BPL131 | BTY1502DX02 AHI Module 7 Channel 2 Fault Alarm | BTY1502DX02DIO1PLM7_Ch02Flt_A | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop02 | BTY1502DX02DIO1PLM7_Ch03Flt_A | BPL131 Drop 2 - BSR131DX01 | BR4_Cluster1 |  |  | BPL131 | BTY1502DX02 AHI Module 7 Channel 3 Fault Alarm | BTY1502DX02DIO1PLM7_Ch03Flt_A | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop02 | BTY1502DX02DIO1PLM7_Ch04Flt_A | BPL131 Drop 2 - BSR131DX01 | BR4_Cluster1 |  |  | BPL131 | BTY1502DX02 AHI Module 7 Channel 4 Fault Alarm | BTY1502DX02DIO1PLM7_Ch04Flt_A | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop02 | BTY1502DX02DIO1PLM7_Ch05Flt_A | BPL131 Drop 2 - BSR131DX01 | BR4_Cluster1 |  |  | BPL131 | BTY1502DX02 AHI Module 7 Channel 5 Fault Alarm | BTY1502DX02DIO1PLM7_Ch05Flt_A | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop02 | BTY1502DX02DIO1PLM7_Ch06Flt_A | BPL131 Drop 2 - BSR131DX01 | BR4_Cluster1 |  |  | BPL131 | BTY1502DX02 AHI Module 7 Channel 6 Fault Alarm | BTY1502DX02DIO1PLM7_Ch06Flt_A | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop02 | BTY1502DX02DIO1PLM7_Ch07Flt_A | BPL131 Drop 2 - BSR131DX01 | BR4_Cluster1 |  |  | BPL131 | BTY1502DX02 AHI Module 7 Channel 7 Fault Alarm | BTY1502DX02DIO1PLM7_Ch07Flt_A | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop02 | BTY1502DX02DIO1PLM7_Flt_A | BPL131 Drop 2 - BSR131DX01 | BR4_Cluster1 |  |  | BPL131 | BTY1502DX02 AHI Module 7 Fault Alarm | BTY1502DX02DIO1PLM7_Flt_A | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop02 | BTY1502DX02DIO1PLM9_Ch00Flt_A | BPL131 Drop 2 - BSR131DX01 | BR4_Cluster1 |  |  | BPL131 | BTY1502DX02 AHO Module 9 Channel 0 Fault Alarm | BTY1502DX02DIO1PLM9_Ch00Flt_A | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop02 | BTY1502DX02DIO1PLM9_Ch01Flt_A | BPL131 Drop 2 - BSR131DX01 | BR4_Cluster1 |  |  | BPL131 | BTY1502DX02 AHO Module 9 Channel 1 Fault Alarm | BTY1502DX02DIO1PLM9_Ch01Flt_A | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop02 | BTY1502DX02DIO1PLM9_Ch02Flt_A | BPL131 Drop 2 - BSR131DX01 | BR4_Cluster1 |  |  | BPL131 | BTY1502DX02 AHO Module 9 Channel 2 Fault Alarm | BTY1502DX02DIO1PLM9_Ch02Flt_A | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop02 | BTY1502DX02DIO1PLM9_Ch03Flt_A | BPL131 Drop 2 - BSR131DX01 | BR4_Cluster1 |  |  | BPL131 | BTY1502DX02 AHO Module 9 Channel 3 Fault Alarm | BTY1502DX02DIO1PLM9_Ch03Flt_A | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop02 | BTY1502DX02DIO1PLM9_Flt_A | BPL131 Drop 2 - BSR131DX01 | BR4_Cluster1 |  |  | BPL131 | BTY1502DX02 AHO Module 9 Fault Alarm | BTY1502DX02DIO1PLM9_Flt_A | BS1_Tags
BR4.UTILITIES.WATER.BS1.BTY1502.FieldIO | BTY1502DX02VDC01_A | BTY1502 - West Turkeys Nest Field I/O | BR4_Cluster1 |  |  | BPL131 | West Turkeys Nest DIO Box 2 24VDC Output Control Supply (Q143) Failure | BTY1502DX02VDC01_A | BS1_Tags
BR4.UTILITIES.WATER.BS1.BTY1502.FieldIO | BTY1502DX02VDC02_A | BTY1502 - West Turkeys Nest Field I/O | BR4_Cluster1 |  |  | BPL131 | West Turkeys Nest DIO Box 2 24VDC GW1 Control Supply (Q157) Failure | BTY1502DX02VDC02_A | BS1_Tags
BR4.UTILITIES.WATER.BS1.BTY1502.FieldIO | BTY1502DX02VDC03_A | BTY1502 - West Turkeys Nest Field I/O | BR4_Cluster1 |  |  | BPL131 | West Turkeys Nest DIO Box 2 24VDC Instrument Control Supply (Q164) Failure | BTY1502DX02VDC03_A | BS1_Tags
BR4.UTILITIES.WATER.BS1.BTY1502.FieldIO | BTY1502DX02VDC04_A | BTY1502 - West Turkeys Nest Field I/O | BR4_Cluster1 |  |  | BPL131 | West Turkeys Nest DIO Box 2 24VDC Transmitter Control Supply (Q168) Failure | BTY1502DX02VDC04_A | BS1_Tags
BR4.UTILITIES.WATER.BS1.BTY1502.FieldIO | BTY1502DX02VDC05_A | BTY1502 - West Turkeys Nest Field I/O | BR4_Cluster1 |  |  | BPL131 | West Turkeys Nest DIO Box 2 24VDC Process Water Control Supply (Q172) Failure | BTY1502DX02VDC05_A | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1101.FieldIO | BTY1502DX02VDC06_A | BPP1101 - Field I/O | BR4_Cluster1 |  |  | BPL131 | West Turkeys Nest DIO Box 2 24VDC BPP1101 Control Supply (Q176) Failure | BTY1502DX02VDC06_A | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1102.FieldIO | BTY1502DX02VDC07_A | BPP1102 - Field I/O | BR4_Cluster1 |  |  | BPL131 | West Turkeys Nest DIO Box 2 24VDC BPP1102 Control Supply (Q180) Failure | BTY1502DX02VDC07_A | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BPP1106.FieldIO | BTY1502DX02VDC08_A | BPP1106 - Field I/O | BR4_Cluster1 |  |  | BPL131 | West Turkeys Nest DIO Box 2 24VDC BPP1106 Control Supply (Q184) Failure | BTY1502DX02VDC08_A | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BPP1107.FieldIO | BTY1502DX02VDC09_A | BPP1107 - Field I/O | BR4_Cluster1 |  |  | BPL131 | West Turkeys Nest DIO Box 2 24VDC BPP1107 Control Supply (Q188) Failure | BTY1502DX02VDC09_A | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BSTD1106.FieldIO | BTY1502DX02VDC10_A | BSTD1106 - Field I/O | BR4_Cluster1 |  |  | BPL131 | West Turkeys Nest DIO Box 2 24VDC BSTD1106 Control Supply (Q192) Failure | BTY1502DX02VDC10_A | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BSTD1107.FieldIO | BTY1502DX02VDC11_A | BSTD1107 - Field I/O | BR4_Cluster1 |  |  | BPL131 | West Turkeys Nest DIO Box 2 24VDC BSTD1107 Control Supply (Q196) Failure | BTY1502DX02VDC11_A | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop03 | BTY1502DX03DIO1PLM0_ComFlt_A | BPL131 Drop 3 - BTY1502DX03 | BR4_Cluster1 |  |  | BPL131 | BTY1502DX03 CRA Comms Module 0 Communications Fault Alarm | BTY1502DX03DIO1PLM0_ComFlt_A | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop03 | BTY1502DX03DIO1PLM0_Flt_A | BPL131 Drop 3 - BTY1502DX03 | BR4_Cluster1 |  |  | BPL131 | BTY1502DX03 CRA Comms Module 0 Fault Alarm | BTY1502DX03DIO1PLM0_Flt_A | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop03 | BTY1502DX03DIO1PLM1_Flt_A | BPL131 Drop 3 - BTY1502DX03 | BR4_Cluster1 |  |  | BPL131 | BTY1502DX03 DI Module 1 Fault Alarm | BTY1502DX03DIO1PLM1_Flt_A | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop03 | BTY1502DX03DIO1PLM1_Grp1Flt_A | BPL131 Drop 3 - BTY1502DX03 | BR4_Cluster1 |  |  | BPL131 | BTY1502DX03 DI Module 1 Group 1 Fault Alarm | BTY1502DX03DIO1PLM1_Grp1Flt_A | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop03 | BTY1502DX03DIO1PLM1_Grp2Flt_A | BPL131 Drop 3 - BTY1502DX03 | BR4_Cluster1 |  |  | BPL131 | BTY1502DX03 DI Module 1 Group 2 Fault Alarm | BTY1502DX03DIO1PLM1_Grp2Flt_A | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop03 | BTY1502DX03DIO1PLM3_Ch00Flt_A | BPL131 Drop 3 - BTY1502DX03 | BR4_Cluster1 |  |  | BPL131 | BTY1502DX03 AHI Module 3 Channel 0 Fault Alarm | BTY1502DX03DIO1PLM3_Ch00Flt_A | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop03 | BTY1502DX03DIO1PLM3_Ch01Flt_A | BPL131 Drop 3 - BTY1502DX03 | BR4_Cluster1 |  |  | BPL131 | BTY1502DX03 AHI Module 3 Channel 1 Fault Alarm | BTY1502DX03DIO1PLM3_Ch01Flt_A | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop03 | BTY1502DX03DIO1PLM3_Ch02Flt_A | BPL131 Drop 3 - BTY1502DX03 | BR4_Cluster1 |  |  | BPL131 | BTY1502DX03 AHI Module 3 Channel 2 Fault Alarm | BTY1502DX03DIO1PLM3_Ch02Flt_A | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop03 | BTY1502DX03DIO1PLM3_Ch03Flt_A | BPL131 Drop 3 - BTY1502DX03 | BR4_Cluster1 |  |  | BPL131 | BTY1502DX03 AHI Module 3 Channel 3 Fault Alarm | BTY1502DX03DIO1PLM3_Ch03Flt_A | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop03 | BTY1502DX03DIO1PLM3_Ch04Flt_A | BPL131 Drop 3 - BTY1502DX03 | BR4_Cluster1 |  |  | BPL131 | BTY1502DX03 AHI Module 3 Channel 4 Fault Alarm | BTY1502DX03DIO1PLM3_Ch04Flt_A | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop03 | BTY1502DX03DIO1PLM3_Ch05Flt_A | BPL131 Drop 3 - BTY1502DX03 | BR4_Cluster1 |  |  | BPL131 | BTY1502DX03 AHI Module 3 Channel 5 Fault Alarm | BTY1502DX03DIO1PLM3_Ch05Flt_A | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop03 | BTY1502DX03DIO1PLM3_Ch06Flt_A | BPL131 Drop 3 - BTY1502DX03 | BR4_Cluster1 |  |  | BPL131 | BTY1502DX03 AHI Module 3 Channel 6 Fault Alarm | BTY1502DX03DIO1PLM3_Ch06Flt_A | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop03 | BTY1502DX03DIO1PLM3_Ch07Flt_A | BPL131 Drop 3 - BTY1502DX03 | BR4_Cluster1 |  |  | BPL131 | BTY1502DX03 AHI Module 3 Channel 7 Fault Alarm | BTY1502DX03DIO1PLM3_Ch07Flt_A | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop03 | BTY1502DX03DIO1PLM3_Flt_A | BPL131 Drop 3 - BTY1502DX03 | BR4_Cluster1 |  |  | BPL131 | BTY1502DX03 AHI Module 3 Fault Alarm | BTY1502DX03DIO1PLM3_Flt_A | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop03 | BTY1502DX03DIO1PLM4_Ch00Flt_A | BPL131 Drop 3 - BTY1502DX03 | BR4_Cluster1 |  |  | BPL131 | BTY1502DX03 AHI Module 4 Channel 0 Fault Alarm | BTY1502DX03DIO1PLM4_Ch00Flt_A | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop03 | BTY1502DX03DIO1PLM4_Ch01Flt_A | BPL131 Drop 3 - BTY1502DX03 | BR4_Cluster1 |  |  | BPL131 | BTY1502DX03 AHI Module 4 Channel 1 Fault Alarm | BTY1502DX03DIO1PLM4_Ch01Flt_A | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop03 | BTY1502DX03DIO1PLM4_Ch02Flt_A | BPL131 Drop 3 - BTY1502DX03 | BR4_Cluster1 |  |  | BPL131 | BTY1502DX03 AHI Module 4 Channel 2 Fault Alarm | BTY1502DX03DIO1PLM4_Ch02Flt_A | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop03 | BTY1502DX03DIO1PLM4_Ch03Flt_A | BPL131 Drop 3 - BTY1502DX03 | BR4_Cluster1 |  |  | BPL131 | BTY1502DX03 AHI Module 4 Channel 3 Fault Alarm | BTY1502DX03DIO1PLM4_Ch03Flt_A | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop03 | BTY1502DX03DIO1PLM4_Ch04Flt_A | BPL131 Drop 3 - BTY1502DX03 | BR4_Cluster1 |  |  | BPL131 | BTY1502DX03 AHI Module 4 Channel 4 Fault Alarm | BTY1502DX03DIO1PLM4_Ch04Flt_A | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop03 | BTY1502DX03DIO1PLM4_Ch05Flt_A | BPL131 Drop 3 - BTY1502DX03 | BR4_Cluster1 |  |  | BPL131 | BTY1502DX03 AHI Module 4 Channel 5 Fault Alarm | BTY1502DX03DIO1PLM4_Ch05Flt_A | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop03 | BTY1502DX03DIO1PLM4_Ch06Flt_A | BPL131 Drop 3 - BTY1502DX03 | BR4_Cluster1 |  |  | BPL131 | BTY1502DX03 AHI Module 4 Channel 6 Fault Alarm | BTY1502DX03DIO1PLM4_Ch06Flt_A | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop03 | BTY1502DX03DIO1PLM4_Ch07Flt_A | BPL131 Drop 3 - BTY1502DX03 | BR4_Cluster1 |  |  | BPL131 | BTY1502DX03 AHI Module 4 Channel 7 Fault Alarm | BTY1502DX03DIO1PLM4_Ch07Flt_A | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop03 | BTY1502DX03DIO1PLM4_Flt_A | BPL131 Drop 3 - BTY1502DX03 | BR4_Cluster1 |  |  | BPL131 | BTY1502DX03 AHI Module 4 Fault Alarm | BTY1502DX03DIO1PLM4_Flt_A | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop03 | BTY1502DX03VDC01_A | BPL131 Drop 3 - BTY1502DX03 | BR4_Cluster1 |  |  | BPL131 | West Turkeys Nest DIO Box 3 24VDC Output Control Supply (Q143) Failure | BTY1502DX03VDC01_A | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop03 | BTY1502DX03VDC02_A | BPL131 Drop 3 - BTY1502DX03 | BR4_Cluster1 |  |  | BPL131 | West Turkeys Nest DIO Box 3 24VDC GW1 Control Supply (Q157) Failure | BTY1502DX03VDC02_A | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop03 | BTY1502DX03VDC03_A | BPL131 Drop 3 - BTY1502DX03 | BR4_Cluster1 |  |  | BPL131 | West Turkeys Nest DIO Box 3 24VDC Instrument Control Supply (Q164) Failure | BTY1502DX03VDC03_A | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop03 | BTY1502DX03VDC04_A | BPL131 Drop 3 - BTY1502DX03 | BR4_Cluster1 |  |  | BPL131 | West Turkeys Nest DIO Box 3 24VDC Transmitter Control Supply (Q168) Failure | BTY1502DX03VDC04_A | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop03 | BTY1502DX03VDC05_A | BPL131 Drop 3 - BTY1502DX03 | BR4_Cluster1 |  |  | BPL131 | West Turkeys Nest DIO Box 3 24VDC BTY1502DX03 Field Control Supply (Q172) Failure | BTY1502DX03VDC05_A | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop03 | BTY1502DX03VDC06_A | BPL131 Drop 3 - BTY1502DX03 | BR4_Cluster1 |  |  | BPL131 | West Turkeys Nest DIO Box 3 24VDC BPP1103 Field Control Supply (Q176) Failure | BTY1502DX03VDC06_A | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop03 | BTY1502DX03VDC07_A | BPL131 Drop 3 - BTY1502DX03 | BR4_Cluster1 |  |  | BPL131 | West Turkeys Nest DIO Box 3 24VDC BPP1104 Field Control Supply (Q180) Failure | BTY1502DX03VDC07_A | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop03 | BTY1502DX03VDC08_A | BPL131 Drop 3 - BTY1502DX03 | BR4_Cluster1 |  |  | BPL131 | West Turkeys Nest DIO Box 3 24VDC BPP1105 Field Control Supply (Q184) Failure | BTY1502DX03VDC08_A | BS1_Tags
BR4.UTILITIES.WATER.BS1.BTY1502.FieldIO.FT02 | BTY1502FT02_Flt_A | BTY1502 - FT02 Recirculation Flowmeter | BR4_Cluster1 |  |  | BPL131 | BTY1502FT02 West Turkeys Nest Recirculation Flow Fault Alarm | BTY1502FT02_Flt_A | BS1_Tags
BR4.UTILITIES.WATER.BS1.BTY1502.FieldIO.FT02 | BTY1502FT02_Frz_A | BTY1502 - FT02 Recirculation Flowmeter | BR4_Cluster1 |  |  | BPL131 | BTY1502FT02 Recirculation FlowTransmitter Frozen Alarm | BTY1502FT02_Frz_A | BS1_Tags
BR4.UTILITIES.WATER.BS1.BTY1502.FieldIO.FT02 | BTY1502FT02_Hi_A | BTY1502 - FT02 Recirculation Flowmeter | BR4_Cluster1 |  |  | BPL131 | BTY1502FT02 Recirculation Flow High Alarm | BTY1502FT02_Hi_A | BS1_Tags
BR4.UTILITIES.WATER.BS1.BTY1502.FieldIO.FT02 | BTY1502FT02_Lo_A | BTY1502 - FT02 Recirculation Flowmeter | BR4_Cluster1 |  |  | BPL131 | BTY1502FT02 Recirculation Flow Low Alarm | BTY1502FT02_Lo_A | BS1_Tags
BR4.UTILITIES.WATER.BS1.BTY1502.FV01 | BTY1502FV01_FTC_A | BTY1502 - FV01 West Turkeys Nest Recirculation Valve | BR4_Cluster1 |  |  | BPL131 | West Turkeys Nest Valve Fail to Close Alarm | BTY1502FV01_FTC_A | BS1_Tags
BR4.UTILITIES.WATER.BS1.BTY1502.FV01 | BTY1502FV01_FTO_A | BTY1502 - FV01 West Turkeys Nest Recirculation Valve | BR4_Cluster1 |  |  | BPL131 | West Turkeys Nest Valve Fail to Open Alarm | BTY1502FV01_FTO_A | BS1_Tags
BR4.UTILITIES.WATER.BS1.BTY1502.FV01 | BTY1502FV01_LmtFlt_A | BTY1502 - FV01 West Turkeys Nest Recirculation Valve | BR4_Cluster1 |  |  | BPL131 | West Turkeys Nest Valve Dual Limit Alarm | BTY1502FV01_LmtFlt_A | BS1_Tags
BR4.UTILITIES.WATER.BS1.BTY1502.FV01 | BTY1502FV01_LocFlt_A | BTY1502 - FV01 West Turkeys Nest Recirculation Valve | BR4_Cluster1 |  |  | BPL131 | BTY1502FV01 Left in Local Alarm | BTY1502FV01_LocFlt_A | BS1_Tags
BR4.UTILITIES.WATER.BS1.BTY1502.FV01.FieldIO.CB01 | BTY1502FV01CB01_A | BTY1502 - FV01 West Turkeys Nest Recirculation Valve Circuit Breaker | BR4_Cluster1 |  |  | BPL131 | West Turkeys Nest 240VAC Flow Valve Power Circuit Breaker Open | BTY1502FV01CB01_A | BS1_Tags
BR4.UTILITIES.WATER.BS1.BTY1502.FV01 | BTY1502FV01XS01_A | BTY1502 - FV01 West Turkeys Nest Recirculation Valve | BR4_Cluster1 |  |  | BPL131 | West Turkeys Nest Valve Unhealthy Alarm | BTY1502FV01XS01_A | BS1_Tags
BR4.UTILITIES.WATER.BS1.BTY1502 | BTY1502LS01_A | BTY1502 - West Turkeys Nest | BR4_Cluster1 |  |  | BPL131 | West Turkeys Nest West Turkeys Nest | BTY1502LS01_A | BS1_Tags
BR4.UTILITIES.WATER.BS1.BTY1502.FieldIO.LT01 | BTY1502LT01_Frz_A | BTY1502 - LT01 West Turkeys Nest Level 1 | BR4_Cluster1 |  |  | BPL131 | BTY1502 Level Transmitter Freeze Alarm | BTY1502LT01_Frz_A | BS1_Tags
BR4.UTILITIES.WATER.BS1.BTY1502.FieldIO.LT01 | BTY1502LT01_Hi_A | BTY1502 - LT01 West Turkeys Nest Level 1 | BR4_Cluster1 |  |  | BPL131 | BTY1502LT01 West Turkeys Nest Level High Alarm | BTY1502LT01_Hi_A | BS1_Tags
BR4.UTILITIES.WATER.BS1.BTY1502.FieldIO.LT01 | BTY1502LT01_HiHi_A | BTY1502 - LT01 West Turkeys Nest Level 1 | BR4_Cluster1 |  |  | BPL131 | BTY1502LT01 West Turkeys Nest Level High High Alarm | BTY1502LT01_HiHi_A | BS1_Tags
BR4.UTILITIES.WATER.BS1.BTY1502.FieldIO.LT01 | BTY1502LT01_Lo_A | BTY1502 - LT01 West Turkeys Nest Level 1 | BR4_Cluster1 |  |  | BPL131 | BTY1502LT01 West Turkeys Nest Level Low Alarm | BTY1502LT01_Lo_A | BS1_Tags
BR4.UTILITIES.WATER.BS1.BTY1502.FieldIO.LT01 | BTY1502LT01_LoLo_A | BTY1502 - LT01 West Turkeys Nest Level 1 | BR4_Cluster1 |  |  | BPL131 | BTY1502LT01 Turkeys Nest Low Low Alarm | BTY1502LT01_LoLo_A | BS1_Tags
BR4.UTILITIES.WATER.BS1.BTY1502.FieldIO.LT01 | BTY1502LT01_SigFlt_A | BTY1502 - LT01 West Turkeys Nest Level 1 | BR4_Cluster1 |  |  | BPL131 | BTY1502LT01 Level Discrepancy Fault Alarm | BTY1502LT01_SigFlt_A | BS1_Tags
BR4.UTILITIES.WATER.BS1.BTY1502.FieldIO.LT02 | BTY1502LT02_Frz_A | BTY1502 - LT02 West Turkeys Nest Level 2 | BR4_Cluster1 |  |  | BPL131 | East Turkeys Nest Raw Water Remote Mode LT02 Freeze Alarm | BTY1502LT02_Frz_A | BS1_Tags
BR4.UTILITIES.WATER.BS1.BTY1502.FieldIO.LT02 | BTY1502LT02_Hi_A | BTY1502 - LT02 West Turkeys Nest Level 2 | BR4_Cluster1 |  |  | BPL131 | BTY1502LT02 West Turkeys Nest Level High Alarm | BTY1502LT02_Hi_A | BS1_Tags
BR4.UTILITIES.WATER.BS1.BTY1502.FieldIO.LT02 | BTY1502LT02_HiHi_A | BTY1502 - LT02 West Turkeys Nest Level 2 | BR4_Cluster1 |  |  | BPL131 | BTY1502LT02 West Turkeys Nest High High Alarm | BTY1502LT02_HiHi_A | BS1_Tags
BR4.UTILITIES.WATER.BS1.BTY1502.FieldIO.LT02 | BTY1502LT02_Lo_A | BTY1502 - LT02 West Turkeys Nest Level 2 | BR4_Cluster1 |  |  | BPL131 | BTY1502LT02 West Turkeys Nest Low Alarm | BTY1502LT02_Lo_A | BS1_Tags
BR4.UTILITIES.WATER.BS1.BTY1502.FieldIO.LT02 | BTY1502LT02_LoLo_A | BTY1502 - LT02 West Turkeys Nest Level 2 | BR4_Cluster1 |  |  | BPL131 | BTK2101LT02 NPI Fire Water Tank Level Low Low Alarm | BTY1502LT02_LoLo_A | BS1_Tags
BR4.UTILITIES.WATER.BS1.BTY1502.FieldIO.LT02 | BTY1502LT02_SigFlt_A | BTY1502 - LT02 West Turkeys Nest Level 2 | BR4_Cluster1 |  |  | BPL131 | BTY1502LT02 West Turkeys Nest Signal Fault Alarm | BTY1502LT02_SigFlt_A | BS1_Tags
BR4.UTILITIES.WATER.BS1.BTY1502.FieldIO.PT01 | BTY1502PT01_Hi_A | BTY1502 - PT01 WTN East Pit Line Pressure | BR4_Cluster1 |  |  | BPL131 | BTY1502PT01 WTN East Collection Header In Flow Pressure High Alarm | BTY1502PT01_Hi_A | BS1_Tags
BR4.UTILITIES.WATER.BS1.BTY1502.FieldIO.PT01 | BTY1502PT01_Lo_A | BTY1502 - PT01 WTN East Pit Line Pressure | BR4_Cluster1 |  |  | BPL131 | BTY1502PT01 WTN East Collection Header In Flow Pressure Low Alarm | BTY1502PT01_Lo_A | BS1_Tags
BR4.UTILITIES.WATER.BS1.BTY1502.FieldIO.PT03 | BTY1502PT03_Hi_A | BTY1502 - PT03 WTN West Pit Line Pressure | BR4_Cluster1 |  |  | BPL131 | BTY1502PT03 WTN West Collection Header In Flow Pressure High Alarm | BTY1502PT03_Hi_A | BS1_Tags

## Trends
BR4.SRV.PWR.BSR131.BMC131.INC03.MasterPact | FltSts1OK | BMC131INC03PR1DAT1_FltSts1OK | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BMC131INC03 Process Incomer MasterPact Fault Status 1 Data Valid | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC03.MasterPact | FltSts1 | BMC131INC03PR1DAT1_FltSts1 | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BMC131INC03 Process Incomer MasterPact Fault Status 1 | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC03.MasterPact | FltSts2OK | BMC131INC03PR1DAT1_FltSts2OK | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BMC131INC03 Process Incomer MasterPact Fault Status 2 Data Valid | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC03.MasterPact | FltSts2 | BMC131INC03PR1DAT1_FltSts2 | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BMC131INC03 Process Incomer MasterPact Fault Status 2 | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC01.MasterPact | FltSts1OK | BMC131INC01PR1DAT1_FltSts1OK | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BMC131INC01 Process Incomer MasterPact Fault Status 1 Data Valid | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC01.MasterPact | FltSts1 | BMC131INC01PR1DAT1_FltSts1 | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BMC131INC01 Process Incomer MasterPact Fault Status 1 | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC01.MasterPact | FltSts2OK | BMC131INC01PR1DAT1_FltSts2OK | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BMC131INC01 Process Incomer MasterPact Fault Status 2 Data Valid | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC01.MasterPact | FltSts2 | BMC131INC01PR1DAT1_FltSts2 | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BMC131INC01 Process Incomer MasterPact Fault Status 2 | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC02.MasterPact | FltSts1OK | BMC131INC02PR1DAT1_FltSts1OK | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BMC131INC02 Process Incomer MasterPact Fault Status 1 Data Valid | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC02.MasterPact | FltSts1 | BMC131INC02PR1DAT1_FltSts1 | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BMC131INC02 Process Incomer MasterPact Fault Status 1 | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC02.MasterPact | FltSts2OK | BMC131INC02PR1DAT1_FltSts2OK | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BMC131INC02 Process Incomer MasterPact Fault Status 2 Data Valid | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC02.MasterPact | FltSts2 | BMC131INC02PR1DAT1_FltSts2 | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BMC131INC02 Process Incomer MasterPact Fault Status 2 | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC03 | 0 | BMC131INC03PR1DAT1 | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BMC131 Generator Bus Incomer Protection Relay Status Data for HMI Display | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC03 | 0 | BPL131_CfgID | BR4_Cluster1 | TRN_PERIODIC | 0:00 | NPI Hub PLC CPU Current Build Number | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131 | 0 | BPL131_ScnAvg | BR4_Cluster1 | TRN_PERIODIC | 0:00 | NPI Hub PLC CPU Average Scan Time (ms) | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131 | 0 | BPL131_ScnMax | BR4_Cluster1 | TRN_PERIODIC | 0:00 | NPI Hub PLC CPU Maximum Scan Time (ms) | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131 | 0 | BPL131_ScnMin | BR4_Cluster1 | TRN_PERIODIC | 0:00 | NPI Hub PLC CPU Minimum Scan Time (ms) | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131 | ScanTm | BPL131_ScnVal | BR4_Cluster1 | TRN_PERIODIC | 0:00 | NPI Hub PLC CPU Last Scan Time (ms) | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131 | 0 | BPL131_SysScnAvg | BR4_Cluster1 | TRN_PERIODIC | 0:00 | NPI Hub PLC CPU Average Overhead Scan Time (ms) | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131 | 0 | BPL131_SysScnMax | BR4_Cluster1 | TRN_PERIODIC | 0:00 | NPI Hub PLC CPU Maximum Overhead Scan Time (ms) | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131 | 0 | BPL131_SysScnMin | BR4_Cluster1 | TRN_PERIODIC | 0:00 | NPI Hub PLC CPU Minimum Overhead Scan Time (ms) | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131 | 0 | BPL131_SysScnVal | BR4_Cluster1 | TRN_PERIODIC | 0:00 | NPI Hub PLC CPU Last Overhead Scan Time (ms) | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131 | 0 | BPL131_WD | BR4_Cluster1 | TRN_PERIODIC | 0:00 | NPI Hub PLC CPU Heart Beat Watchdog | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131 | 0 | BPL131PLM0STS2 | BR4_Cluster1 | TRN_PERIODIC | 0:00 | NPI Hub PLC CPU RIO Network Status Data | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1101 | 0 | BPP1101DRVSTAT | BR4_Cluster1 | TRN_PERIODIC | 0:00 | Production Plant and NPI Water Supply Pump 1 Status Word | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1102 | 0 | BPP1102DRVSTAT | BR4_Cluster1 | TRN_PERIODIC | 0:00 | Production Plant and NPI Water Supply Pump 2 Status Word | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1103 | 0 | BPP1103DRVSTAT | BR4_Cluster1 | TRN_PERIODIC | 0:00 | Water Transfer Pump 1 Status Word | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1103.FieldIO.FT03 | 0 | BPP1103FT03_Tot | BR4_Cluster1 | TRN_PERIODIC | 0:00 | Water Transfer Pump 1 Flow Rate (m3/h) Flow Totals | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1103.FieldIO.FT06 | 0 | BPP1103FT06_Tot | BR4_Cluster1 | TRN_PERIODIC | 0:00 | Water Transfer Pump 1 Flow Rate (m3/h) Flow Totals | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1104 | 0 | BPP1104DRVSTAT | BR4_Cluster1 | TRN_PERIODIC | 0:00 | Water Transfer Pump 2 Status Word | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1104.FieldIO.FT04 | 0 | BPP1104FT04_Tot | BR4_Cluster1 | TRN_PERIODIC | 0:00 | Water Transfer Pump 2 Flow Rate (m3/h) Flow Totals | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1105.Sub.CB01 | 0 | BPP1105DRVSTAT | BR4_Cluster1 | TRN_PERIODIC | 0:00 | Water Transfer Pump 3 Status Word | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1105.FieldIO.FT05 | 0 | BPP1105FT05_Tot | BR4_Cluster1 | TRN_PERIODIC | 0:00 | Water Transfer Pump 3 Flow Rate (m3/h) Flow Totals | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BPP1106 | 0 | BPP1106DRVSTAT | BR4_Cluster1 | TRN_PERIODIC | 0:00 | HME & LME Standpipe Pump 3 Status Word | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BPP1107 | 0 | BPP1107DRVSTAT | BR4_Cluster1 | TRN_PERIODIC | 0:00 | HME & LME Standpipe Pump 4 Status Word | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop01 | 0 | BSR131DX01DIO1PLM0STS1 | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131DX01 CRA Comms Module 0 Modules Status | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop01 | 0 | BSR131DX01DIO1PLM1STS1 | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131DX01 DI Module 1 Status | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop01 | 0 | BSR131DX01DIO1PLM2STS1 | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131DX01 DI Module 2 Status | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop01 | 0 | BSR131DX01DIO1PLM3STS1 | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131DX01 DI Module 3 Status | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop01 | 0 | BSR131DX01DIO1PLM4STS1 | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131DX01 DI Module 4 Status | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop01 | 0 | BSR131DX01DIO1PLM5STS1 | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131DX01 DI Module 5 Status | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop01 | 0 | BSR131DX01DIO1PLM6STS1 | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131DX01 DI Module 6 Status | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop01 | 0 | BSR131DX01DIO1PLM7STS1 | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131DX01 DI Module 7 Status | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop01 | 0 | BSR131DX01DIO1PLM8STS1 | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131DX01 DO Module 8 Status | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop04 | 0 | BTK2101DX04DIO1PLM0STS1 | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BTK2101DX04 CRA Comms Module 0 Modules Status | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop04 | 0 | BTK2101DX04DIO1PLM1STS1 | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BTK2101DX04 DI Module 1 Status | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop04 | 0 | BTK2101DX04DIO1PLM3STS1 | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BTK2101DX04 AHI Module 3 Module Status | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop02 | 0 | BTY1502DX02DIO1PLM0STS1 | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BTY1502DX02 CRA Comms Module 0 Modules Status | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop02 | 0 | BTY1502DX02DIO1PLM1STS1 | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BTY1502DX02 DI Module 1 Status | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop02 | 0 | BTY1502DX02DIO1PLM2STS1 | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BTY1502DX02 DI Module 2 Status | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop02 | 0 | BTY1502DX02DIO1PLM3STS1 | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BTY1502DX02 DI Module 3 Status | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop02 | 0 | BTY1502DX02DIO1PLM4STS1 | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BTY1502DX02 DO Module 4 Status | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop02 | 0 | BTY1502DX02DIO1PLM5STS1 | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BTY1502DX02 AHI Module 5 Module Status | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop02 | 0 | BTY1502DX02DIO1PLM6STS1 | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BTY1502DX02 AHI Module 6 Module Status | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop02 | 0 | BTY1502DX02DIO1PLM7STS1 | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BTY1502DX02 AHI Module 7 Module Status | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop02 | 0 | BTY1502DX02DIO1PLM9STS1 | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BTY1502DX02 AHO Module 9 Module Status | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop03 | 0 | BTY1502DX03DIO1PLM0STS1 | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BTY1502DX03 CRA Comms Module 0 Modules Status | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop03 | 0 | BTY1502DX03DIO1PLM1STS1 | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BTY1502DX03 DI Module 1 Status | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop03 | 0 | BTY1502DX03DIO1PLM3STS1 | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BTY1502DX03 AHI Module 3 Module Status | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.CTRLSYS.PLC.BPL131.Drop03 | 0 | BTY1502DX03DIO1PLM4STS1 | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BTY1502DX03 AHI Module 4 Module Status | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.UTILITIES.WATER.BS1.BTY1502.FieldIO.FT01 | 0 | BTY1502FT01_Tot | BR4_Cluster1 | TRN_PERIODIC | 0:00 | West Turkeys Nest Flow Rate (m3/h) Flow Totals | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.UTILITIES.WATER.BS1.BTY1502.FieldIO.FT03 | 0 | BTY1502FT03_Tot | BR4_Cluster1 | TRN_PERIODIC | 0:00 | West Turkeys Nest Flow Rate (m3/h) Flow Totals | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.BC02.BACS | Str1I | BSR131BC02BACSDAT1_Str1I | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131BC02 Battery Charger BACS String 1 Current | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.BC02.BACS | Str1AltI | BSR131BC02BACSDAT1_Str1AltI | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131BC02 Battery Charger BACS String 1 AC Current | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.BC02.BACS | Str1SumV | BSR131BC02BACSDAT1_Str1SumV | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131BC02 Battery Charger BACS String 1 Overall Voltage | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.BC02.BACS | Str1AvgV | BSR131BC02BACSDAT1_Str1AvgV | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131BC02 Battery Charger BACS String 1 Average Voltage | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.BC02.BACS | Mod1Tmp | BSR131BC02BACSDAT1_Mod1Tmp | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131BC02 Battery Charger BACS Module 1 Temperature | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.BC02.BACS | Mod1V | BSR131BC02BACSDAT1_Mod1V | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131BC02 Battery Charger BACS Module 1 Voltage | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.BC02.BACS | Mod1Imp | BSR131BC02BACSDAT1_Mod1Imp | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131BC02 Battery Charger BACS Module 1 Impedance | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.BC02.BACS | Mod1EqPerc | BSR131BC02BACSDAT1_Mod1EqPerc | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131BC02 Battery Charger BACS Module 1 Equalizing / Balancing | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.BC02.BACS | Mod2Tmp | BSR131BC02BACSDAT1_Mod2Tmp | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131BC02 Battery Charger BACS Module 2 Temperature | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.BC02.BACS | Mod2V | BSR131BC02BACSDAT1_Mod2V | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131BC02 Battery Charger BACS Module 2 Voltage | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.BC02.BACS | Mod2Imp | BSR131BC02BACSDAT1_Mod2Imp | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131BC02 Battery Charger BACS Module 2 Impedance | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.BC02.BACS | Mod2EqPerc | BSR131BC02BACSDAT1_Mod2EqPerc | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131BC02 Battery Charger BACS Module 2 Equalizing / Balancing | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.BC02.BACS | Mod3Tmp | BSR131BC02BACSDAT1_Mod3Tmp | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131BC02 Battery Charger BACS Module 3 Temperature | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.BC02.BACS | Mod3V | BSR131BC02BACSDAT1_Mod3V | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131BC02 Battery Charger BACS Module 3 Voltage | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.BC02.BACS | Mod3Imp | BSR131BC02BACSDAT1_Mod3Imp | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131BC02 Battery Charger BACS Module 3 Impedance | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.BC02.BACS | Mod3EqPerc | BSR131BC02BACSDAT1_Mod3EqPerc | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131BC02 Battery Charger BACS Module 3 Equalizing / Balancing | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.BC02.BACS | Mod4Tmp | BSR131BC02BACSDAT1_Mod4Tmp | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131BC02 Battery Charger BACS Module 4 Temperature | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.BC02.BACS | Mod4V | BSR131BC02BACSDAT1_Mod4V | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131BC02 Battery Charger BACS Module 4 Voltage | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.BC02.BACS | Mod4Imp | BSR131BC02BACSDAT1_Mod4Imp | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131BC02 Battery Charger BACS Module 4 Impedance | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.BC02.BACS | Mod4EqPerc | BSR131BC02BACSDAT1_Mod4EqPerc | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131BC02 Battery Charger BACS Module 4 Equalizing / Balancing | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.BC02.BACS | Mod5Tmp | BSR131BC02BACSDAT1_Mod5Tmp | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131BC02 Battery Charger BACS Module 5 Temperature | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.BC02.BACS | Mod5V | BSR131BC02BACSDAT1_Mod5V | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131BC02 Battery Charger BACS Module 5 Voltage | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.BC02.BACS | Mod5Imp | BSR131BC02BACSDAT1_Mod5Imp | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131BC02 Battery Charger BACS Module 5 Impedance | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.BC02.BACS | Mod5EqPerc | BSR131BC02BACSDAT1_Mod5EqPerc | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131BC02 Battery Charger BACS Module 5 Equalizing / Balancing | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.BC02.BACS | Mod6Tmp | BSR131BC02BACSDAT1_Mod6Tmp | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131BC02 Battery Charger BACS Module 6 Temperature | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.BC02.BACS | Mod6V | BSR131BC02BACSDAT1_Mod6V | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131BC02 Battery Charger BACS Module 6 Voltage | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.BC02.BACS | Mod6Imp | BSR131BC02BACSDAT1_Mod6Imp | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131BC02 Battery Charger BACS Module 6 Impedance | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.BC02.BACS | Mod6EqPerc | BSR131BC02BACSDAT1_Mod6EqPerc | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131BC02 Battery Charger BACS Module 6 Equalizing / Balancing | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.BC02.BACS | Mod7Tmp | BSR131BC02BACSDAT1_Mod7Tmp | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131BC02 Battery Charger BACS Module 7 Temperature | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.BC02.BACS | Mod7V | BSR131BC02BACSDAT1_Mod7V | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131BC02 Battery Charger BACS Module 7 Voltage | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.BC02.BACS | Mod7Imp | BSR131BC02BACSDAT1_Mod7Imp | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131BC02 Battery Charger BACS Module 7 Impedance | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.BC02.BACS | Mod7EqPerc | BSR131BC02BACSDAT1_Mod7EqPerc | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131BC02 Battery Charger BACS Module 7 Equalizing / Balancing | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.BC02.BACS | Mod8Tmp | BSR131BC02BACSDAT1_Mod8Tmp | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131BC02 Battery Charger BACS Module 8 Temperature | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.BC02.BACS | Mod8V | BSR131BC02BACSDAT1_Mod8V | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131BC02 Battery Charger BACS Module 8 Voltage | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.BC02.BACS | Mod8Imp | BSR131BC02BACSDAT1_Mod8Imp | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131BC02 Battery Charger BACS Module 8 Impedance | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.BC02.BACS | Mod8EqPerc | BSR131BC02BACSDAT1_Mod8EqPerc | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131BC02 Battery Charger BACS Module 8 Equalizing / Balancing | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.BC02.BACS | Mod9Tmp | BSR131BC02BACSDAT1_Mod9Tmp | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131BC02 Battery Charger BACS Module 9 Temperature | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.BC02.BACS | Mod9V | BSR131BC02BACSDAT1_Mod9V | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131BC02 Battery Charger BACS Module 9 Voltage | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.BC02.BACS | Mod9Imp | BSR131BC02BACSDAT1_Mod9Imp | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131BC02 Battery Charger BACS Module 9 Impedance | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.BC02.BACS | Mod9EqPerc | BSR131BC02BACSDAT1_Mod9EqPerc | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131BC02 Battery Charger BACS Module 9 Equalizing / Balancing | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.UPScale | AlmID1 | BSR131UP01DAT1_AlmID1 | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS Alarm ID 1 | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.UPScale | AlmID2 | BSR131UP01DAT1_AlmID2 | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS Alarm ID 2 | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.UPScale | InVPhs1 | BSR131UP01DAT1_InVPhs1 | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS Input Voltage Phase 1 (V) | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.UPScale | InVPhs2 | BSR131UP01DAT1_InVPhs2 | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS Input Voltage Phase 2 (V) | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.UPScale | InVPhs3 | BSR131UP01DAT1_InVPhs3 | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS Input Voltage Phase 3 (V) | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.UPScale | Tmp | BSR131UP01DAT1_Tmp | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS Temperature (C) | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.UPScale | BatTmRemn | BSR131UP01DAT1_BatTmRemn | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS Battery Time Remaining (min) | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.UPScale | BatV | BSR131UP01DAT1_BatV | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS Battery Voltage (V) | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1I | BSR131UP01BACSDAT1_Str1I | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 1 Current | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1AltI | BSR131UP01BACSDAT1_Str1AltI | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 1 AC Current | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1SumV | BSR131UP01BACSDAT1_Str1SumV | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 1 Overall Voltage | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1AvgV | BSR131UP01BACSDAT1_Str1AvgV | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 1 Average Voltage | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod1Tmp | BSR131UP01BACSDAT1_Str1Mod1Tmp | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 1 Module 1 Temperature | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod1V | BSR131UP01BACSDAT1_Str1Mod1V | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 1 Module 1 Voltage | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod1Imp | BSR131UP01BACSDAT1_Str1Mod1Imp | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 1 Module 1 Impedance | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod1EqPerc | BSR131UP01BACSDAT1_Str1Mod1EqPerc | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 1 Module 1 Equalizing / Balancing | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod2Tmp | BSR131UP01BACSDAT1_Str1Mod2Tmp | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 1 Module 2 Temperature | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod2V | BSR131UP01BACSDAT1_Str1Mod2V | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 1 Module 2 Voltage | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod2Imp | BSR131UP01BACSDAT1_Str1Mod2Imp | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 1 Module 2 Impedance | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod2EqPerc | BSR131UP01BACSDAT1_Str1Mod2EqPerc | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 1 Module 2 Equalizing / Balancing | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod3Tmp | BSR131UP01BACSDAT1_Str1Mod3Tmp | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 1 Module 3 Temperature | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod3V | BSR131UP01BACSDAT1_Str1Mod3V | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 1 Module 3 Voltage | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod3Imp | BSR131UP01BACSDAT1_Str1Mod3Imp | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 1 Module 3 Impedance | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod3EqPerc | BSR131UP01BACSDAT1_Str1Mod3EqPerc | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 1 Module 3 Equalizing / Balancing | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod4Tmp | BSR131UP01BACSDAT1_Str1Mod4Tmp | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 1 Module 4 Temperature | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod4V | BSR131UP01BACSDAT1_Str1Mod4V | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 1 Module 4 Voltage | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod4Imp | BSR131UP01BACSDAT1_Str1Mod4Imp | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 1 Module 4 Impedance | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod4EqPerc | BSR131UP01BACSDAT1_Str1Mod4EqPerc | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 1 Module 4 Equalizing / Balancing | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod5Tmp | BSR131UP01BACSDAT1_Str1Mod5Tmp | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 1 Module 5 Temperature | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod5V | BSR131UP01BACSDAT1_Str1Mod5V | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 1 Module 5 Voltage | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod5Imp | BSR131UP01BACSDAT1_Str1Mod5Imp | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 1 Module 5 Impedance | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod5EqPerc | BSR131UP01BACSDAT1_Str1Mod5EqPerc | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 1 Module 5 Equalizing / Balancing | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod6Tmp | BSR131UP01BACSDAT1_Str1Mod6Tmp | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 1 Module 6 Temperature | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod6V | BSR131UP01BACSDAT1_Str1Mod6V | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 1 Module 6 Voltage | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod6Imp | BSR131UP01BACSDAT1_Str1Mod6Imp | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 1 Module 6 Impedance | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod6EqPerc | BSR131UP01BACSDAT1_Str1Mod6EqPerc | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 1 Module 6 Equalizing / Balancing | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod7Tmp | BSR131UP01BACSDAT1_Str1Mod7Tmp | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 1 Module 7 Temperature | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod7V | BSR131UP01BACSDAT1_Str1Mod7V | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 1 Module 7 Voltage | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod7Imp | BSR131UP01BACSDAT1_Str1Mod7Imp | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 1 Module 7 Impedance | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod7EqPerc | BSR131UP01BACSDAT1_Str1Mod7EqPerc | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 1 Module 7 Equalizing / Balancing | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod8Tmp | BSR131UP01BACSDAT1_Str1Mod8Tmp | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 1 Module 8 Temperature | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod8V | BSR131UP01BACSDAT1_Str1Mod8V | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 1 Module 8 Voltage | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod8Imp | BSR131UP01BACSDAT1_Str1Mod8Imp | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 1 Module 8 Impedance | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod8EqPerc | BSR131UP01BACSDAT1_Str1Mod8EqPerc | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 1 Module 8 Equalizing / Balancing | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod9Tmp | BSR131UP01BACSDAT1_Str1Mod9Tmp | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 1 Module 9 Temperature | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod9V | BSR131UP01BACSDAT1_Str1Mod9V | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 1 Module 9 Voltage | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod9Imp | BSR131UP01BACSDAT1_Str1Mod9Imp | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 1 Module 9 Impedance | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod9EqPerc | BSR131UP01BACSDAT1_Str1Mod9EqPerc | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 1 Module 9 Equalizing / Balancing | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod10Tmp | BSR131UP01BACSDAT1_Str1Mod10Tmp | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 1 Module 10 Temperature | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod10V | BSR131UP01BACSDAT1_Str1Mod10V | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 1 Module 10 Voltage | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod10Imp | BSR131UP01BACSDAT1_Str1Mod10Imp | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 1 Module 10 Impedance | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod10EqPerc | BSR131UP01BACSDAT1_Str1Mod10EqPerc | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 1 Module 10 Equalizing / Balancing | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod11Tmp | BSR131UP01BACSDAT1_Str1Mod11Tmp | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 1 Module 11 Temperature | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod11V | BSR131UP01BACSDAT1_Str1Mod11V | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 1 Module 11 Voltage | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod11Imp | BSR131UP01BACSDAT1_Str1Mod11Imp | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 1 Module 11 Impedance | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod11EqPerc | BSR131UP01BACSDAT1_Str1Mod11EqPerc | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 1 Module 11 Equalizing / Balancing | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod12Tmp | BSR131UP01BACSDAT1_Str1Mod12Tmp | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 1 Module 12 Temperature | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod12V | BSR131UP01BACSDAT1_Str1Mod12V | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 1 Module 12 Voltage | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod12Imp | BSR131UP01BACSDAT1_Str1Mod12Imp | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 1 Module 12 Impedance | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod12EqPerc | BSR131UP01BACSDAT1_Str1Mod12EqPerc | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 1 Module 12 Equalizing / Balancing | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod13Tmp | BSR131UP01BACSDAT1_Str1Mod13Tmp | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 1 Module 13 Temperature | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod13V | BSR131UP01BACSDAT1_Str1Mod13V | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 1 Module 13 Voltage | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod13Imp | BSR131UP01BACSDAT1_Str1Mod13Imp | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 1 Module 13 Impedance | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod13EqPerc | BSR131UP01BACSDAT1_Str1Mod13EqPerc | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 1 Module 13 Equalizing / Balancing | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod14Tmp | BSR131UP01BACSDAT1_Str1Mod14Tmp | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 1 Module 14 Temperature | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod14V | BSR131UP01BACSDAT1_Str1Mod14V | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 1 Module 14 Voltage | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod14Imp | BSR131UP01BACSDAT1_Str1Mod14Imp | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 1 Module 14 Impedance | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod14EqPerc | BSR131UP01BACSDAT1_Str1Mod14EqPerc | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 1 Module 14 Equalizing / Balancing | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod15Tmp | BSR131UP01BACSDAT1_Str1Mod15Tmp | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 1 Module 15 Temperature | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod15V | BSR131UP01BACSDAT1_Str1Mod15V | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 1 Module 15 Voltage | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod15Imp | BSR131UP01BACSDAT1_Str1Mod15Imp | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 1 Module 15 Impedance | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod15EqPerc | BSR131UP01BACSDAT1_Str1Mod15EqPerc | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 1 Module 15 Equalizing / Balancing | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod16Tmp | BSR131UP01BACSDAT1_Str1Mod16Tmp | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 1 Module 16 Temperature | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod16V | BSR131UP01BACSDAT1_Str1Mod16V | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 1 Module 16 Voltage | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod16Imp | BSR131UP01BACSDAT1_Str1Mod16Imp | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 1 Module 16 Impedance | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod16EqPerc | BSR131UP01BACSDAT1_Str1Mod16EqPerc | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 1 Module 16 Equalizing / Balancing | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod17Tmp | BSR131UP01BACSDAT1_Str1Mod17Tmp | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 1 Module 17 Temperature | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod17V | BSR131UP01BACSDAT1_Str1Mod17V | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 1 Module 17 Voltage | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod17Imp | BSR131UP01BACSDAT1_Str1Mod17Imp | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 1 Module 17 Impedance | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod17EqPerc | BSR131UP01BACSDAT1_Str1Mod17EqPerc | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 1 Module 17 Equalizing / Balancing | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod18Tmp | BSR131UP01BACSDAT1_Str1Mod18Tmp | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 1 Module 18 Temperature | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod18V | BSR131UP01BACSDAT1_Str1Mod18V | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 1 Module 18 Voltage | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod18Imp | BSR131UP01BACSDAT1_Str1Mod18Imp | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 1 Module 18 Impedance | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod18EqPerc | BSR131UP01BACSDAT1_Str1Mod18EqPerc | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 1 Module 18 Equalizing / Balancing | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod19Tmp | BSR131UP01BACSDAT1_Str1Mod19Tmp | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 1 Module 19 Temperature | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod19V | BSR131UP01BACSDAT1_Str1Mod19V | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 1 Module 19 Voltage | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod19Imp | BSR131UP01BACSDAT1_Str1Mod19Imp | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 1 Module 19 Impedance | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod19EqPerc | BSR131UP01BACSDAT1_Str1Mod19EqPerc | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 1 Module 19 Equalizing / Balancing | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod20Tmp | BSR131UP01BACSDAT1_Str1Mod20Tmp | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 1 Module 20 Temperature | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod20V | BSR131UP01BACSDAT1_Str1Mod20V | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 1 Module 20 Voltage | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod20Imp | BSR131UP01BACSDAT1_Str1Mod20Imp | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 1 Module 20 Impedance | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod20EqPerc | BSR131UP01BACSDAT1_Str1Mod20EqPerc | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 1 Module 20 Equalizing / Balancing | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod21Tmp | BSR131UP01BACSDAT1_Str1Mod21Tmp | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 1 Module 21 Temperature | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod21V | BSR131UP01BACSDAT1_Str1Mod21V | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 1 Module 21 Voltage | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod21Imp | BSR131UP01BACSDAT1_Str1Mod21Imp | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 1 Module 21 Impedance | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod21EqPerc | BSR131UP01BACSDAT1_Str1Mod21EqPerc | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 1 Module 21 Equalizing / Balancing | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod22V | BSR131UP01BACSDAT1_Str2Mod22V | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 2 Module 22 Voltage | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod22Tmp | BSR131UP01BACSDAT1_Str1Mod22Tmp | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 1 Module 22 Temperature | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod22Imp | BSR131UP01BACSDAT1_Str2Mod22Imp | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 2 Module 22 Impedance | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod22V | BSR131UP01BACSDAT1_Str1Mod22V | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 1 Module 22 Voltage | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod22Imp | BSR131UP01BACSDAT1_Str1Mod22Imp | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 1 Module 22 Impedance | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod22EqPerc | BSR131UP01BACSDAT1_Str2Mod22EqPerc | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 2 Module 22 Equalizing / Balancing | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod23Tmp | BSR131UP01BACSDAT1_Str2Mod23Tmp | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 2 Module 23 Temperature | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod22EqPerc | BSR131UP01BACSDAT1_Str1Mod22EqPerc | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 1 Module 22 Equalizing / Balancing | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod23V | BSR131UP01BACSDAT1_Str2Mod23V | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 2 Module 23 Voltage | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod23Tmp | BSR131UP01BACSDAT1_Str1Mod23Tmp | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 1 Module 23 Temperature | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod23Imp | BSR131UP01BACSDAT1_Str2Mod23Imp | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 2 Module 23 Impedance | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod23V | BSR131UP01BACSDAT1_Str1Mod23V | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 1 Module 23 Voltage | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod23Imp | BSR131UP01BACSDAT1_Str1Mod23Imp | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 1 Module 23 Impedance | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod23EqPerc | BSR131UP01BACSDAT1_Str2Mod23EqPerc | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 2 Module 23 Equalizing / Balancing | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod24Tmp | BSR131UP01BACSDAT1_Str2Mod24Tmp | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 2 Module 24 Temperature | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod23EqPerc | BSR131UP01BACSDAT1_Str1Mod23EqPerc | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 1 Module 23 Equalizing / Balancing | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod24V | BSR131UP01BACSDAT1_Str2Mod24V | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 2 Module 24 Voltage | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod24Tmp | BSR131UP01BACSDAT1_Str1Mod24Tmp | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 1 Module 24 Temperature | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod24Imp | BSR131UP01BACSDAT1_Str2Mod24Imp | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 2 Module 24 Impedance | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod24V | BSR131UP01BACSDAT1_Str1Mod24V | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 1 Module 24 Voltage | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod24Imp | BSR131UP01BACSDAT1_Str1Mod24Imp | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 1 Module 24 Impedance | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod24EqPerc | BSR131UP01BACSDAT1_Str2Mod24EqPerc | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 2 Module 24 Equalizing / Balancing | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod25Tmp | BSR131UP01BACSDAT1_Str2Mod25Tmp | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 2 Module 25 Temperature | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod24EqPerc | BSR131UP01BACSDAT1_Str1Mod24EqPerc | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 1 Module 24 Equalizing / Balancing | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod25V | BSR131UP01BACSDAT1_Str2Mod25V | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 2 Module 25 Voltage | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod25Tmp | BSR131UP01BACSDAT1_Str1Mod25Tmp | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 1 Module 25 Temperature | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod25Imp | BSR131UP01BACSDAT1_Str2Mod25Imp | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 2 Module 25 Impedance | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod25V | BSR131UP01BACSDAT1_Str1Mod25V | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 1 Module 25 Voltage | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod25Imp | BSR131UP01BACSDAT1_Str1Mod25Imp | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 1 Module 25 Impedance | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod25EqPerc | BSR131UP01BACSDAT1_Str2Mod25EqPerc | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 2 Module 25 Equalizing / Balancing | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod26Tmp | BSR131UP01BACSDAT1_Str2Mod26Tmp | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 2 Module 26 Temperature | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod25EqPerc | BSR131UP01BACSDAT1_Str1Mod25EqPerc | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 1 Module 25 Equalizing / Balancing | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod26V | BSR131UP01BACSDAT1_Str2Mod26V | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 2 Module 26 Voltage | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod26Tmp | BSR131UP01BACSDAT1_Str1Mod26Tmp | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 1 Module 26 Temperature | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod26Imp | BSR131UP01BACSDAT1_Str2Mod26Imp | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 2 Module 26 Impedance | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod26V | BSR131UP01BACSDAT1_Str1Mod26V | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 1 Module 26 Voltage | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod26Imp | BSR131UP01BACSDAT1_Str1Mod26Imp | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 1 Module 26 Impedance | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod26EqPerc | BSR131UP01BACSDAT1_Str2Mod26EqPerc | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 2 Module 26 Equalizing / Balancing | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod27Tmp | BSR131UP01BACSDAT1_Str2Mod27Tmp | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 2 Module 27 Temperature | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod26EqPerc | BSR131UP01BACSDAT1_Str1Mod26EqPerc | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 1 Module 26 Equalizing / Balancing | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod27V | BSR131UP01BACSDAT1_Str2Mod27V | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 2 Module 27 Voltage | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod27Tmp | BSR131UP01BACSDAT1_Str1Mod27Tmp | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 1 Module 27 Temperature | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod27Imp | BSR131UP01BACSDAT1_Str2Mod27Imp | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 2 Module 27 Impedance | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod27V | BSR131UP01BACSDAT1_Str1Mod27V | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 1 Module 27 Voltage | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod27Imp | BSR131UP01BACSDAT1_Str1Mod27Imp | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 1 Module 27 Impedance | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod27EqPerc | BSR131UP01BACSDAT1_Str2Mod27EqPerc | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 2 Module 27 Equalizing / Balancing | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod28Tmp | BSR131UP01BACSDAT1_Str2Mod28Tmp | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 2 Module 28 Temperature | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod27EqPerc | BSR131UP01BACSDAT1_Str1Mod27EqPerc | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 1 Module 27 Equalizing / Balancing | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod28V | BSR131UP01BACSDAT1_Str2Mod28V | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 2 Module 28 Voltage | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod28Tmp | BSR131UP01BACSDAT1_Str1Mod28Tmp | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 1 Module 28 Temperature | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod28Imp | BSR131UP01BACSDAT1_Str2Mod28Imp | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 2 Module 28 Impedance | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod28V | BSR131UP01BACSDAT1_Str1Mod28V | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 1 Module 28 Voltage | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod28Imp | BSR131UP01BACSDAT1_Str1Mod28Imp | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 1 Module 28 Impedance | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod28EqPerc | BSR131UP01BACSDAT1_Str2Mod28EqPerc | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 2 Module 28 Equalizing / Balancing | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod29Tmp | BSR131UP01BACSDAT1_Str2Mod29Tmp | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 2 Module 29 Temperature | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod28EqPerc | BSR131UP01BACSDAT1_Str1Mod28EqPerc | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 1 Module 28 Equalizing / Balancing | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod29V | BSR131UP01BACSDAT1_Str2Mod29V | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 2 Module 29 Voltage | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod29Tmp | BSR131UP01BACSDAT1_Str1Mod29Tmp | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 1 Module 29 Temperature | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod29Imp | BSR131UP01BACSDAT1_Str2Mod29Imp | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 2 Module 29 Impedance | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod29V | BSR131UP01BACSDAT1_Str1Mod29V | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 1 Module 29 Voltage | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod29Imp | BSR131UP01BACSDAT1_Str1Mod29Imp | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 1 Module 29 Impedance | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod29EqPerc | BSR131UP01BACSDAT1_Str2Mod29EqPerc | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 2 Module 29 Equalizing / Balancing | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod30Tmp | BSR131UP01BACSDAT1_Str2Mod30Tmp | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 2 Module 30 Temperature | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod29EqPerc | BSR131UP01BACSDAT1_Str1Mod29EqPerc | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 1 Module 29 Equalizing / Balancing | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod30V | BSR131UP01BACSDAT1_Str2Mod30V | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 2 Module 30 Voltage | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod30Tmp | BSR131UP01BACSDAT1_Str1Mod30Tmp | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 1 Module 30 Temperature | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod30Imp | BSR131UP01BACSDAT1_Str2Mod30Imp | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 2 Module 30 Impedance | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod30V | BSR131UP01BACSDAT1_Str1Mod30V | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 1 Module 30 Voltage | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod30Imp | BSR131UP01BACSDAT1_Str1Mod30Imp | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 1 Module 30 Impedance | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod30EqPerc | BSR131UP01BACSDAT1_Str2Mod30EqPerc | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 2 Module 30 Equalizing / Balancing | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod31Tmp | BSR131UP01BACSDAT1_Str2Mod31Tmp | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 2 Module 31 Temperature | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod30EqPerc | BSR131UP01BACSDAT1_Str1Mod30EqPerc | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 1 Module 30 Equalizing / Balancing | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod31V | BSR131UP01BACSDAT1_Str2Mod31V | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 2 Module 31 Voltage | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod31Tmp | BSR131UP01BACSDAT1_Str1Mod31Tmp | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 1 Module 31 Temperature | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod31Imp | BSR131UP01BACSDAT1_Str2Mod31Imp | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 2 Module 31 Impedance | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod31V | BSR131UP01BACSDAT1_Str1Mod31V | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 1 Module 31 Voltage | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod31Imp | BSR131UP01BACSDAT1_Str1Mod31Imp | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 1 Module 31 Impedance | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod31EqPerc | BSR131UP01BACSDAT1_Str2Mod31EqPerc | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 2 Module 31 Equalizing / Balancing | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod32Tmp | BSR131UP01BACSDAT1_Str2Mod32Tmp | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 2 Module 32 Temperature | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod31EqPerc | BSR131UP01BACSDAT1_Str1Mod31EqPerc | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 1 Module 31 Equalizing / Balancing | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod32V | BSR131UP01BACSDAT1_Str2Mod32V | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 2 Module 32 Voltage | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod32Tmp | BSR131UP01BACSDAT1_Str1Mod32Tmp | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 1 Module 32 Temperature | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod32Imp | BSR131UP01BACSDAT1_Str2Mod32Imp | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 2 Module 32 Impedance | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod32V | BSR131UP01BACSDAT1_Str1Mod32V | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 1 Module 32 Voltage | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod32Imp | BSR131UP01BACSDAT1_Str1Mod32Imp | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 1 Module 32 Impedance | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod32EqPerc | BSR131UP01BACSDAT1_Str2Mod32EqPerc | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 2 Module 32 Equalizing / Balancing | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod33Tmp | BSR131UP01BACSDAT1_Str2Mod33Tmp | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 2 Module 33 Temperature | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod32EqPerc | BSR131UP01BACSDAT1_Str1Mod32EqPerc | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 1 Module 32 Equalizing / Balancing | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod33V | BSR131UP01BACSDAT1_Str2Mod33V | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 2 Module 33 Voltage | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod33Tmp | BSR131UP01BACSDAT1_Str1Mod33Tmp | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 1 Module 33 Temperature | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod33Imp | BSR131UP01BACSDAT1_Str2Mod33Imp | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 2 Module 33 Impedance | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod33V | BSR131UP01BACSDAT1_Str1Mod33V | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 1 Module 33 Voltage | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod33Imp | BSR131UP01BACSDAT1_Str1Mod33Imp | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 1 Module 33 Impedance | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod33EqPerc | BSR131UP01BACSDAT1_Str2Mod33EqPerc | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 2 Module 33 Equalizing / Balancing | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod34Tmp | BSR131UP01BACSDAT1_Str2Mod34Tmp | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 2 Module 34 Temperature | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod33EqPerc | BSR131UP01BACSDAT1_Str1Mod33EqPerc | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 1 Module 33 Equalizing / Balancing | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod34V | BSR131UP01BACSDAT1_Str2Mod34V | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 2 Module 34 Voltage | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod34Tmp | BSR131UP01BACSDAT1_Str1Mod34Tmp | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 1 Module 34 Temperature | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod34Imp | BSR131UP01BACSDAT1_Str2Mod34Imp | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 2 Module 34 Impedance | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod34V | BSR131UP01BACSDAT1_Str1Mod34V | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 1 Module 34 Voltage | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod34Imp | BSR131UP01BACSDAT1_Str1Mod34Imp | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 1 Module 34 Impedance | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod34EqPerc | BSR131UP01BACSDAT1_Str2Mod34EqPerc | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 2 Module 34 Equalizing / Balancing | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod35Tmp | BSR131UP01BACSDAT1_Str2Mod35Tmp | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 2 Module 35 Temperature | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod34EqPerc | BSR131UP01BACSDAT1_Str1Mod34EqPerc | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 1 Module 34 Equalizing / Balancing | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod35V | BSR131UP01BACSDAT1_Str2Mod35V | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 2 Module 35 Voltage | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod35Tmp | BSR131UP01BACSDAT1_Str1Mod35Tmp | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 1 Module 35 Temperature | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod35Imp | BSR131UP01BACSDAT1_Str2Mod35Imp | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 2 Module 35 Impedance | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod35V | BSR131UP01BACSDAT1_Str1Mod35V | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 1 Module 35 Voltage | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod35Imp | BSR131UP01BACSDAT1_Str1Mod35Imp | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 1 Module 35 Impedance | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod35EqPerc | BSR131UP01BACSDAT1_Str2Mod35EqPerc | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 2 Module 35 Equalizing / Balancing | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod36Tmp | BSR131UP01BACSDAT1_Str2Mod36Tmp | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 2 Module 36 Temperature | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod35EqPerc | BSR131UP01BACSDAT1_Str1Mod35EqPerc | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 1 Module 35 Equalizing / Balancing | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod36V | BSR131UP01BACSDAT1_Str2Mod36V | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 2 Module 36 Voltage | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod36Tmp | BSR131UP01BACSDAT1_Str1Mod36Tmp | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 1 Module 36 Temperature | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod36Imp | BSR131UP01BACSDAT1_Str2Mod36Imp | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 2 Module 36 Impedance | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod36V | BSR131UP01BACSDAT1_Str1Mod36V | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 1 Module 36 Voltage | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod36Imp | BSR131UP01BACSDAT1_Str1Mod36Imp | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 1 Module 36 Impedance | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod36EqPerc | BSR131UP01BACSDAT1_Str2Mod36EqPerc | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 2 Module 36 Equalizing / Balancing | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod37Tmp | BSR131UP01BACSDAT1_Str2Mod37Tmp | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 2 Module 37 Temperature | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod36EqPerc | BSR131UP01BACSDAT1_Str1Mod36EqPerc | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 1 Module 36 Equalizing / Balancing | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod37V | BSR131UP01BACSDAT1_Str2Mod37V | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 2 Module 37 Voltage | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod37Tmp | BSR131UP01BACSDAT1_Str1Mod37Tmp | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 1 Module 37 Temperature | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod37Imp | BSR131UP01BACSDAT1_Str2Mod37Imp | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 2 Module 37 Impedance | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod37V | BSR131UP01BACSDAT1_Str1Mod37V | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 1 Module 37 Voltage | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod37Imp | BSR131UP01BACSDAT1_Str1Mod37Imp | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 1 Module 37 Impedance | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod37EqPerc | BSR131UP01BACSDAT1_Str2Mod37EqPerc | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 2 Module 37 Equalizing / Balancing | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod38Tmp | BSR131UP01BACSDAT1_Str2Mod38Tmp | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 2 Module 38 Temperature | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod37EqPerc | BSR131UP01BACSDAT1_Str1Mod37EqPerc | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 1 Module 37 Equalizing / Balancing | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod38V | BSR131UP01BACSDAT1_Str2Mod38V | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 2 Module 38 Voltage | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod38Tmp | BSR131UP01BACSDAT1_Str1Mod38Tmp | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 1 Module 38 Temperature | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod38Imp | BSR131UP01BACSDAT1_Str2Mod38Imp | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 2 Module 38 Impedance | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod38V | BSR131UP01BACSDAT1_Str1Mod38V | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 1 Module 38 Voltage | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod38Imp | BSR131UP01BACSDAT1_Str1Mod38Imp | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 1 Module 38 Impedance | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod38EqPerc | BSR131UP01BACSDAT1_Str2Mod38EqPerc | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 2 Module 38 Equalizing / Balancing | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod39Tmp | BSR131UP01BACSDAT1_Str2Mod39Tmp | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 2 Module 39 Temperature | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod38EqPerc | BSR131UP01BACSDAT1_Str1Mod38EqPerc | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 1 Module 38 Equalizing / Balancing | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod39V | BSR131UP01BACSDAT1_Str2Mod39V | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 2 Module 39 Voltage | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod39Tmp | BSR131UP01BACSDAT1_Str1Mod39Tmp | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 1 Module 39 Temperature | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod39Imp | BSR131UP01BACSDAT1_Str2Mod39Imp | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 2 Module 39 Impedance | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod39V | BSR131UP01BACSDAT1_Str1Mod39V | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 1 Module 39 Voltage | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod39Imp | BSR131UP01BACSDAT1_Str1Mod39Imp | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 1 Module 39 Impedance | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod39EqPerc | BSR131UP01BACSDAT1_Str2Mod39EqPerc | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 2 Module 39 Equalizing / Balancing | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod40Tmp | BSR131UP01BACSDAT1_Str2Mod40Tmp | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 2 Module 40 Temperature | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod39EqPerc | BSR131UP01BACSDAT1_Str1Mod39EqPerc | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 1 Module 39 Equalizing / Balancing | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod40V | BSR131UP01BACSDAT1_Str2Mod40V | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 2 Module 40 Voltage | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod40Tmp | BSR131UP01BACSDAT1_Str1Mod40Tmp | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 1 Module 40 Temperature | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod40Imp | BSR131UP01BACSDAT1_Str2Mod40Imp | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 2 Module 40 Impedance | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod40V | BSR131UP01BACSDAT1_Str1Mod40V | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 1 Module 40 Voltage | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod40Imp | BSR131UP01BACSDAT1_Str1Mod40Imp | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 1 Module 40 Impedance | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod40EqPerc | BSR131UP01BACSDAT1_Str2Mod40EqPerc | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 2 Module 40 Equalizing / Balancing | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod40EqPerc | BSR131UP01BACSDAT1_Str1Mod40EqPerc | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 1 Module 40 Equalizing / Balancing | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2I | BSR131UP01BACSDAT1_Str2I | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 2 Current | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2AltI | BSR131UP01BACSDAT1_Str2AltI | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 2 AC Current | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2SumV | BSR131UP01BACSDAT1_Str2SumV | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 2 Overall Voltage | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2AvgV | BSR131UP01BACSDAT1_Str2AvgV | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 2 Average Voltage | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod1Tmp | BSR131UP01BACSDAT1_Str2Mod1Tmp | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 2 Module 1 Temperature | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod1V | BSR131UP01BACSDAT1_Str2Mod1V | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 2 Module 1 Voltage | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod1Imp | BSR131UP01BACSDAT1_Str2Mod1Imp | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 2 Module 1 Impedance | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod1EqPerc | BSR131UP01BACSDAT1_Str2Mod1EqPerc | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 2 Module 1 Equalizing / Balancing | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod2Tmp | BSR131UP01BACSDAT1_Str2Mod2Tmp | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 2 Module 2 Temperature | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod2V | BSR131UP01BACSDAT1_Str2Mod2V | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 2 Module 2 Voltage | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod2Imp | BSR131UP01BACSDAT1_Str2Mod2Imp | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 2 Module 2 Impedance | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod2EqPerc | BSR131UP01BACSDAT1_Str2Mod2EqPerc | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 2 Module 2 Equalizing / Balancing | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod3Tmp | BSR131UP01BACSDAT1_Str2Mod3Tmp | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 2 Module 3 Temperature | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod3V | BSR131UP01BACSDAT1_Str2Mod3V | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 2 Module 3 Voltage | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod3Imp | BSR131UP01BACSDAT1_Str2Mod3Imp | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 2 Module 3 Impedance | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod3EqPerc | BSR131UP01BACSDAT1_Str2Mod3EqPerc | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 2 Module 3 Equalizing / Balancing | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod4Tmp | BSR131UP01BACSDAT1_Str2Mod4Tmp | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 2 Module 4 Temperature | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod4V | BSR131UP01BACSDAT1_Str2Mod4V | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 2 Module 4 Voltage | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod4Imp | BSR131UP01BACSDAT1_Str2Mod4Imp | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 2 Module 4 Impedance | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod4EqPerc | BSR131UP01BACSDAT1_Str2Mod4EqPerc | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 2 Module 4 Equalizing / Balancing | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod5Tmp | BSR131UP01BACSDAT1_Str2Mod5Tmp | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 2 Module 5 Temperature | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod5V | BSR131UP01BACSDAT1_Str2Mod5V | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 2 Module 5 Voltage | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod5Imp | BSR131UP01BACSDAT1_Str2Mod5Imp | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 2 Module 5 Impedance | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod5EqPerc | BSR131UP01BACSDAT1_Str2Mod5EqPerc | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 2 Module 5 Equalizing / Balancing | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod6Tmp | BSR131UP01BACSDAT1_Str2Mod6Tmp | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 2 Module 6 Temperature | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod6V | BSR131UP01BACSDAT1_Str2Mod6V | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 2 Module 6 Voltage | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod6Imp | BSR131UP01BACSDAT1_Str2Mod6Imp | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 2 Module 6 Impedance | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod6EqPerc | BSR131UP01BACSDAT1_Str2Mod6EqPerc | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 2 Module 6 Equalizing / Balancing | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod7Tmp | BSR131UP01BACSDAT1_Str2Mod7Tmp | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 2 Module 7 Temperature | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod7V | BSR131UP01BACSDAT1_Str2Mod7V | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 2 Module 7 Voltage | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod7Imp | BSR131UP01BACSDAT1_Str2Mod7Imp | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 2 Module 7 Impedance | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod7EqPerc | BSR131UP01BACSDAT1_Str2Mod7EqPerc | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 2 Module 7 Equalizing / Balancing | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod8Tmp | BSR131UP01BACSDAT1_Str2Mod8Tmp | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 2 Module 8 Temperature | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod8V | BSR131UP01BACSDAT1_Str2Mod8V | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 2 Module 8 Voltage | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod8Imp | BSR131UP01BACSDAT1_Str2Mod8Imp | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 2 Module 8 Impedance | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod8EqPerc | BSR131UP01BACSDAT1_Str2Mod8EqPerc | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 2 Module 8 Equalizing / Balancing | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod9Tmp | BSR131UP01BACSDAT1_Str2Mod9Tmp | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 2 Module 9 Temperature | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod9V | BSR131UP01BACSDAT1_Str2Mod9V | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 2 Module 9 Voltage | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod9Imp | BSR131UP01BACSDAT1_Str2Mod9Imp | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 2 Module 9 Impedance | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod9EqPerc | BSR131UP01BACSDAT1_Str2Mod9EqPerc | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 2 Module 9 Equalizing / Balancing | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod10Tmp | BSR131UP01BACSDAT1_Str2Mod10Tmp | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 2 Module 10 Temperature | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod10V | BSR131UP01BACSDAT1_Str2Mod10V | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 2 Module 10 Voltage | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod10Imp | BSR131UP01BACSDAT1_Str2Mod10Imp | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 2 Module 10 Impedance | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod10EqPerc | BSR131UP01BACSDAT1_Str2Mod10EqPerc | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 2 Module 10 Equalizing / Balancing | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod11Tmp | BSR131UP01BACSDAT1_Str2Mod11Tmp | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 2 Module 11 Temperature | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod11V | BSR131UP01BACSDAT1_Str2Mod11V | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 2 Module 11 Voltage | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod11Imp | BSR131UP01BACSDAT1_Str2Mod11Imp | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 2 Module 11 Impedance | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod11EqPerc | BSR131UP01BACSDAT1_Str2Mod11EqPerc | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 2 Module 11 Equalizing / Balancing | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod12Tmp | BSR131UP01BACSDAT1_Str2Mod12Tmp | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 2 Module 12 Temperature | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod12V | BSR131UP01BACSDAT1_Str2Mod12V | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 2 Module 12 Voltage | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod12Imp | BSR131UP01BACSDAT1_Str2Mod12Imp | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 2 Module 12 Impedance | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod12EqPerc | BSR131UP01BACSDAT1_Str2Mod12EqPerc | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 2 Module 12 Equalizing / Balancing | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod13Tmp | BSR131UP01BACSDAT1_Str2Mod13Tmp | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 2 Module 13 Temperature | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod13V | BSR131UP01BACSDAT1_Str2Mod13V | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 2 Module 13 Voltage | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod13Imp | BSR131UP01BACSDAT1_Str2Mod13Imp | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 2 Module 13 Impedance | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod13EqPerc | BSR131UP01BACSDAT1_Str2Mod13EqPerc | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 2 Module 13 Equalizing / Balancing | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod14Tmp | BSR131UP01BACSDAT1_Str2Mod14Tmp | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 2 Module 14 Temperature | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod14V | BSR131UP01BACSDAT1_Str2Mod14V | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 2 Module 14 Voltage | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod14Imp | BSR131UP01BACSDAT1_Str2Mod14Imp | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 2 Module 14 Impedance | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod14EqPerc | BSR131UP01BACSDAT1_Str2Mod14EqPerc | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 2 Module 14 Equalizing / Balancing | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod15Tmp | BSR131UP01BACSDAT1_Str2Mod15Tmp | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 2 Module 15 Temperature | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod15V | BSR131UP01BACSDAT1_Str2Mod15V | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 2 Module 15 Voltage | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod15Imp | BSR131UP01BACSDAT1_Str2Mod15Imp | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 2 Module 15 Impedance | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod15EqPerc | BSR131UP01BACSDAT1_Str2Mod15EqPerc | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 2 Module 15 Equalizing / Balancing | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod16Tmp | BSR131UP01BACSDAT1_Str2Mod16Tmp | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 2 Module 16 Temperature | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod16V | BSR131UP01BACSDAT1_Str2Mod16V | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 2 Module 16 Voltage | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod16Imp | BSR131UP01BACSDAT1_Str2Mod16Imp | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 2 Module 16 Impedance | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod16EqPerc | BSR131UP01BACSDAT1_Str2Mod16EqPerc | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 2 Module 16 Equalizing / Balancing | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod17Tmp | BSR131UP01BACSDAT1_Str2Mod17Tmp | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 2 Module 17 Temperature | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod17V | BSR131UP01BACSDAT1_Str2Mod17V | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 2 Module 17 Voltage | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod17Imp | BSR131UP01BACSDAT1_Str2Mod17Imp | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 2 Module 17 Impedance | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod17EqPerc | BSR131UP01BACSDAT1_Str2Mod17EqPerc | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 2 Module 17 Equalizing / Balancing | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod18Tmp | BSR131UP01BACSDAT1_Str2Mod18Tmp | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 2 Module 18 Temperature | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod18V | BSR131UP01BACSDAT1_Str2Mod18V | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 2 Module 18 Voltage | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod18Imp | BSR131UP01BACSDAT1_Str2Mod18Imp | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 2 Module 18 Impedance | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod18EqPerc | BSR131UP01BACSDAT1_Str2Mod18EqPerc | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 2 Module 18 Equalizing / Balancing | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod19Tmp | BSR131UP01BACSDAT1_Str2Mod19Tmp | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 2 Module 19 Temperature | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod19V | BSR131UP01BACSDAT1_Str2Mod19V | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 2 Module 19 Voltage | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod19Imp | BSR131UP01BACSDAT1_Str2Mod19Imp | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 2 Module 19 Impedance | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod19EqPerc | BSR131UP01BACSDAT1_Str2Mod19EqPerc | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 2 Module 19 Equalizing / Balancing | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod20Tmp | BSR131UP01BACSDAT1_Str2Mod20Tmp | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 2 Module 20 Temperature | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod20V | BSR131UP01BACSDAT1_Str2Mod20V | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 2 Module 20 Voltage | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod20Imp | BSR131UP01BACSDAT1_Str2Mod20Imp | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 2 Module 20 Impedance | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod20EqPerc | BSR131UP01BACSDAT1_Str2Mod20EqPerc | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 2 Module 20 Equalizing / Balancing | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod21Tmp | BSR131UP01BACSDAT1_Str2Mod21Tmp | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 2 Module 21 Temperature | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod21V | BSR131UP01BACSDAT1_Str2Mod21V | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 2 Module 21 Voltage | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod21Imp | BSR131UP01BACSDAT1_Str2Mod21Imp | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 2 Module 21 Impedance | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod21EqPerc | BSR131UP01BACSDAT1_Str2Mod21EqPerc | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 2 Module 21 Equalizing / Balancing | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod22Tmp | BSR131UP01BACSDAT1_Str2Mod22Tmp | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 2 Module 22 Temperature | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1101 | 0 | BPP1101PIC01_Cmd | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BPP1101 Pressure Controller HMI Commands | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1103 | 0 | BPP1103LIC01_Cmd | BR4_Cluster1 | TRN_PERIODIC | 0:00 | West Turkeys Nest Level Controller HMI Commands | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BSTD1106 | 0 | BSTD1106FIC01_Cmd | BR4_Cluster1 | TRN_PERIODIC | 0:00 | West Turkeys Nest LME Standpipe Flow Controller HMI Commands | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BSTD1107 | 0 | BSTD1107FIC01_Cmd | BR4_Cluster1 | TRN_PERIODIC | 0:00 | West Turkeys Nest HME Standpipe Flow Controller HMI Commands | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC01 | 0 | BMC131INC01PR1DAT1 | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BMC131 Process Bus Incomer Protection Relay Status Data for HMI Display | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC02 | 0 | BMC131INC02PR1DAT1 | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BMC131 Essential Bus Incomer Protection Relay Status Data for HMI Display | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1101 | 0 | BPP1101_RunTm | BR4_Cluster1 | TRN_PERIODIC | 0:00 | Production Plant and NPI Water Supply Pump 1 Running Time Totaliser (min) | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1102 | 0 | BPP1102_RunTm | BR4_Cluster1 | TRN_PERIODIC | 0:00 | Production Plant and NPI Water Supply Pump 2 Running Time Totaliser (min) | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1103 | 0 | BPP1103_RunTm | BR4_Cluster1 | TRN_PERIODIC | 0:00 | Water Transfer Pump 1 Running Time Totaliser (min) | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1104 | 0 | BPP1104_RunTm | BR4_Cluster1 | TRN_PERIODIC | 0:00 | Water Transfer Pump 2 Running Time Totaliser (min) | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1105 | 0 | BPP1105_RunTm | BR4_Cluster1 | TRN_PERIODIC | 0:00 | Water Transfer Pump 3 Running Time Totaliser (min) | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BPP1106 | 0 | BPP1106_RunTm | BR4_Cluster1 | TRN_PERIODIC | 0:00 | HME & LME Standpipe Pump 3 Running Time Totaliser (min) | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BPP1107 | 0 | BPP1107_RunTm | BR4_Cluster1 | TRN_PERIODIC | 0:00 | HME & LME Standpipe Pump 4 Running Time Totaliser (min) | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1101.VS01 | FltID | BPP1101VS01DAT1_FltID | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BPP1101VS01 VVVF Drive Fault ID | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1102.VS01 | FltID | BPP1102VS01DAT1_FltID | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BPP1102VS01 VVVF Drive Fault ID | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1103.VS01 | FltID | BPP1103VS01DAT1_FltID | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BPP1103VS01 VVVF Drive Fault ID | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1104.VS01 | FltID | BPP1104VS01DAT1_FltID | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BPP1104VS01 VVVF Drive Fault ID | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1105.VS01 | FltID | BPP1105VS01DAT1_FltID | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BPP1105VS01 VVVF Drive Fault ID | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1106.VS01 | FltID | BPP1106VS01DAT1_FltID | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BPP1106VS01 VVVF Drive Fault ID | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1107.VS01 | FltID | BPP1107VS01DAT1_FltID | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BPP1107VS01 VVVF Drive Fault ID | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC02.MasterPact | In | BMC131INC02PR1DAT1_In | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BMC131INC02 Process Incomer MasterPact RMS Current on Neutral | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC02.MasterPact | Vab | BMC131INC02PR1DAT1_Vab | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BMC131INC02 Process Incomer MasterPact RMS Phase A to B Voltage | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC02.MasterPact | Vbc | BMC131INC02PR1DAT1_Vbc | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BMC131INC02 Process Incomer MasterPact RMS Phase B to C Voltage | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC02.MasterPact | Vca | BMC131INC02PR1DAT1_Vca | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BMC131INC02 Process Incomer MasterPact RMS Phase C to A Voltage | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC02.MasterPact | Van | BMC131INC02PR1DAT1_Van | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BMC131INC02 Process Incomer MasterPact RMS Phase A Voltage | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC02.MasterPact | Vbn | BMC131INC02PR1DAT1_Vbn | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BMC131INC02 Process Incomer MasterPact RMS Phase B Voltage | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC02.MasterPact | Vcn | BMC131INC02PR1DAT1_Vcn | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BMC131INC02 Process Incomer MasterPact RMS Phase C Voltage | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC02.MasterPact | Ig | BMC131INC02PR1DAT1_Ig | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BMC131INC02 Process Incomer MasterPact Ground Fault Current | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC02.MasterPact | PwrAct | BMC131INC02PR1DAT1_PwrAct | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BMC131INC02 Process Incomer MasterPact Total Active Power | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC02.MasterPact | PwrRct | BMC131INC02PR1DAT1_PwrRct | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BMC131INC02 Process Incomer MasterPact Total Reactive Power | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC02.MasterPact | PwrApr | BMC131INC02PR1DAT1_PwrApr | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BMC131INC02 Process Incomer MasterPact Total Apparent Power | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC02.MasterPact | PF | BMC131INC02PR1DAT1_PF | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BMC131INC02 Process Incomer MasterPact Total Power Factor | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC02.MasterPact | VabTHD | BMC131INC02PR1DAT1_VabTHD | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BMC131INC02 Process Incomer MasterPact RMS Phase A to B Voltage Total Harmonic Distortion | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC02.MasterPact | VbcTHD | BMC131INC02PR1DAT1_VbcTHD | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BMC131INC02 Process Incomer MasterPact RMS Phase B to C Voltage Total Harmonic Distortion | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC02.MasterPact | VcaTHD | BMC131INC02PR1DAT1_VcaTHD | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BMC131INC02 Process Incomer MasterPact RMS Phase C to A Voltage Total Harmonic Distortion | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC02.MasterPact | VanTHD | BMC131INC02PR1DAT1_VanTHD | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BMC131INC02 Process Incomer MasterPact RMS Phase A Voltage Total Harmonic Distortion | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC02.MasterPact | VbnTHD | BMC131INC02PR1DAT1_VbnTHD | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BMC131INC02 Process Incomer MasterPact RMS Phase B Voltage Total Harmonic Distortion | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC02.MasterPact | VcnTHD | BMC131INC02PR1DAT1_VcnTHD | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BMC131INC02 Process Incomer MasterPact RMS Phase C Voltage Total Harmonic Distortion | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC02.MasterPact | IaTHD | BMC131INC02PR1DAT1_IaTHD | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BMC131INC02 Process Incomer MasterPact RMS Current on Phase A Total Harmonic Distortion | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC02.MasterPact | IbTHD | BMC131INC02PR1DAT1_IbTHD | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BMC131INC02 Process Incomer MasterPact RMS Current on Phase B Total Harmonic Distortion | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC02.MasterPact | IcTHD | BMC131INC02PR1DAT1_IcTHD | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BMC131INC02 Process Incomer MasterPact RMS Current on Phase C Total Harmonic Distortion | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC03.MasterPact | Frq | BMC131INC03PR1DAT1_Frq | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BMC131INC03 Process Incomer MasterPact Frequency | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC03.MasterPact | Ia | BMC131INC03PR1DAT1_Ia | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BMC131INC03 Process Incomer MasterPact RMS Current on Phase A | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC03.MasterPact | Ib | BMC131INC03PR1DAT1_Ib | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BMC131INC03 Process Incomer MasterPact RMS Current on Phase B | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC03.MasterPact | Ic | BMC131INC03PR1DAT1_Ic | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BMC131INC03 Process Incomer MasterPact RMS Current on Phase C | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC03.MasterPact | In | BMC131INC03PR1DAT1_In | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BMC131INC03 Process Incomer MasterPact RMS Current on Neutral | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC03.MasterPact | Vab | BMC131INC03PR1DAT1_Vab | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BMC131INC03 Process Incomer MasterPact RMS Phase A to B Voltage | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC03.MasterPact | Vbc | BMC131INC03PR1DAT1_Vbc | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BMC131INC03 Process Incomer MasterPact RMS Phase B to C Voltage | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC03.MasterPact | Vca | BMC131INC03PR1DAT1_Vca | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BMC131INC03 Process Incomer MasterPact RMS Phase C to A Voltage | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC03.MasterPact | Van | BMC131INC03PR1DAT1_Van | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BMC131INC03 Process Incomer MasterPact RMS Phase A Voltage | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC03.MasterPact | Vbn | BMC131INC03PR1DAT1_Vbn | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BMC131INC03 Process Incomer MasterPact RMS Phase B Voltage | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC03.MasterPact | Vcn | BMC131INC03PR1DAT1_Vcn | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BMC131INC03 Process Incomer MasterPact RMS Phase C Voltage | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC03.MasterPact | Ig | BMC131INC03PR1DAT1_Ig | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BMC131INC03 Process Incomer MasterPact Ground Fault Current | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC03.MasterPact | PwrAct | BMC131INC03PR1DAT1_PwrAct | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BMC131INC03 Process Incomer MasterPact Total Active Power | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC03.MasterPact | PwrRct | BMC131INC03PR1DAT1_PwrRct | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BMC131INC03 Process Incomer MasterPact Total Reactive Power | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC03.MasterPact | PwrApr | BMC131INC03PR1DAT1_PwrApr | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BMC131INC03 Process Incomer MasterPact Total Apparent Power | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC03.MasterPact | PF | BMC131INC03PR1DAT1_PF | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BMC131INC03 Process Incomer MasterPact Total Power Factor | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC03.MasterPact | VabTHD | BMC131INC03PR1DAT1_VabTHD | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BMC131INC03 Process Incomer MasterPact RMS Phase A to B Voltage Total Harmonic Distortion | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC03.MasterPact | VbcTHD | BMC131INC03PR1DAT1_VbcTHD | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BMC131INC03 Process Incomer MasterPact RMS Phase B to C Voltage Total Harmonic Distortion | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC03.MasterPact | VcaTHD | BMC131INC03PR1DAT1_VcaTHD | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BMC131INC03 Process Incomer MasterPact RMS Phase C to A Voltage Total Harmonic Distortion | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC03.MasterPact | VanTHD | BMC131INC03PR1DAT1_VanTHD | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BMC131INC03 Process Incomer MasterPact RMS Phase A Voltage Total Harmonic Distortion | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC03.MasterPact | VbnTHD | BMC131INC03PR1DAT1_VbnTHD | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BMC131INC03 Process Incomer MasterPact RMS Phase B Voltage Total Harmonic Distortion | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC03.MasterPact | VcnTHD | BMC131INC03PR1DAT1_VcnTHD | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BMC131INC03 Process Incomer MasterPact RMS Phase C Voltage Total Harmonic Distortion | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC03.MasterPact | IaTHD | BMC131INC03PR1DAT1_IaTHD | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BMC131INC03 Process Incomer MasterPact RMS Current on Phase A Total Harmonic Distortion | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC03.MasterPact | IbTHD | BMC131INC03PR1DAT1_IbTHD | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BMC131INC03 Process Incomer MasterPact RMS Current on Phase B Total Harmonic Distortion | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC03.MasterPact | IcTHD | BMC131INC03PR1DAT1_IcTHD | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BMC131INC03 Process Incomer MasterPact RMS Current on Phase C Total Harmonic Distortion | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC01.MasterPact | Frq | BMC131INC01PR1DAT1_Frq | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BMC131INC01 Process Incomer MasterPact Frequency | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC01.MasterPact | Ia | BMC131INC01PR1DAT1_Ia | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BMC131INC01 Process Incomer MasterPact RMS Current on Phase A | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC01.MasterPact | Ib | BMC131INC01PR1DAT1_Ib | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BMC131INC01 Process Incomer MasterPact RMS Current on Phase B | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC01.MasterPact | Ic | BMC131INC01PR1DAT1_Ic | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BMC131INC01 Process Incomer MasterPact RMS Current on Phase C | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC01.MasterPact | In | BMC131INC01PR1DAT1_In | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BMC131INC01 Process Incomer MasterPact RMS Current on Neutral | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC01.MasterPact | Vab | BMC131INC01PR1DAT1_Vab | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BMC131INC01 Process Incomer MasterPact RMS Phase A to B Voltage | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC01.MasterPact | Vbc | BMC131INC01PR1DAT1_Vbc | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BMC131INC01 Process Incomer MasterPact RMS Phase B to C Voltage | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC01.MasterPact | Vca | BMC131INC01PR1DAT1_Vca | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BMC131INC01 Process Incomer MasterPact RMS Phase C to A Voltage | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC01.MasterPact | Van | BMC131INC01PR1DAT1_Van | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BMC131INC01 Process Incomer MasterPact RMS Phase A Voltage | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC01.MasterPact | Vbn | BMC131INC01PR1DAT1_Vbn | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BMC131INC01 Process Incomer MasterPact RMS Phase B Voltage | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC01.MasterPact | Vcn | BMC131INC01PR1DAT1_Vcn | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BMC131INC01 Process Incomer MasterPact RMS Phase C Voltage | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC01.MasterPact | Ig | BMC131INC01PR1DAT1_Ig | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BMC131INC01 Process Incomer MasterPact Ground Fault Current | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC01.MasterPact | PwrAct | BMC131INC01PR1DAT1_PwrAct | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BMC131INC01 Process Incomer MasterPact Total Active Power | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC01.MasterPact | PwrRct | BMC131INC01PR1DAT1_PwrRct | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BMC131INC01 Process Incomer MasterPact Total Reactive Power | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC01.MasterPact | PwrApr | BMC131INC01PR1DAT1_PwrApr | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BMC131INC01 Process Incomer MasterPact Total Apparent Power | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC01.MasterPact | PF | BMC131INC01PR1DAT1_PF | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BMC131INC01 Process Incomer MasterPact Total Power Factor | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC01.MasterPact | VabTHD | BMC131INC01PR1DAT1_VabTHD | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BMC131INC01 Process Incomer MasterPact RMS Phase A to B Voltage Total Harmonic Distortion | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC01.MasterPact | VbcTHD | BMC131INC01PR1DAT1_VbcTHD | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BMC131INC01 Process Incomer MasterPact RMS Phase B to C Voltage Total Harmonic Distortion | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC01.MasterPact | VcaTHD | BMC131INC01PR1DAT1_VcaTHD | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BMC131INC01 Process Incomer MasterPact RMS Phase C to A Voltage Total Harmonic Distortion | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC01.MasterPact | VanTHD | BMC131INC01PR1DAT1_VanTHD | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BMC131INC01 Process Incomer MasterPact RMS Phase A Voltage Total Harmonic Distortion | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC01.MasterPact | VbnTHD | BMC131INC01PR1DAT1_VbnTHD | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BMC131INC01 Process Incomer MasterPact RMS Phase B Voltage Total Harmonic Distortion | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC01.MasterPact | VcnTHD | BMC131INC01PR1DAT1_VcnTHD | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BMC131INC01 Process Incomer MasterPact RMS Phase C Voltage Total Harmonic Distortion | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC01.MasterPact | IaTHD | BMC131INC01PR1DAT1_IaTHD | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BMC131INC01 Process Incomer MasterPact RMS Current on Phase A Total Harmonic Distortion | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC01.MasterPact | IbTHD | BMC131INC01PR1DAT1_IbTHD | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BMC131INC01 Process Incomer MasterPact RMS Current on Phase B Total Harmonic Distortion | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC01.MasterPact | IcTHD | BMC131INC01PR1DAT1_IcTHD | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BMC131INC01 Process Incomer MasterPact RMS Current on Phase C Total Harmonic Distortion | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC02.MasterPact | Frq | BMC131INC02PR1DAT1_Frq | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BMC131INC02 Process Incomer MasterPact Frequency | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC02.MasterPact | Ia | BMC131INC02PR1DAT1_Ia | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BMC131INC02 Process Incomer MasterPact RMS Current on Phase A | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC02.MasterPact | Ib | BMC131INC02PR1DAT1_Ib | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BMC131INC02 Process Incomer MasterPact RMS Current on Phase B | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.BMC131.INC02.MasterPact | Ic | BMC131INC02PR1DAT1_Ic | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BMC131INC02 Process Incomer MasterPact RMS Current on Phase C | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1101 | 0 | BPP1101PIC01_PV | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BPP1101 Pressure Controller Process Variable | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1101 | 0 | BPP1101PIC01_SP | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BPP1101 Pressure Controller Setpoint | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1103 | 0 | BPP1103LIC01_PV | BR4_Cluster1 | TRN_PERIODIC | 0:00 | West Turkeys Nest Level Controller Process Variable | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1103 | 0 | BPP1103LIC01_SP | BR4_Cluster1 | TRN_PERIODIC | 0:00 | West Turkeys Nest Level Controller Setpoint | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BSTD1106 | 0 | BSTD1106FIC01_PV | BR4_Cluster1 | TRN_PERIODIC | 0:00 | West Turkeys Nest LME Standpipe Flow Controller Process Variable | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BSTD1106 | 0 | BSTD1106FIC01_SP | BR4_Cluster1 | TRN_PERIODIC | 0:00 | West Turkeys Nest LME Standpipe Flow Controller Setpoint | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BSTD1107 | 0 | BSTD1107FIC01_PV | BR4_Cluster1 | TRN_PERIODIC | 0:00 | West Turkeys Nest HME Standpipe Flow Controller Process Variable | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BSTD1107 | 0 | BSTD1107FIC01_SP | BR4_Cluster1 | TRN_PERIODIC | 0:00 | West Turkeys Nest HME Standpipe Flow Controller Setpoint | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.UTILITIES.WATER.BS1.BTY1502.FieldIO.FT01 | 0 | BTY1502FT01_PV | BR4_Cluster1 | TRN_PERIODIC | 0:00 | West Turkeys Nest Flow Rate (m3/h) | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.UTILITIES.WATER.BS1.BTY1502.FieldIO.FT03 | 0 | BTY1502FT03_PV | BR4_Cluster1 | TRN_PERIODIC | 0:00 | West Turkeys Nest Flow Rate (m3/h) | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.UTILITIES.WATER.BS1.BTY1502.FieldIO.PT01 | 0 | BTY1502PT01_PV | BR4_Cluster1 | TRN_PERIODIC | 0:00 | West Turkeys Nest Pressure (kPa) | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.UTILITIES.WATER.BS1.BTY1502.FieldIO.PT03 | 0 | BTY1502PT03_PV | BR4_Cluster1 | TRN_PERIODIC | 0:00 | West Turkeys Nest Pressure (kPa) | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BSTD1106.FieldIO.FT03 | 0 | BSTD1106FT03_PV | BR4_Cluster1 | TRN_PERIODIC | 0:00 | West Turkeys Nest LME Standpipe Flow Rate (m3/h) | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BSTD1107 | 0 | BSTD1107FT02_PV | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSTD1107FT02 Flow Rate (m3/h) | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BSTD1106.FV03.FieldIO.ZT01 | 0 | BSTD1106FV03ZT01_PV | BR4_Cluster1 | TRN_PERIODIC | 0:00 | West Turkeys Nest LME Standpipe Flow Valve Position (%) | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BSTD1107.FV02.FieldIO.ZT01 | 0 | BSTD1107FV02ZT01_PV | BR4_Cluster1 | TRN_PERIODIC | 0:00 | West Turkeys Nest HME Standpipe Flow Valve Position (%) | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BPP1106.FieldIO.PT01 | 0 | BPP1106PT01_PV | BR4_Cluster1 | TRN_PERIODIC | 0:00 | HME & LME Standpipe Pump 3 Pressure (kPa) | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BPP1107.FieldIO.PT02 | 0 | BPP1107PT02_PV | BR4_Cluster1 | TRN_PERIODIC | 0:00 | HME & LME Standpipe Pump 4 Pressure (kPa) | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1101.FieldIO.PT03 | 0 | BPP1101PT03_PV | BR4_Cluster1 | TRN_PERIODIC | 0:00 | Production Plant and NPI Water Supply Pump 1 Discharge Pressure (kPa) | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1102.FieldIO.PT04 | 0 | BPP1102PT04_PV | BR4_Cluster1 | TRN_PERIODIC | 0:00 | Production Plant and NPI Water Supply Pump 2 Discharge Pressure (kPa) | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1101.FieldIO.FT01 | 0 | BPP1101FT01_PV | BR4_Cluster1 | TRN_PERIODIC | 0:00 | Production Plant and NPI Water Supply Pump 1 Flow Rate (m3/h) | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.UTILITIES.WATER.BS1.BTY1502.FieldIO.FT02 | 0 | BTY1502FT02_PV | BR4_Cluster1 | TRN_PERIODIC | 0:00 | West Turkeys Nest Flow Rate (m3/h) | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.UTILITIES.WATER.BS1.BTY1502.FV01.FieldIO.ZT01 | 0 | BTY1502FV01ZT01_PV | BR4_Cluster1 | TRN_PERIODIC | 0:00 | West Turkeys Nest Flow Valve Position (%) | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1101.FieldIO.PT10 | 0 | BPP1101PT10_PV | BR4_Cluster1 | TRN_PERIODIC | 0:00 | Production Plant and NPI Water Supply Pump 1 Discharge Pressure 1 (kPa) | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1101.FieldIO.PT11 | 0 | BPP1101PT11_PV | BR4_Cluster1 | TRN_PERIODIC | 0:00 | Production Plant and NPI Water Supply Pump 1 Discharge Pressure 2 (kPa) | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1103.FieldIO.FT03 | 0 | BPP1103FT03_PV | BR4_Cluster1 | TRN_PERIODIC | 0:00 | Water Transfer Pump 1 Flow Rate (m3/h) | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1103.FieldIO.PT05 | 0 | BPP1103PT05_PV | BR4_Cluster1 | TRN_PERIODIC | 0:00 | Water Transfer Pump 1 Discharge Pressure (kPa) | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1104.FieldIO.FT04 | 0 | BPP1104FT04_PV | BR4_Cluster1 | TRN_PERIODIC | 0:00 | Water Transfer Pump 2 Flow Rate (m3/h) | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1104.FieldIO.PT06 | 0 | BPP1104PT06_PV | BR4_Cluster1 | TRN_PERIODIC | 0:00 | Water Transfer Pump 2 Discharge Pressure (kPa) | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1105.FieldIO.FT05 | 0 | BPP1105FT05_PV | BR4_Cluster1 | TRN_PERIODIC | 0:00 | Water Transfer Pump 3 Flow Rate (m3/h) | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1105.FieldIO.PT07 | 0 | BPP1105PT07_PV | BR4_Cluster1 | TRN_PERIODIC | 0:00 | Water Transfer Pump 3 Discharge Pressure (kPa) | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1103.FieldIO.FT06 | 0 | BPP1103FT06_PV | BR4_Cluster1 | TRN_PERIODIC | 0:00 | Water Transfer Pump 1 Flow Rate (m3/h) | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1103.FieldIO.PT08 | 0 | BPP1103PT08_PV | BR4_Cluster1 | TRN_PERIODIC | 0:00 | Water Transfer Pump 1 Discharge Pressure (kPa) | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.UTILITIES.WATER.BS1.BTY1502.FieldIO.LT01 | 0 | BTY1502LT01_PV | BR4_Cluster1 | TRN_PERIODIC | 0:00 | West Turkeys Nest Level 1 (mm) | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.UTILITIES.WATER.BS1.BTY1502.FieldIO.LT02 | 0 | BTY1502LT02_PV | BR4_Cluster1 | TRN_PERIODIC | 0:00 | West Turkeys Nest Level 2 (mm) | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.UTILITIES.WATER.BS1.P3FIREWATER.BTK2101.FieldIO.LT01 | 0 | BTK2101LT01_PV | BR4_Cluster1 | TRN_PERIODIC | 0:00 | NPI Fire Water Tank 1 Tank Level (%) | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.UTILITIES.WATER.BS1.P3FIREWATER.BTK2102.FieldIO.LT01 | 0 | BTK2102LT01_PV | BR4_Cluster1 | TRN_PERIODIC | 0:00 | NPI Fire Water Tank 2 Tank Level (%) | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1101.FieldIO.FT01 | 0 | BPP1101FT02_PV | BR4_Cluster1 | TRN_PERIODIC | 0:00 | Production Plant and NPI Water Supply Pump 1 Flow Rate (m3/h) | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.BC02.Cordex | SysV | BSR131BC02CordexDAT1_SysV | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131BC02 Battery Charger Cordex System Voltage | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.BC02.Cordex | TotLdI | BSR131BC02CordexDAT1_TotLdI | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131BC02 Battery Charger Cordex Total Load Current | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.BC02.Cordex | BatV | BSR131BC02CordexDAT1_BatV | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131BC02 Battery Charger Cordex Battery Voltage | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.BC02.Cordex | BatI | BSR131BC02CordexDAT1_BatI | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131BC02 Battery Charger Cordex Battery Current | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.BC02.Cordex | TotRecOPI | BSR131BC02CordexDAT1_TotRecOPI | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131BC02 Battery Charger Cordex Total Rectifier O/P Current | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.BC02.Cordex | TotOPPwr | BSR131BC02CordexDAT1_TotOPPwr | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131BC02 Battery Charger Cordex Total Output Power | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.BC02.Cordex | TotCap1 | BSR131BC02CordexDAT1_TotCap1 | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131BC02 Battery Charger Cordex Total Capacity Installed | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.BC02.Cordex | TotCap2 | BSR131BC02CordexDAT1_TotCap2 | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131BC02 Battery Charger Cordex Total Capacity Installed | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.BC02.Cordex | CapRemn1 | BSR131BC02CordexDAT1_CapRemn1 | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131BC02 Battery Charger Cordex Estimated Capacity Remaining | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.BC02.Cordex | CapRemn2 | BSR131BC02CordexDAT1_CapRemn2 | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131BC02 Battery Charger Cordex Estimated Capacity Remaining | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.BC02.Cordex | AvgDCOPV | BSR131BC02CordexDAT1_AvgDCOPV | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131BC02 Battery Charger Cordex Average DC Bus Output Voltage | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.BC02.Cordex | Phs1V | BSR131BC02CordexDAT1_Phs1V | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131BC02 Battery Charger Cordex Estimated AC Phase 1 Voltage | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.BC02.Cordex | Phs2V | BSR131BC02CordexDAT1_Phs2V | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131BC02 Battery Charger Cordex Estimated AC Phase 2 Voltage | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.BC02.Cordex | Phs3V | BSR131BC02CordexDAT1_Phs3V | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131BC02 Battery Charger Cordex Estimated AC Phase 3 Voltage | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.BC02.Cordex | CapRqd | BSR131BC02CordexDAT1_CapRqd | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131BC02 Battery Charger Cordex Estimated Required Capacity | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.BC02.Cordex | CapAvl | BSR131BC02CordexDAT1_CapAvl | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131BC02 Battery Charger Cordex Estimated Available Capacity | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.BC02.Cordex | RedunCap | BSR131BC02CordexDAT1_RedunCap | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131BC02 Battery Charger Cordex Estimated Redundant Capacity | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.BC02.Cordex | SbyCap | BSR131BC02CordexDAT1_SbyCap | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131BC02 Battery Charger Cordex Estimated Standby Capacity | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.BC02.Cordex | BatTmp | BSR131BC02CordexDAT1_BatTmp | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131BC02 Battery Charger Cordex Battery Temperature | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.BC02.Cordex | StgCharge | BSR131BC02CordexDAT1_StgCharge | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131BC02 Battery Charger Cordex Estimated State of Charge | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.BC02.Cordex | BatRunTm | BSR131BC02CordexDAT1_BatRunTm | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131BC02 Battery Charger Cordex Estimated Battery Runtime | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.BC02.Cordex | MaxRecAmbTmp | BSR131BC02CordexDAT1_MaxRecAmbTmp | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131BC02 Battery Charger Cordex Maximum Rectifier Ambient Temperature | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1101.VS01 | Iavg | BPP1101VS01DAT1_Iavg | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BPP1101VS01 VVVF Average Current (A) | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1101.VS01 | Spd | BPP1101VS01DAT1_Spd | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BPP1101VS01 VVVF Speed (%) | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1101.VS01 | Trq | BPP1101VS01DAT1_Trq | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BPP1101VS01 VVVF Torque (%) | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1101.VS01 | Frq | BPP1101VS01DAT1_Frq | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BPP1101VS01 VVVF Frequency (Hz) | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1101.VS01 | Pwr | BPP1101VS01DAT1_Pwr | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BPP1101VS01 VVVF Power (kW) | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1101.VS01 | Tmp | BPP1101VS01DAT1_Tmp | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BPP1101VS01 VVVF Temperature (degC) | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1101.VS01 | SpdEng | BPP1101VS01DAT1_SpdEng | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BPP1101VS01 VVVF Speed (rpm) | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1102.VS01 | Iavg | BPP1102VS01DAT1_Iavg | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BPP1102VS01 VVVF Average Current (A) | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1102.VS01 | Spd | BPP1102VS01DAT1_Spd | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BPP1102VS01 VVVF Speed (%) | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1102.VS01 | Trq | BPP1102VS01DAT1_Trq | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BPP1102VS01 VVVF Torque (%) | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1102.VS01 | Frq | BPP1102VS01DAT1_Frq | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BPP1102VS01 VVVF Frequency (Hz) | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1102.VS01 | Pwr | BPP1102VS01DAT1_Pwr | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BPP1102VS01 VVVF Power (kW) | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1102.VS01 | Tmp | BPP1102VS01DAT1_Tmp | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BPP1102VS01 VVVF Temperature (degC) | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1102.VS01 | SpdEng | BPP1102VS01DAT1_SpdEng | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BPP1102VS01 VVVF Speed (rpm) | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1103.VS01 | Iavg | BPP1103VS01DAT1_Iavg | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BPP1103VS01 VVVF Average Current (A) | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1103.VS01 | Spd | BPP1103VS01DAT1_Spd | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BPP1103VS01 VVVF Speed (%) | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1103.VS01 | Trq | BPP1103VS01DAT1_Trq | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BPP1103VS01 VVVF Torque (%) | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1103.VS01 | Frq | BPP1103VS01DAT1_Frq | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BPP1103VS01 VVVF Frequency (Hz) | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1103.VS01 | Pwr | BPP1103VS01DAT1_Pwr | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BPP1103VS01 VVVF Power (kW) | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1103.VS01 | Tmp | BPP1103VS01DAT1_Tmp | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BPP1103VS01 VVVF Temperature (degC) | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1103.VS01 | SpdEng | BPP1103VS01DAT1_SpdEng | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BPP1103VS01 VVVF Speed (rpm) | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1104.VS01 | Iavg | BPP1104VS01DAT1_Iavg | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BPP1104VS01 VVVF Average Current (A) | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1104.VS01 | Spd | BPP1104VS01DAT1_Spd | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BPP1104VS01 VVVF Speed (%) | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1104.VS01 | Trq | BPP1104VS01DAT1_Trq | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BPP1104VS01 VVVF Torque (%) | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1104.VS01 | Frq | BPP1104VS01DAT1_Frq | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BPP1104VS01 VVVF Frequency (Hz) | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1104.VS01 | Pwr | BPP1104VS01DAT1_Pwr | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BPP1104VS01 VVVF Power (kW) | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1104.VS01 | Tmp | BPP1104VS01DAT1_Tmp | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BPP1104VS01 VVVF Temperature (degC) | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1104.VS01 | SpdEng | BPP1104VS01DAT1_SpdEng | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BPP1104VS01 VVVF Speed (rpm) | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1105.VS01 | Iavg | BPP1105VS01DAT1_Iavg | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BPP1105VS01 VVVF Average Current (A) | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1105.VS01 | Spd | BPP1105VS01DAT1_Spd | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BPP1105VS01 VVVF Speed (%) | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1105.VS01 | Trq | BPP1105VS01DAT1_Trq | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BPP1105VS01 VVVF Torque (%) | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1105.VS01 | Frq | BPP1105VS01DAT1_Frq | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BPP1105VS01 VVVF Frequency (Hz) | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1105.VS01 | Pwr | BPP1105VS01DAT1_Pwr | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BPP1105VS01 VVVF Power (kW) | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1105.VS01 | Tmp | BPP1105VS01DAT1_Tmp | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BPP1105VS01 VVVF Temperature (degC) | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1105.VS01 | SpdEng | BPP1105VS01DAT1_SpdEng | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BPP1105VS01 VVVF Speed (rpm) | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1106.VS01 | Iavg | BPP1106VS01DAT1_Iavg | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BPP1106VS01 VVVF Average Current (A) | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1106.VS01 | Spd | BPP1106VS01DAT1_Spd | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BPP1106VS01 VVVF Speed (%) | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1106.VS01 | Trq | BPP1106VS01DAT1_Trq | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BPP1106VS01 VVVF Torque (%) | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1106.VS01 | Frq | BPP1106VS01DAT1_Frq | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BPP1106VS01 VVVF Frequency (Hz) | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1106.VS01 | Pwr | BPP1106VS01DAT1_Pwr | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BPP1106VS01 VVVF Power (kW) | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1106.VS01 | Tmp | BPP1106VS01DAT1_Tmp | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BPP1106VS01 VVVF Temperature (degC) | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1106.VS01 | SpdEng | BPP1106VS01DAT1_SpdEng | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BPP1106VS01 VVVF Speed (rpm) | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1107.VS01 | Iavg | BPP1107VS01DAT1_Iavg | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BPP1107VS01 VVVF Average Current (A) | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1107.VS01 | Spd | BPP1107VS01DAT1_Spd | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BPP1107VS01 VVVF Speed (%) | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1107.VS01 | Trq | BPP1107VS01DAT1_Trq | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BPP1107VS01 VVVF Torque (%) | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1107.VS01 | Frq | BPP1107VS01DAT1_Frq | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BPP1107VS01 VVVF Frequency (Hz) | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1107.VS01 | Pwr | BPP1107VS01DAT1_Pwr | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BPP1107VS01 VVVF Power (kW) | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1107.VS01 | Tmp | BPP1107VS01DAT1_Tmp | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BPP1107VS01 VVVF Temperature (degC) | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1107.VS01 | SpdEng | BPP1107VS01DAT1_SpdEng | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BPP1107VS01 VVVF Speed (rpm) | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1101 |  | BPP1101PIC01_KD | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BPP1101 Pressure Controller Derivative Gain | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1101 |  | BPP1101PIC01_KI | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BPP1101 Pressure Controller Integral Gain | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1101 |  | BPP1101PIC01_KP | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BPP1101 Pressure Controller Proportional Gain | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1101 |  | BPP1101PIC01_OP | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BPP1101 Pressure Controller Output Value | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWD1.BPP1101 |  | BPP1101PIC01_OPMan | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BPP1101 Pressure Controller Manual Setpoint | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1103 |  | BPP1103LIC01_KD | BR4_Cluster1 | TRN_PERIODIC | 0:00 | West Turkeys Nest Level Controller Derivative Gain | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1103 |  | BPP1103LIC01_KI | BR4_Cluster1 | TRN_PERIODIC | 0:00 | West Turkeys Nest Level Controller Integral Gain | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1103 |  | BPP1103LIC01_KP | BR4_Cluster1 | TRN_PERIODIC | 0:00 | West Turkeys Nest Level Controller Proportional Gain | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1103 |  | BPP1103LIC01_OP | BR4_Cluster1 | TRN_PERIODIC | 0:00 | West Turkeys Nest Level Controller Output Value | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.UTILITIES.WATER.BS1.RWT.BPP1103 |  | BPP1103LIC01_OPMan | BR4_Cluster1 | TRN_PERIODIC | 0:00 | West Turkeys Nest Level Controller Manual Setpoint | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BSTD1106 |  | BSTD1106FIC01_KD | BR4_Cluster1 | TRN_PERIODIC | 0:00 | West Turkeys Nest LME Standpipe Flow Controller Derivative Gain | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BSTD1106 |  | BSTD1106FIC01_KI | BR4_Cluster1 | TRN_PERIODIC | 0:00 | West Turkeys Nest LME Standpipe Flow Controller Integral Gain | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BSTD1106 |  | BSTD1106FIC01_KP | BR4_Cluster1 | TRN_PERIODIC | 0:00 | West Turkeys Nest LME Standpipe Flow Controller Proportional Gain | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BSTD1106 |  | BSTD1106FIC01_OP | BR4_Cluster1 | TRN_PERIODIC | 0:00 | West Turkeys Nest LME Standpipe Flow Controller Output Value | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BSTD1106 |  | BSTD1106FIC01_OPMan | BR4_Cluster1 | TRN_PERIODIC | 0:00 | West Turkeys Nest LME Standpipe Flow Controller Manual Setpoint | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BSTD1107 |  | BSTD1107FIC01_KD | BR4_Cluster1 | TRN_PERIODIC | 0:00 | West Turkeys Nest HME Standpipe Flow Controller Derivative Gain | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BSTD1107 |  | BSTD1107FIC01_KI | BR4_Cluster1 | TRN_PERIODIC | 0:00 | West Turkeys Nest HME Standpipe Flow Controller Integral Gain | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BSTD1107 |  | BSTD1107FIC01_KP | BR4_Cluster1 | TRN_PERIODIC | 0:00 | West Turkeys Nest HME Standpipe Flow Controller Proportional Gain | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BSTD1107 |  | BSTD1107FIC01_OP | BR4_Cluster1 | TRN_PERIODIC | 0:00 | West Turkeys Nest HME Standpipe Flow Controller Output Value | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.UTILITIES.WATER.BS1.STD1.BSTD1107 |  | BSTD1107FIC01_OPMan | BR4_Cluster1 | TRN_PERIODIC | 0:00 | West Turkeys Nest HME Standpipe Flow Controller Manual Setpoint | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.BC02.BACS | AlmID1 | BSR131BC02BACSDAT1_AlmID1 | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131BC02 Battery Charger BACS Alarm ID 1 | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.BC02.BACS | AlmID2 | BSR131BC02BACSDAT1_AlmID2 | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131BC02 Battery Charger BACS Alarm ID 2 | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.BC02.BACS | AlmID3 | BSR131BC02BACSDAT1_AlmID3 | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131BC02 Battery Charger BACS Alarm ID 3 | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.BC02.BACS | NumStr | BSR131BC02BACSDAT1_NumStr | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131BC02 Battery Charger BACS Number of BACS Strings | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.BC02.BACS | NumMod | BSR131BC02BACSDAT1_NumMod | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131BC02 Battery Charger BACS Number of BACS Modules | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.BC02.BACS | Mod1AlmID | BSR131BC02BACSDAT1_Mod1AlmID | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131BC02 Battery Charger BACS Module 1 Alarm ID | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.BC02.BACS | Mod2AlmID | BSR131BC02BACSDAT1_Mod2AlmID | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131BC02 Battery Charger BACS Module 2 Alarm ID | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.BC02.BACS | Mod3AlmID | BSR131BC02BACSDAT1_Mod3AlmID | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131BC02 Battery Charger BACS Module 3 Alarm ID | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.BC02.BACS | Mod4AlmID | BSR131BC02BACSDAT1_Mod4AlmID | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131BC02 Battery Charger BACS Module 4 Alarm ID | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.BC02.BACS | Mod5AlmID | BSR131BC02BACSDAT1_Mod5AlmID | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131BC02 Battery Charger BACS Module 5 Alarm ID | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.BC02.BACS | Mod6AlmID | BSR131BC02BACSDAT1_Mod6AlmID | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131BC02 Battery Charger BACS Module 6 Alarm ID | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.BC02.BACS | Mod7AlmID | BSR131BC02BACSDAT1_Mod7AlmID | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131BC02 Battery Charger BACS Module 7 Alarm ID | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.BC02.BACS | Mod8AlmID | BSR131BC02BACSDAT1_Mod8AlmID | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131BC02 Battery Charger BACS Module 8 Alarm ID | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.BC02.BACS | Mod9AlmID | BSR131BC02BACSDAT1_Mod9AlmID | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131BC02 Battery Charger BACS Module 9 Alarm ID | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.UPScale | StsID | BSR131UP01DAT1_StsID | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS Status ID | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.UPScale | OPPhs1Pwr | BSR131UP01DAT1_OPPhs1Pwr | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS Output Power Phase 1 (%) | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.UPScale | OPPhs2Pwr | BSR131UP01DAT1_OPPhs2Pwr | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS Output Power Phase 2 (%) | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.UPScale | OPPhs3Pwr | BSR131UP01DAT1_OPPhs3Pwr | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS Output Power Phase 3 (%) | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.UPScale | BatCap | BSR131UP01DAT1_BatCap | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS Battery Capacity (%) | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.UPScale | InFrqPhs1 | BSR131UP01DAT1_InFrqPhs1 | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS Input Frequency Phase 1 (Hz) | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.UPScale | InFrqPhs2 | BSR131UP01DAT1_InFrqPhs2 | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS Input Frequency Phase 2 (Hz) | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.UPScale | InFrqPhs3 | BSR131UP01DAT1_InFrqPhs3 | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS Input Frequency Phase 3 (Hz) | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.UPScale | PwrFltCnt | BSR131UP01DAT1_PwrFltCnt | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS Power Fail Counter | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.UPScale | ManBypCls | BSR131UP01DAT1_ManBypCls | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS Manual Bypass Switch Closed | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.UPScale | OPVPhs1 | BSR131UP01DAT1_OPVPhs1 | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS Output Voltage Phase 1 (V) | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.UPScale | OPVPhs2 | BSR131UP01DAT1_OPVPhs2 | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS Output Voltage Phase 2 (V) | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.UPScale | OPVPhs3 | BSR131UP01DAT1_OPVPhs3 | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS Output Voltage Phase 3 (V) | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.UPScale | OPIPhs1 | BSR131UP01DAT1_OPIPhs1 | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS Output Current Phase 1 (A) | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.UPScale | OPIPhs2 | BSR131UP01DAT1_OPIPhs2 | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS Output Current Phase 2 (A) | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.UPScale | OPIPhs3 | BSR131UP01DAT1_OPIPhs3 | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS Output Current Phase 3 (A) | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.UPScale | TrueOPPwrPhs1 | BSR131UP01DAT1_TrueOPPwrPhs1 | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS True Output Power Phase 1 (kW) | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.UPScale | TrueOPPwrPhs2 | BSR131UP01DAT1_TrueOPPwrPhs2 | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS True Output Power Phase 2 (kW) | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.UPScale | TrueOPPwrPhs3 | BSR131UP01DAT1_TrueOPPwrPhs3 | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS True Output Power Phase 3 (kW) | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.UPScale | BatI | BSR131UP01DAT1_BatI | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS Battery Current (A) | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.UPScale | OFFrq | BSR131UP01DAT1_OFFrq | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS Output Frequency (Hz) | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.UPScale | BypFrq | BSR131UP01DAT1_BypFrq | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS Bypass Frequency (Hz) | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.UPScale | BypVPhs1 | BSR131UP01DAT1_BypVPhs1 | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS Bypass Voltage Phase 1 (V) | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.UPScale | BypVPhs2 | BSR131UP01DAT1_BypVPhs2 | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS Bypass Voltage Phase 2 (V) | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.UPScale | BypVPhs3 | BSR131UP01DAT1_BypVPhs3 | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS Bypass Voltage Phase 3 (V) | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.UPScale | BatCnd | BSR131UP01DAT1_BatCnd | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS Battery Condition (0 = good, 1 = weak, 2 = replace) | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.BC02.Cordex | AlmID1 | BSR131BC02CordexDAT1_AlmID1 | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131BC02 Battery Charger Cordex Alarm ID 1 | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.BC02.Cordex | AlmID2 | BSR131BC02CordexDAT1_AlmID2 | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131BC02 Battery Charger Cordex Alarm ID 2 | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.BC02.Cordex | AlmID3 | BSR131BC02CordexDAT1_AlmID3 | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131BC02 Battery Charger Cordex Alarm ID 3 | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | AlmID1 | BSR131UP01BACSDAT1_AlmID1 | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS Alarm ID 1 | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | AlmID2 | BSR131UP01BACSDAT1_AlmID2 | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS Alarm ID 2 | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | AlmID3 | BSR131UP01BACSDAT1_AlmID3 | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS Alarm ID 3 | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | NumStr | BSR131UP01BACSDAT1_NumStr | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS Number of BACS Strings | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | NumMod | BSR131UP01BACSDAT1_NumMod | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS Number of BACS String 1 Modules | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod1AlmID | BSR131UP01BACSDAT1_Str1Mod1AlmID | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 1 Module 1 Alarm ID | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod2AlmID | BSR131UP01BACSDAT1_Str1Mod2AlmID | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 1 Module 2 Alarm ID | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod3AlmID | BSR131UP01BACSDAT1_Str1Mod3AlmID | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 1 Module 3 Alarm ID | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod4AlmID | BSR131UP01BACSDAT1_Str1Mod4AlmID | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 1 Module 4 Alarm ID | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod5AlmID | BSR131UP01BACSDAT1_Str1Mod5AlmID | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 1 Module 5 Alarm ID | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod6AlmID | BSR131UP01BACSDAT1_Str1Mod6AlmID | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 1 Module 6 Alarm ID | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod7AlmID | BSR131UP01BACSDAT1_Str1Mod7AlmID | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 1 Module 7 Alarm ID | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod8AlmID | BSR131UP01BACSDAT1_Str1Mod8AlmID | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 1 Module 8 Alarm ID | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod9AlmID | BSR131UP01BACSDAT1_Str1Mod9AlmID | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 1 Module 9 Alarm ID | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod10AlmID | BSR131UP01BACSDAT1_Str1Mod10AlmID | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 1 Module 10 Alarm ID | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod11AlmID | BSR131UP01BACSDAT1_Str1Mod11AlmID | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 1 Module 11 Alarm ID | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod12AlmID | BSR131UP01BACSDAT1_Str1Mod12AlmID | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 1 Module 12 Alarm ID | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod13AlmID | BSR131UP01BACSDAT1_Str1Mod13AlmID | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 1 Module 13 Alarm ID | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod14AlmID | BSR131UP01BACSDAT1_Str1Mod14AlmID | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 1 Module 14 Alarm ID | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod15AlmID | BSR131UP01BACSDAT1_Str1Mod15AlmID | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 1 Module 15 Alarm ID | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod16AlmID | BSR131UP01BACSDAT1_Str1Mod16AlmID | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 1 Module 16 Alarm ID | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod17AlmID | BSR131UP01BACSDAT1_Str1Mod17AlmID | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 1 Module 17 Alarm ID | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod18AlmID | BSR131UP01BACSDAT1_Str1Mod18AlmID | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 1 Module 18 Alarm ID | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod19AlmID | BSR131UP01BACSDAT1_Str1Mod19AlmID | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 1 Module 19 Alarm ID | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod20AlmID | BSR131UP01BACSDAT1_Str1Mod20AlmID | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 1 Module 20 Alarm ID | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod21AlmID | BSR131UP01BACSDAT1_Str1Mod21AlmID | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 1 Module 21 Alarm ID | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod22AlmID | BSR131UP01BACSDAT1_Str2Mod22AlmID | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 2 Module 22 Alarm ID | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod22AlmID | BSR131UP01BACSDAT1_Str1Mod22AlmID | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 1 Module 22 Alarm ID | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod23AlmID | BSR131UP01BACSDAT1_Str2Mod23AlmID | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 2 Module 23 Alarm ID | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod23AlmID | BSR131UP01BACSDAT1_Str1Mod23AlmID | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 1 Module 23 Alarm ID | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod24AlmID | BSR131UP01BACSDAT1_Str2Mod24AlmID | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 2 Module 24 Alarm ID | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod24AlmID | BSR131UP01BACSDAT1_Str1Mod24AlmID | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 1 Module 24 Alarm ID | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod25AlmID | BSR131UP01BACSDAT1_Str2Mod25AlmID | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 2 Module 25 Alarm ID | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod25AlmID | BSR131UP01BACSDAT1_Str1Mod25AlmID | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 1 Module 25 Alarm ID | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod26AlmID | BSR131UP01BACSDAT1_Str2Mod26AlmID | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 2 Module 26 Alarm ID | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod26AlmID | BSR131UP01BACSDAT1_Str1Mod26AlmID | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 1 Module 26 Alarm ID | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod27AlmID | BSR131UP01BACSDAT1_Str2Mod27AlmID | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 2 Module 27 Alarm ID | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod27AlmID | BSR131UP01BACSDAT1_Str1Mod27AlmID | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 1 Module 27 Alarm ID | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod28AlmID | BSR131UP01BACSDAT1_Str2Mod28AlmID | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 2 Module 28 Alarm ID | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod28AlmID | BSR131UP01BACSDAT1_Str1Mod28AlmID | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 1 Module 28 Alarm ID | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod29AlmID | BSR131UP01BACSDAT1_Str2Mod29AlmID | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 2 Module 29 Alarm ID | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod29AlmID | BSR131UP01BACSDAT1_Str1Mod29AlmID | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 1 Module 29 Alarm ID | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod30AlmID | BSR131UP01BACSDAT1_Str2Mod30AlmID | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 2 Module 30 Alarm ID | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod30AlmID | BSR131UP01BACSDAT1_Str1Mod30AlmID | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 1 Module 30 Alarm ID | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod31AlmID | BSR131UP01BACSDAT1_Str2Mod31AlmID | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 2 Module 31 Alarm ID | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod31AlmID | BSR131UP01BACSDAT1_Str1Mod31AlmID | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 1 Module 31 Alarm ID | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod32AlmID | BSR131UP01BACSDAT1_Str2Mod32AlmID | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 2 Module 32 Alarm ID | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod32AlmID | BSR131UP01BACSDAT1_Str1Mod32AlmID | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 1 Module 32 Alarm ID | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod33AlmID | BSR131UP01BACSDAT1_Str2Mod33AlmID | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 2 Module 33 Alarm ID | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod33AlmID | BSR131UP01BACSDAT1_Str1Mod33AlmID | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 1 Module 33 Alarm ID | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod34AlmID | BSR131UP01BACSDAT1_Str2Mod34AlmID | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 2 Module 34 Alarm ID | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod34AlmID | BSR131UP01BACSDAT1_Str1Mod34AlmID | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 1 Module 34 Alarm ID | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod35AlmID | BSR131UP01BACSDAT1_Str2Mod35AlmID | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 2 Module 35 Alarm ID | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod35AlmID | BSR131UP01BACSDAT1_Str1Mod35AlmID | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 1 Module 35 Alarm ID | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod36AlmID | BSR131UP01BACSDAT1_Str2Mod36AlmID | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 2 Module 36 Alarm ID | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod36AlmID | BSR131UP01BACSDAT1_Str1Mod36AlmID | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 1 Module 36 Alarm ID | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod37AlmID | BSR131UP01BACSDAT1_Str2Mod37AlmID | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 2 Module 37 Alarm ID | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod37AlmID | BSR131UP01BACSDAT1_Str1Mod37AlmID | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 1 Module 37 Alarm ID | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod38AlmID | BSR131UP01BACSDAT1_Str2Mod38AlmID | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 2 Module 38 Alarm ID | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod38AlmID | BSR131UP01BACSDAT1_Str1Mod38AlmID | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 1 Module 38 Alarm ID | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod39AlmID | BSR131UP01BACSDAT1_Str2Mod39AlmID | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 2 Module 39 Alarm ID | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod39AlmID | BSR131UP01BACSDAT1_Str1Mod39AlmID | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 1 Module 39 Alarm ID | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod40AlmID | BSR131UP01BACSDAT1_Str2Mod40AlmID | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 2 Module 40 Alarm ID | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str1Mod40AlmID | BSR131UP01BACSDAT1_Str1Mod40AlmID | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 1 Module 40 Alarm ID | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod1AlmID | BSR131UP01BACSDAT1_Str2Mod1AlmID | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 2 Module 1 Alarm ID | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod2AlmID | BSR131UP01BACSDAT1_Str2Mod2AlmID | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 2 Module 2 Alarm ID | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod3AlmID | BSR131UP01BACSDAT1_Str2Mod3AlmID | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 2 Module 3 Alarm ID | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod4AlmID | BSR131UP01BACSDAT1_Str2Mod4AlmID | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 2 Module 4 Alarm ID | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod5AlmID | BSR131UP01BACSDAT1_Str2Mod5AlmID | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 2 Module 5 Alarm ID | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod6AlmID | BSR131UP01BACSDAT1_Str2Mod6AlmID | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 2 Module 6 Alarm ID | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod7AlmID | BSR131UP01BACSDAT1_Str2Mod7AlmID | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 2 Module 7 Alarm ID | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod8AlmID | BSR131UP01BACSDAT1_Str2Mod8AlmID | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 2 Module 8 Alarm ID | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod9AlmID | BSR131UP01BACSDAT1_Str2Mod9AlmID | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 2 Module 9 Alarm ID | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod10AlmID | BSR131UP01BACSDAT1_Str2Mod10AlmID | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 2 Module 10 Alarm ID | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod11AlmID | BSR131UP01BACSDAT1_Str2Mod11AlmID | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 2 Module 11 Alarm ID | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod12AlmID | BSR131UP01BACSDAT1_Str2Mod12AlmID | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 2 Module 12 Alarm ID | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod13AlmID | BSR131UP01BACSDAT1_Str2Mod13AlmID | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 2 Module 13 Alarm ID | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod14AlmID | BSR131UP01BACSDAT1_Str2Mod14AlmID | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 2 Module 14 Alarm ID | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod15AlmID | BSR131UP01BACSDAT1_Str2Mod15AlmID | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 2 Module 15 Alarm ID | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod16AlmID | BSR131UP01BACSDAT1_Str2Mod16AlmID | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 2 Module 16 Alarm ID | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod17AlmID | BSR131UP01BACSDAT1_Str2Mod17AlmID | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 2 Module 17 Alarm ID | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod18AlmID | BSR131UP01BACSDAT1_Str2Mod18AlmID | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 2 Module 18 Alarm ID | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod19AlmID | BSR131UP01BACSDAT1_Str2Mod19AlmID | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 2 Module 19 Alarm ID | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod20AlmID | BSR131UP01BACSDAT1_Str2Mod20AlmID | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 2 Module 20 Alarm ID | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags
BR4.SRV.PWR.BSR131.UP01.BACS | Str2Mod21AlmID | BSR131UP01BACSDAT1_Str2Mod21AlmID | BR4_Cluster1 | TRN_PERIODIC | 0:00 | BSR131UP01 UPS BACS String 2 Module 21 Alarm ID | 6 | 1st | 0:00 | Floating Point (8-byte samples) | BS1_Tags

## REF Alarms
BR4_Tags | R1Col_W | ACS/SMS PLC505 M580 | BRC501 Collision Alarm | R1Col_W | CAT_P2 |  | PRIV_ALARMACK | A_CM_ACSSMS | BRC501 Collision Alarm | R1Col_W | C_HIPRI | ACSNEW | Class_Equipment | BR4_Cluster1 | BR4.STOCKYARD.ACS.BRC501
BR4_Tags | S2Col_W | ACS/SMS PLC505 M580 | BST502 Collision Alarm | S2Col_W | CAT_P2 |  | PRIV_ALARMACK | A_CM_ACSSMS | BST502 Collision Alarm | S2Col_W | C_HIPRI | ACSNEW | Class_Equipment | BR4_Cluster1 | BR4.STOCKYARD.ACS.BST502
BR4_Tags | S1Col_W | ACS/SMS PLC505 M580 | BST501 Collision Alarm | S1Col_W | CAT_P2 |  | PRIV_ALARMACK | A_CM_ACSSMS | BST501 Collision Alarm | S1Col_W | C_HIPRI | ACSNEW | Class_Equipment | BR4_Cluster1 | BR4.STOCKYARD.ACS.BST501
BR4_Tags | R1ACSByp_A | ACS/SMS PLC505 M580 | BRC501 Anti-Col Bypassed Alarm | R1ACSByp_A | CAT_P2 |  | PRIV_ALARMACK | A_CM_ACSSMS | BRC501 Anti-Col Bypassed Alarm | R1ACSByp_A | C_HIPRI | ACSNEW | Class_Equipment | BR4_Cluster1 | BR4.STOCKYARD.ACS.BRC501
BR4_Tags | S2ACSByp_A | ACS/SMS PLC505 M580 | BST502 Anti-Col Bypassed Alarm | S2ACSByp_A | CAT_P2 |  | PRIV_ALARMACK | A_CM_ACSSMS | BST502 Anti-Col Bypassed Alarm | S2ACSByp_A | C_HIPRI | ACSNEW | Class_Equipment | BR4_Cluster1 | BR4.STOCKYARD.ACS.BST502
BR4_Tags | S1ACSByp_A | ACS/SMS PLC505 M580 | BST501 Anti-Col Bypassed Alarm | S1ACSByp_A | CAT_P2 |  | PRIV_ALARMACK | A_CM_ACSSMS | BST501 Anti-Col Bypassed Alarm | S1ACSByp_A | C_HIPRI | ACSNEW | Class_Equipment | BR4_Cluster1 | BR4.STOCKYARD.ACS.BST501
BR4_Tags | R1LastPos_A | ACS/SMS PLC505 M580 | BRC501 Anti-Col In Last Known Position Alarm | R1LastPos_A | CAT_P3 |  | PRIV_ALARMACK | A_CM_ACSSMS | BRC501 Anti-Col In Last Known Position Alarm | R1LastPos_A | C_LOPRI | ACSNEW | Class_Equipment | BR4_Cluster1 | BR4.STOCKYARD.ACS.BRC501
BR4_Tags | S2LastPos_A | ACS/SMS PLC505 M580 | BST502 Anti-Col In Last Known Position Alarm | S2LastPos_A | CAT_P3 |  | PRIV_ALARMACK | A_CM_ACSSMS | BST502 Anti-Col In Last Known Position Alarm | S2LastPos_A | C_LOPRI | ACSNEW | Class_Equipment | BR4_Cluster1 | BR4.STOCKYARD.ACS.BST502
BR4_Tags | S1LastPos_A | ACS/SMS PLC505 M580 | BST501 Anti-Col In Last Known Position Alarm | S1LastPos_A | CAT_P3 |  | PRIV_ALARMACK | A_CM_ACSSMS | BST501 Anti-Col In Last Known Position Alarm | S1LastPos_A | C_LOPRI | ACSNEW | Class_Equipment | BR4_Cluster1 | BR4.STOCKYARD.ACS.BST501
BR4_Tags | R1Col_A | ACS/SMS PLC505 M580 | BRC501 Crash Alarm | R1Col_A | CAT_P1 |  | PRIV_ALARMACK | A_CM_ACSSMS | BRC501 Crash Alarm | R1Col_A | C_CRITPRI | ACSNEW | Class_Equipment | BR4_Cluster1 | BR4.STOCKYARD.ACS.BRC501
BR4_Tags | S2Col_A | ACS/SMS PLC505 M580 | BST502 Crash Alarm | S2Col_A | CAT_P1 |  | PRIV_ALARMACK | A_CM_ACSSMS | BST502 Crash Alarm | S2Col_A | C_CRITPRI | ACSNEW | Class_Equipment | BR4_Cluster1 | BR4.STOCKYARD.ACS.BST502
BR4_Tags | S1Col_A | ACS/SMS PLC505 M580 | BST501 Crash Alarm | S1Col_A | CAT_P1 |  | PRIV_ALARMACK | A_CM_ACSSMS | BST501 Crash Alarm | S1Col_A | C_CRITPRI | ACSNEW | Class_Equipment | BR4_Cluster1 | BR4.STOCKYARD.ACS.BST501
BR4_Tags | BPL505_BPL551CommsFlt_A | ACS/SMS PLC505 M580 | BRC501 InterPLC Communications Alarm | BPL505_BPL551CommsFlt_A | CAT_P2 |  | PRIV_ALARMACK | A_CM_ACSSMS | ACS to BRC501 Communications Fault Alarm | BPL505_BPL551CommsFlt_A | C_HIPRI | ACSNEW | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL505
BR4_Tags | BPL505_BPL542CommsFlt_A | ACS/SMS PLC505 M580 | BST502 InterPLC Communications Alarm | BPL505_BPL542CommsFlt_A | CAT_P2 |  | PRIV_ALARMACK | A_CM_ACSSMS | ACS to BST502 Communications Fault Alarm | BPL505_BPL542CommsFlt_A | C_HIPRI | ACSNEW | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL505
BR4_Tags | BPL505_BPL541CommsFlt_A | ACS/SMS PLC505 M580 | BST501 InterPLC Communications Alarm | BPL505_BPL541CommsFlt_A | CAT_P2 |  | PRIV_ALARMACK | A_CM_ACSSMS | ACS to BST501 Communications Fault Alarm | BPL505_BPL541CommsFlt_A | C_HIPRI | ACSNEW | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL505
BR4_Tags | BPL505_CPUBattFlt_A | ACS/SMS PLC505 M580 | BPL505 PLC Battery Fault Alarm | BPL505_CPUBattFlt_A | CAT_P2 |  | PRIV_ALARMACK | A_CM_ACSSMS | BPL505 PLC Battery Fault Alarm | BPL505_CPUBattFlt_A | C_HIPRI | ACSNEW | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL505
BR4_Tags | BPL505_CPUEthLinkOK_A | ACS/SMS PLC505 M580 | BPL505 PLC CPU Ethernet Link OK | BPL505_CPUEthLinkOK_A | CAT_P2 |  | PRIV_ALARMACK | A_CM_ACSSMS | BPL505 PLC CPU Ethernet Link OK | BPL505_CPUEthLinkOK_A | C_HIPRI | ACSNEW | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL505 | Slot1_A
BR4_Tags | BPL505_CPUEthSysOK_A | ACS/SMS PLC505 M580 | BPL505 PLC CPU Ethernet OK | BPL505_CPUEthSysOK_A | CAT_P2 |  | PRIV_ALARMACK | A_CM_ACSSMS | BPL505 PLC CPU Ethernet OK | BPL505_CPUEthSysOK_A | C_HIPRI | ACSNEW | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL505
BR4_Tags | BPL505_NOC1SysOK_A | ACS/SMS PLC505 M580 | BPL505 PLC NOC1 Ethernet OK | BPL505_NOC1SysOK_A | CAT_P2 |  | PRIV_ALARMACK | A_CM_ACSSMS | BPL505 PLC NOC1 Ethernet OK | BPL505_NOC1SysOK_A | C_HIPRI | ACSNEW | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL505
BR4_Tags | BPL505_NOC1LinkOK_A | ACS/SMS PLC505 M580 | BPL505 PLC NOC1 Ethernet Link OK | BPL505_NOC1LinkOK_A | CAT_P2 |  | PRIV_ALARMACK | A_CM_ACSSMS | BPL505 PLC NOC1 Ethernet Link OK | BPL505_NOC1LinkOK_A | C_HIPRI | ACSNEW | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL505 | Slot2_A
BR4_Tags | BPL505_NOC2SysOK_A | ACS/SMS PLC505 M580 | BPL505 PLC NOC2 Ethernet OK | BPL505_NOC2SysOK_A | CAT_P2 |  | PRIV_ALARMACK | A_CM_ACSSMS | BPL505 PLC NOC2 Ethernet OK | BPL505_NOC2SysOK_A | C_HIPRI | ACSNEW | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL505
BR4_Tags | BPL505_NOC2LinkOK_A | ACS/SMS PLC505 M580 | BPL505 PLC NOC2 Ethernet Link OK | BPL505_NOC2LinkOK_A | CAT_P2 |  | PRIV_ALARMACK | A_CM_ACSSMS | BPL505 PLC NOC2 Ethernet Link OK | BPL505_NOC2LinkOK_A | C_HIPRI | ACSNEW | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL505 | Slot3_A
BR4_Tags | B201_CommsFlt_A | Bore | Comms Fail | B201_CommsFlt_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B201_CommsFlt_A | C_LOPRI | B201 | Class_Equipment | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B201
BR4_Tags | B201_DCOK01_A | Bore | 24V I/O Supply Fault | B201_DCOK01_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B201_DCOK01_A | C_LOPRI | B201 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B201
BR4_Tags | B201_DCOK02_A | Bore | 24V Supply Fault | B201_DCOK02_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B201_DCOK02_A | C_LOPRI | B201 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B201
BR4_Tags | B201_EARTH_A | Bore | Earth Leakage Fault | B201_EARTH_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B201_EARTH_A | C_LOPRI | B201 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B201
BR4_Tags | B201_ECR_A | Bore | ECR Fault | B201_ECR_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B201_ECR_A | C_LOPRI | B201 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B201
BR4_Tags | B201_FS01_A | Bore | Flow Switch Low | B201_FS01_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B201_FS01_A | C_LOPRI | B201 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B201
BR4_Tags | B201_FT01_Lo_A | Bore | Flow Low | B201_FT01_Lo_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B201_FT01_Lo_A | C_LOPRI | B201 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B201.FT01
BR4_Tags | B201_GenFlt_A | Bore | Generator Alarm | B201_GenFlt_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B201_GenFlt_A | C_LOPRI | B201 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B201
BR4_Tags | B201_GenFuelLow_A | Bore | Generator Fuel Low | B201_GenFuelLow_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B201_GenFuelLow_A | C_LOPRI | B201 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B201
BR4_Tags | B201_GenSttFail_A | Bore | Generator Failed to Start | B201_GenSttFail_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B201_GenSttFail_A | C_LOPRI | B201 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B201
BR4_Tags | B201_LOS01_A | Bore | E-stop 01 Activated | B201_LOS01_A | CAT_P1 |  | PRIV_ALARMACK | A_P1_SERV | E-stop 01 Activated | B201_LOS01_A | C_LOPRI | B201 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B201
BR4_Tags | B201_LOS02_A | Bore | E-stop 02 Activated | B201_LOS02_A | CAT_P1 |  | PRIV_ALARMACK | A_P1_SERV | E-stop 02 Activated | B201_LOS02_A | C_LOPRI | B201 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B201
BR4_Tags | B201_LSL_A | Bore | Level Switch Low | B201_LSL_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B201_LSL_A | C_LOPRI | B201 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B201
BR4_Tags | B201_LT01_Lo_A | Bore | Level Low | B201_LT01_Lo_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B201_LT01_Lo_A | C_LOPRI | B201 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B201.LT01
BR4_Tags | B201_MC01_A | Bore | Main Contactor Fault | B201_MC01_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B201_MC01_A | C_LOPRI | B201 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B201.MC01
BR4_Tags | B305_PT01_Hi_A | Bore | Upstream Pressure Hi | B305_PT01_Hi_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B305_PT01_Hi_A | C_LOPRI | B305 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B305.PT01
BR4_Tags | B305_PT01_HiHi_A | Bore | Upstream Pressure HiHi | B305_PT01_HiHi_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B305_PT01_HiHi_A | C_LOPRI | B305 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B305.PT01
BR4_Tags | B305_PT02_Hi_A | Bore | Downstream Pressure Hi | B305_PT02_Hi_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B305_PT02_Hi_A | C_LOPRI | B305 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B305.PT02
BR4_Tags | B305_PT02_HiHi_A | Bore | Downstream Pressure HiHi | B305_PT02_HiHi_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B305_PT02_HiHi_A | C_LOPRI | B305 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B305.PT02
BR4_Tags | B304_PT01_Hi_A | Bore | Upstream Pressure Hi | B304_PT01_Hi_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B304_PT01_Hi_A | C_LOPRI | B304 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B304.PT01
BR4_Tags | B304_PT01_HiHi_A | Bore | Upstream Pressure HiHi | B304_PT01_HiHi_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B304_PT01_HiHi_A | C_LOPRI | B304 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B304.PT01
BR4_Tags | B304_PT02_Hi_A | Bore | Downstream Pressure Hi | B304_PT02_Hi_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B304_PT02_Hi_A | C_LOPRI | B304 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B304.PT02
BR4_Tags | B304_PT02_HiHi_A | Bore | Downstream Pressure HiHi | B304_PT02_HiHi_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B304_PT02_HiHi_A | C_LOPRI | B304 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B304.PT02
BR4_Tags | B303_PT01_Hi_A | Bore | Upstream Pressure Hi | B303_PT01_Hi_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B303_PT01_Hi_A | C_LOPRI | B303 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B303.PT01
BR4_Tags | B303_PT01_HiHi_A | Bore | Upstream Pressure HiHi | B303_PT01_HiHi_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B303_PT01_HiHi_A | C_LOPRI | B303 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B303.PT01
BR4_Tags | B303_PT02_Hi_A | Bore | Downstream Pressure Hi | B303_PT02_Hi_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B303_PT02_Hi_A | C_LOPRI | B303 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B303.PT02
BR4_Tags | B303_PT02_HiHi_A | Bore | Downstream Pressure HiHi | B303_PT02_HiHi_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B303_PT02_HiHi_A | C_LOPRI | B303 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B303.PT02
BR4_Tags | B301_PT01_Hi_A | Bore | Upstream Pressure Hi | B301_PT01_Hi_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B301_PT01_Hi_A | C_LOPRI | B301 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B301.PT01
BR4_Tags | B301_PT01_HiHi_A | Bore | Upstream Pressure HiHi | B301_PT01_HiHi_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B301_PT01_HiHi_A | C_LOPRI | B301 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B301.PT01
BR4_Tags | B301_PT02_Hi_A | Bore | Downstream Pressure Hi | B301_PT02_Hi_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B301_PT02_Hi_A | C_LOPRI | B301 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B301.PT02
BR4_Tags | B301_PT02_HiHi_A | Bore | Downstream Pressure HiHi | B301_PT02_HiHi_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B301_PT02_HiHi_A | C_LOPRI | B301 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B301.PT02
BR4_Tags | B209_PT01_Hi_A | Bore | Upstream Pressure Hi | B209_PT01_Hi_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B209_PT01_Hi_A | C_LOPRI | B209 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B209.PT01
BR4_Tags | B209_PT01_HiHi_A | Bore | Upstream Pressure HiHi | B209_PT01_HiHi_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B209_PT01_HiHi_A | C_LOPRI | B209 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B209.PT01
BR4_Tags | B209_PT02_Hi_A | Bore | Downstream Pressure Hi | B209_PT02_Hi_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B209_PT02_Hi_A | C_LOPRI | B209 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B209.PT02
BR4_Tags | B209_PT02_HiHi_A | Bore | Downstream Pressure HiHi | B209_PT02_HiHi_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B209_PT02_HiHi_A | C_LOPRI | B209 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B209.PT02
BR4_Tags | B204_PT01_Hi_A | Bore | Upstream Pressure Hi | B204_PT01_Hi_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B204_PT01_Hi_A | C_LOPRI | B204 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B204.PT01
BR4_Tags | B204_PT01_HiHi_A | Bore | Upstream Pressure HiHi | B204_PT01_HiHi_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B204_PT01_HiHi_A | C_LOPRI | B204 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B204.PT01
BR4_Tags | B204_PT02_Hi_A | Bore | Downstream Pressure Hi | B204_PT02_Hi_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B204_PT02_Hi_A | C_LOPRI | B204 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B204.PT02
BR4_Tags | B204_PT02_HiHi_A | Bore | Downstream Pressure HiHi | B204_PT02_HiHi_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B204_PT02_HiHi_A | C_LOPRI | B204 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B204.PT02
BR4_Tags | B201_PT01_Hi_A | Bore | Upstream Pressure Hi | B201_PT01_Hi_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B201_PT01_Hi_A | C_LOPRI | B201 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B201.PT01
BR4_Tags | B201_PT01_HiHi_A | Bore | Upstream Pressure HiHi | B201_PT01_HiHi_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B201_PT01_HiHi_A | C_LOPRI | B201 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B201.PT01
BR4_Tags | B201_PT02_Hi_A | Bore | Downstream Pressure Hi | B201_PT02_Hi_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B201_PT02_Hi_A | C_LOPRI | B201 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B201.PT02
BR4_Tags | B201_PT02_HiHi_A | Bore | Downstream Pressure HiHi | B201_PT02_HiHi_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B201_PT02_HiHi_A | C_LOPRI | B201 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B201.PT02
BR4_Tags | B201_PS03_Hi_A | Bore | Pressure Hi | B201_PS03_Hi_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B201_PS03_Hi_A | C_LOPRI | B201 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B201
BR4_Tags | B201_PS04_HiHi_A | Bore | Pressure HiHi | B201_PS04_HiHi_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B201_PS04_HiHi_A | C_LOPRI | B201 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B201
BR4_Tags | B201_SD01Flt_A | Bore | Surge Diverter Fault | B201_SD01Flt_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B201_SD01Flt_A | C_LOPRI | B201 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B201
BR4_Tags | B201_SS01_A | Bore | Soft Starter Fault | B201_SS01_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B201_SS01_A | C_LOPRI | B201 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B201
BR4_Tags | B201_Stt_A | Bore | Excessive Starts | B201_Stt_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B201_Stt_A | C_LOPRI | B201 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B201
BR4_Tags | B201_TS01_Hi_A | Bore | Temp Switch Hi | B201_TS01_Hi_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B201_TS01_Hi_A | C_LOPRI | B201 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B201
BR4_Tags | B201_TT01_Hi_A | Bore | Temperature High | B201_TT01_Hi_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B201_TT01_Hi_A | C_LOPRI | B201 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B201.TT01
BR4_Tags | B202_Commn_E | Bore | Common Warning Alarm | B202_Commn_E | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B202_Commn_E | C_LOPRI | B202 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B202
BR4_Tags | B202_CommnSd_A | Bore | Common Shutdown Alarm | B202_CommnSd_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B202_CommnSd_A | C_LOPRI | B202 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B202
BR4_Tags | B202_CommsFlt_A | Bore | Comms Fail | B202_CommsFlt_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B202_CommsFlt_A | C_LOPRI | B202 | Class_Equipment | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B202
BR4_Tags | B202_CurrUnbal_A | Bore | Phase Current Imbalance | B202_CurrUnbal_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B202_CurrUnbal_A | C_LOPRI | B202 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B202
BR4_Tags | B202_EARTH_A | Bore | Earth Leakage Shutdown | B202_EARTH_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B202_EARTH_A | C_LOPRI | B202 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B202
BR4_Tags | B202_ECR_A | Bore | Earth Continuity Shutdown | B202_ECR_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B202_ECR_A | C_LOPRI | B202 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B202
BR4_Tags | B202_ECR_Overide_A | Bore | ECR Bypass On | B202_ECR_Overide_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B202_ECR_Overide_A | C_LOPRI | B202 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B202
BR4_Tags | B202_ECU_A | Bore | ECU Shutdown Fault | B202_ECU_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B202_ECU_A | C_LOPRI | B202 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B202
BR4_Tags | B202_ECUWarning_E | Bore | ECU Warning Fault | B202_ECUWarning_E | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B202_ECUWarning_E | C_LOPRI | B202 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B202
BR4_Tags | B202_FT01_Lo_A | Bore | Flow Low Warning | B202_FT01_Lo_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B202_FT01_Lo_A | C_LOPRI | B202 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B202.FT01
BR4_Tags | B202_FT01_LoLo_A | Bore | Flow Low Low Shutdown | B202_FT01_LoLo_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B202_FT01_LoLo_A | C_LOPRI | B202 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B202.FT01
BR4_Tags | B202_LOS_A | Bore | Emergency Stop Shutdown | B202_LOS_A | CAT_P1 |  | PRIV_ALARMACK | A_P1_SERV |  | B202_LOS_A | C_LOPRI | B202 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B202
BR4_Tags | B202_LT01_Lo_A | Bore | Low Bore Level Warning | B202_LT01_Lo_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B202_LT01_Lo_A | C_LOPRI | B202 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B202.LT01
BR4_Tags | B202_LT01_LoLo_A | Bore | Low Bore Level Shutdown | B202_LT01_LoLo_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B202_LT01_LoLo_A | C_LOPRI | B202 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B202.LT01
BR4_Tags | B202_LT02_Lo_A | Bore | Low Fuel Warning | B202_LT02_Lo_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B202_LT02_Lo_A | C_LOPRI | B202 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B202.LT02
BR4_Tags | B202_LT02_LoLo_A | Bore | Low Fuel Shutdown | B202_LT02_LoLo_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B202_LT02_LoLo_A | C_LOPRI | B202 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B202.LT02
BR4_Tags | B202_MCB_A | Bore | Main Breaker Tripped | B202_MCB_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B202_MCB_A | C_LOPRI | B202 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B202.MCB
BR4_Tags | B202_OverCurr_A | Bore | Over Current Shutdown | B202_OverCurr_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B202_OverCurr_A | C_LOPRI | B202 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B202
BR4_Tags | B202_OverVolt_A | Bore | Over Voltage Shutdown | B202_OverVolt_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B202_OverVolt_A | C_LOPRI | B202 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B202
BR4_Tags | B202_PT01_Hi_A | Bore | High Upstream Pressure Warning | B202_PT01_Hi_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B202_PT01_Hi_A | C_LOPRI | B202 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B202.PT01
BR4_Tags | B202_PT01_HiHi_A | Bore | High Upstream Pressure Shutdown | B202_PT01_HiHi_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B202_PT01_HiHi_A | C_LOPRI | B202 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B202.PT01
BR4_Tags | B202_PT02_Hi_A | Bore | High Downstream Pressure Warning | B202_PT02_Hi_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B202_PT02_Hi_A | C_LOPRI | B202 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B202.PT02
BR4_Tags | B202_PT02_HiHi_A | Bore | High Downstream Pressure Shutdown | B202_PT02_HiHi_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B202_PT02_HiHi_A | C_LOPRI | B202 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B202.PT02
BR4_Tags | B202_RnngFail_A | Bore | Failed while Running | B202_RnngFail_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B202_RnngFail_A | C_LOPRI | B202 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B202
BR4_Tags | B202_StpFail_A | Bore | Failed to Stop | B202_StpFail_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B202_StpFail_A | C_LOPRI | B202 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B202
BR4_Tags | B202_Stt_A | Bore | Excessive Starts | B202_Stt_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B202_Stt_A | C_LOPRI | B202 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B202
BR4_Tags | B202_SttFail_A | Bore | Failed to Start | B202_SttFail_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B202_SttFail_A | C_LOPRI | B202 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B202
BR4_Tags | B202_TOL01_A | Bore | Thermal Overload Shutdown | B202_TOL01_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B202_TOL01_A | C_LOPRI | B202 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B202
BR4_Tags | B202_TT01_Hi_A | Bore | High Pump Temp Warning | B202_TT01_Hi_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B202_TT01_Hi_A | C_LOPRI | B202 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B202.TT01
BR4_Tags | B202_TT01_HiHi_A | Bore | High Pump Temp Shutdown | B202_TT01_HiHi_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B202_TT01_HiHi_A | C_LOPRI | B202 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B202.TT01
BR4_Tags | B204_CommsFlt_A | Bore | Comms Fail | B204_CommsFlt_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B204_CommsFlt_A | C_LOPRI | B204 | Class_Equipment | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B204
BR4_Tags | B204_DCOK01_A | Bore | 24V I/O Supply Fault | B204_DCOK01_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B204_DCOK01_A | C_LOPRI | B204 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B204
BR4_Tags | B204_DCOK02_A | Bore | 24V Supply Fault | B204_DCOK02_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B204_DCOK02_A | C_LOPRI | B204 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B204
BR4_Tags | B204_EARTH_A | Bore | Earth Leakage Fault | B204_EARTH_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B204_EARTH_A | C_LOPRI | B204 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B204
BR4_Tags | B204_ECR_A | Bore | ECR Fault | B204_ECR_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B204_ECR_A | C_LOPRI | B204 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B204
BR4_Tags | B204_FS01_A | Bore | Flow Switch Low | B204_FS01_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B204_FS01_A | C_LOPRI | B204 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B204
BR4_Tags | B204_FT01_Lo_A | Bore | Flow Low | B204_FT01_Lo_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B204_FT01_Lo_A | C_LOPRI | B204 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B204.FT01
BR4_Tags | B204_GenFlt_A | Bore | Generator Alarm | B204_GenFlt_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B204_GenFlt_A | C_LOPRI | B204 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B204
BR4_Tags | B204_GenFuelLow_A | Bore | Generator Fuel Low | B204_GenFuelLow_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B204_GenFuelLow_A | C_LOPRI | B204 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B204
BR4_Tags | B204_GenSttFail_A | Bore | Generator Failed to Start | B204_GenSttFail_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B204_GenSttFail_A | C_LOPRI | B204 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B204
BR4_Tags | B204_LOS01_A | Bore | E-stop 01 Activated | B204_LOS01_A | CAT_P1 |  | PRIV_ALARMACK | A_P1_SERV | E-stop 01 Activated | B204_LOS01_A | C_LOPRI | B204 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B204
BR4_Tags | B204_LOS02_A | Bore | E-stop 02 Activated | B204_LOS02_A | CAT_P1 |  | PRIV_ALARMACK | A_P1_SERV | E-stop 02 Activated | B204_LOS02_A | C_LOPRI | B204 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B204
BR4_Tags | B204_LSL_A | Bore | Level Switch Low | B204_LSL_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B204_LSL_A | C_LOPRI | B204 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B204
BR4_Tags | B204_LT01_Lo_A | Bore | Level Low | B204_LT01_Lo_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B204_LT01_Lo_A | C_LOPRI | B204 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B204.LT01
BR4_Tags | B204_MC01_A | Bore | Main Contactor Fault | B204_MC01_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B204_MC01_A | C_LOPRI | B204 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B204.MC01
BR4_Tags | B204_PS03_Hi_A | Bore | Pressure Hi | B204_PS03_Hi_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B204_PS03_Hi_A | C_LOPRI | B204 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B204
BR4_Tags | B204_PS04_HiHi_A | Bore | Pressure HiHi | B204_PS04_HiHi_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B204_PS04_HiHi_A | C_LOPRI | B204 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B204
BR4_Tags | B204_SD01Flt_A | Bore | Surge Diverter Fault | B204_SD01Flt_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B204_SD01Flt_A | C_LOPRI | B204 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B204
BR4_Tags | B204_SS01_A | Bore | Soft Starter Fault | B204_SS01_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B204_SS01_A | C_LOPRI | B204 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B204
BR4_Tags | B204_Stt_A | Bore | Excessive Starts | B204_Stt_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B204_Stt_A | C_LOPRI | B204 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B204
BR4_Tags | B204_TS01_Hi_A | Bore | Temp Switch Hi | B204_TS01_Hi_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B204_TS01_Hi_A | C_LOPRI | B204 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B204
BR4_Tags | B204_TT01_Hi_A | Bore | Temperature High | B204_TT01_Hi_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B204_TT01_Hi_A | C_LOPRI | B204 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B204.TT01
BR4_Tags | B209_CommsFlt_A | Bore | Comms Fail | B209_CommsFlt_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B209_CommsFlt_A | C_LOPRI | B209 | Class_Equipment | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B209
BR4_Tags | B209_DCOK01_A | Bore | 24V I/O Supply Fault | B209_DCOK01_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B209_DCOK01_A | C_LOPRI | B209 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B209
BR4_Tags | B209_DCOK02_A | Bore | 24V Supply Fault | B209_DCOK02_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B209_DCOK02_A | C_LOPRI | B209 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B209
BR4_Tags | B209_EARTH_A | Bore | Earth Leakage Fault | B209_EARTH_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B209_EARTH_A | C_LOPRI | B209 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B209
BR4_Tags | B209_ECR_A | Bore | ECR Fault | B209_ECR_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B209_ECR_A | C_LOPRI | B209 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B209
BR4_Tags | B209_FS01_A | Bore | Flow Switch Low | B209_FS01_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B209_FS01_A | C_LOPRI | B209 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B209
BR4_Tags | B209_FT01_Lo_A | Bore | Flow Low | B209_FT01_Lo_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B209_FT01_Lo_A | C_LOPRI | B209 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B209.FT01
BR4_Tags | B209_GenFlt_A | Bore | Generator Alarm | B209_GenFlt_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B209_GenFlt_A | C_LOPRI | B209 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B209
BR4_Tags | B209_GenFuelLow_A | Bore | Generator Fuel Low | B209_GenFuelLow_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B209_GenFuelLow_A | C_LOPRI | B209 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B209
BR4_Tags | B209_GenSttFail_A | Bore | Generator Failed to Start | B209_GenSttFail_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B209_GenSttFail_A | C_LOPRI | B209 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B209
BR4_Tags | B209_LOS01_A | Bore | E-stop 01 Activated | B209_LOS01_A | CAT_P1 |  | PRIV_ALARMACK | A_P1_SERV | E-stop 01 Activated | B209_LOS01_A | C_LOPRI | B209 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B209
BR4_Tags | B209_LOS02_A | Bore | E-stop 02 Activated | B209_LOS02_A | CAT_P1 |  | PRIV_ALARMACK | A_P1_SERV | E-stop 02 Activated | B209_LOS02_A | C_LOPRI | B209 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B209
BR4_Tags | B209_LSL_A | Bore | Level Switch Low | B209_LSL_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B209_LSL_A | C_LOPRI | B209 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B209
BR4_Tags | B209_LT01_Lo_A | Bore | Level Low | B209_LT01_Lo_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B209_LT01_Lo_A | C_LOPRI | B209 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B209.LT01
BR4_Tags | B209_MC01_A | Bore | Main Contactor Fault | B209_MC01_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B209_MC01_A | C_LOPRI | B209 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B209.MC01
BR4_Tags | B209_PS03_Hi_A | Bore | Pressure Hi | B209_PS03_Hi_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B209_PS03_Hi_A | C_LOPRI | B209 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B209
BR4_Tags | B209_PS04_HiHi_A | Bore | Pressure HiHi | B209_PS04_HiHi_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B209_PS04_HiHi_A | C_LOPRI | B209 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B209
BR4_Tags | B209_SD01Flt_A | Bore | Surge Diverter Fault | B209_SD01Flt_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B209_SD01Flt_A | C_LOPRI | B209 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B209
BR4_Tags | B209_SS01_A | Bore | Soft Starter Fault | B209_SS01_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B209_SS01_A | C_LOPRI | B209 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B209
BR4_Tags | B209_Stt_A | Bore | Excessive Starts | B209_Stt_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B209_Stt_A | C_LOPRI | B209 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B209
BR4_Tags | B209_TS01_Hi_A | Bore | Temp Switch Hi | B209_TS01_Hi_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B209_TS01_Hi_A | C_LOPRI | B209 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B209
BR4_Tags | B209_TT01_Hi_A | Bore | Temperature High | B209_TT01_Hi_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B209_TT01_Hi_A | C_LOPRI | B209 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B209.TT01
BR4_Tags | B301_CommsFlt_A | Bore | Comms Fail | B301_CommsFlt_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B301_CommsFlt_A | C_LOPRI | B301 | Class_Equipment | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B301
BR4_Tags | B301_DCOK01_A | Bore | 24V I/O Supply Fault | B301_DCOK01_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B301_DCOK01_A | C_LOPRI | B301 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B301
BR4_Tags | B301_DCOK02_A | Bore | 24V Supply Fault | B301_DCOK02_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B301_DCOK02_A | C_LOPRI | B301 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B301
BR4_Tags | B301_EARTH_A | Bore | Earth Leakage Fault | B301_EARTH_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B301_EARTH_A | C_LOPRI | B301 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B301
BR4_Tags | B301_ECR_A | Bore | ECR Fault | B301_ECR_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B301_ECR_A | C_LOPRI | B301 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B301
BR4_Tags | B301_FS01_A | Bore | Flow Switch Low | B301_FS01_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B301_FS01_A | C_LOPRI | B301 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B301
BR4_Tags | B301_FT01_Lo_A | Bore | Flow Low | B301_FT01_Lo_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B301_FT01_Lo_A | C_LOPRI | B301 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B301.FT01
BR4_Tags | B301_GenFlt_A | Bore | Generator Alarm | B301_GenFlt_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B301_GenFlt_A | C_LOPRI | B301 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B301
BR4_Tags | B301_GenFuelLow_A | Bore | Generator Fuel Low | B301_GenFuelLow_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B301_GenFuelLow_A | C_LOPRI | B301 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B301
BR4_Tags | B301_GenSttFail_A | Bore | Generator Failed to Start | B301_GenSttFail_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B301_GenSttFail_A | C_LOPRI | B301 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B301
BR4_Tags | B301_LOS01_A | Bore | E-stop 01 Activated | B301_LOS01_A | CAT_P1 |  | PRIV_ALARMACK | A_P1_SERV | E-stop 01 Activated | B301_LOS01_A | C_LOPRI | B301 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B301
BR4_Tags | B301_LOS02_A | Bore | E-stop 02 Activated | B301_LOS02_A | CAT_P1 |  | PRIV_ALARMACK | A_P1_SERV | E-stop 02 Activated | B301_LOS02_A | C_LOPRI | B301 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B301
BR4_Tags | B301_LSL_A | Bore | Level Switch Low | B301_LSL_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B301_LSL_A | C_LOPRI | B301 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B301
BR4_Tags | B301_LT01_Lo_A | Bore | Level Low | B301_LT01_Lo_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B301_LT01_Lo_A | C_LOPRI | B301 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B301.LT01
BR4_Tags | B301_MC01_A | Bore | Main Contactor Fault | B301_MC01_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B301_MC01_A | C_LOPRI | B301 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B301.MC01
BR4_Tags | B301_PS03_Hi_A | Bore | Pressure Hi | B301_PS03_Hi_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B301_PS03_Hi_A | C_LOPRI | B301 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B301
BR4_Tags | B301_PS04_HiHi_A | Bore | Pressure HiHi | B301_PS04_HiHi_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B301_PS04_HiHi_A | C_LOPRI | B301 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B301
BR4_Tags | B301_SD01Flt_A | Bore | Surge Diverter Fault | B301_SD01Flt_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B301_SD01Flt_A | C_LOPRI | B301 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B301
BR4_Tags | B301_SS01_A | Bore | Soft Starter Fault | B301_SS01_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B301_SS01_A | C_LOPRI | B301 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B301
BR4_Tags | B301_Stt_A | Bore | Excessive Starts | B301_Stt_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B301_Stt_A | C_LOPRI | B301 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B301
BR4_Tags | B301_TS01_Hi_A | Bore | Temp Switch Hi | B301_TS01_Hi_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B301_TS01_Hi_A | C_LOPRI | B301 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B301
BR4_Tags | B301_TT01_Hi_A | Bore | Temperature High | B301_TT01_Hi_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B301_TT01_Hi_A | C_LOPRI | B301 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B301.TT01
BR4_Tags | B302_CommsFlt_A | Bore | Comms Fail | B302_CommsFlt_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B302_CommsFlt_A | C_LOPRI | B302 | Class_Equipment | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B302
BR4_Tags | B302_DCOK01_A | Bore | 24V I/O Supply Fault | B302_DCOK01_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B302_DCOK01_A | C_LOPRI | B302 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B302
BR4_Tags | B302_DCOK02_A | Bore | 24V Supply Fault | B302_DCOK02_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B302_DCOK02_A | C_LOPRI | B302 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B302
BR4_Tags | B302_EARTH_A | Bore | Earth Leakage Fault | B302_EARTH_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B302_EARTH_A | C_LOPRI | B302 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B302
BR4_Tags | B302_ECR_A | Bore | ECR Fault | B302_ECR_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B302_ECR_A | C_LOPRI | B302 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B302
BR4_Tags | B302_FS01_A | Bore | Flow Switch Low | B302_FS01_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B302_FS01_A | C_LOPRI | B302 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B302
BR4_Tags | B302_FT01_Lo_A | Bore | Flow Low | B302_FT01_Lo_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B302_FT01_Lo_A | C_LOPRI | B302 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B302.FT01
BR4_Tags | B302_GenFlt_A | Bore | Generator Alarm | B302_GenFlt_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B302_GenFlt_A | C_LOPRI | B302 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B302
BR4_Tags | B302_GenFuelLow_A | Bore | Generator Fuel Low | B302_GenFuelLow_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B302_GenFuelLow_A | C_LOPRI | B302 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B302
BR4_Tags | B302_GenSttFail_A | Bore | Generator Failed to Start | B302_GenSttFail_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B302_GenSttFail_A | C_LOPRI | B302 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B302
BR4_Tags | B302_LOS01_A | Bore | E-stop 01 Activated | B302_LOS01_A | CAT_P1 |  | PRIV_ALARMACK | A_P1_SERV | E-stop 01 Activated | B302_LOS01_A | C_LOPRI | B302 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B302
BR4_Tags | B302_LOS02_A | Bore | E-stop 02 Activated | B302_LOS02_A | CAT_P1 |  | PRIV_ALARMACK | A_P1_SERV | E-stop 02 Activated | B302_LOS02_A | C_LOPRI | B302 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B302
BR4_Tags | B302_LSL_A | Bore | Level Switch Low | B302_LSL_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B302_LSL_A | C_LOPRI | B302 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B302
BR4_Tags | B302_LT01_Lo_A | Bore | Level Low | B302_LT01_Lo_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B302_LT01_Lo_A | C_LOPRI | B302 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B302.LT01
BR4_Tags | B302_MC01_A | Bore | Main Contactor Fault | B302_MC01_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B302_MC01_A | C_LOPRI | B302 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B302.MC01
BR4_Tags | B302_PT01_Hi_A | Bore | Upstream Pressure Hi | B302_PT01_Hi_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B302_PT01_Hi_A | C_LOPRI | B302 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B302.PT01
BR4_Tags | B302_PT01_HiHi_A | Bore | Upstream Pressure HiHi | B302_PT01_HiHi_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B302_PT01_HiHi_A | C_LOPRI | B302 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B302.PT01
BR4_Tags | B302_PT02_Hi_A | Bore | Downstream Pressure Hi | B302_PT02_Hi_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B302_PT02_Hi_A | C_LOPRI | B302 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B302.PT02
BR4_Tags | B302_PT02_HiHi_A | Bore | Downstream Pressure HiHi | B302_PT02_HiHi_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B302_PT02_HiHi_A | C_LOPRI | B302 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B302.PT02
BR4_Tags | B302_PS03_Hi_A | Bore | Pressure Hi | B302_PS03_Hi_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B302_PS03_Hi_A | C_LOPRI | B302 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B302
BR4_Tags | B302_PS04_HiHi_A | Bore | Pressure HiHi | B302_PS04_HiHi_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B302_PS04_HiHi_A | C_LOPRI | B302 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B302
BR4_Tags | B302_SD01Flt_A | Bore | Surge Diverter Fault | B302_SD01Flt_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B302_SD01Flt_A | C_LOPRI | B302 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B302
BR4_Tags | B302_SS01_A | Bore | Soft Starter Fault | B302_SS01_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B302_SS01_A | C_LOPRI | B302 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B302
BR4_Tags | B302_Stt_A | Bore | Excessive Starts | B302_Stt_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B302_Stt_A | C_LOPRI | B302 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B302
BR4_Tags | B302_TS01_Hi_A | Bore | Temp Switch Hi | B302_TS01_Hi_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B302_TS01_Hi_A | C_LOPRI | B302 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B302
BR4_Tags | B302_TT01_Hi_A | Bore | Temperature High | B302_TT01_Hi_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B302_TT01_Hi_A | C_LOPRI | B302 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B302.TT01
BR4_Tags | B303_CommsFlt_A | Bore | Comms Fail | B303_CommsFlt_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B303_CommsFlt_A | C_LOPRI | B303 | Class_Equipment | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B303
BR4_Tags | B303_DCOK01_A | Bore | 24V I/O Supply Fault | B303_DCOK01_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B303_DCOK01_A | C_LOPRI | B303 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B303
BR4_Tags | B303_DCOK02_A | Bore | 24V Supply Fault | B303_DCOK02_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B303_DCOK02_A | C_LOPRI | B303 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B303
BR4_Tags | B303_EARTH_A | Bore | Earth Leakage Fault | B303_EARTH_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B303_EARTH_A | C_LOPRI | B303 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B303
BR4_Tags | B303_ECR_A | Bore | ECR Fault | B303_ECR_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B303_ECR_A | C_LOPRI | B303 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B303
BR4_Tags | B303_FS01_A | Bore | Flow Switch Low | B303_FS01_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B303_FS01_A | C_LOPRI | B303 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B303
BR4_Tags | B303_FT01_Lo_A | Bore | Flow Low | B303_FT01_Lo_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B303_FT01_Lo_A | C_LOPRI | B303 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B303.FT01
BR4_Tags | B303_GenFlt_A | Bore | Generator Alarm | B303_GenFlt_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B303_GenFlt_A | C_LOPRI | B303 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B303
BR4_Tags | B303_GenFuelLow_A | Bore | Generator Fuel Low | B303_GenFuelLow_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B303_GenFuelLow_A | C_LOPRI | B303 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B303
BR4_Tags | B303_GenSttFail_A | Bore | Generator Failed to Start | B303_GenSttFail_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B303_GenSttFail_A | C_LOPRI | B303 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B303
BR4_Tags | B303_LOS01_A | Bore | E-stop 01 Activated | B303_LOS01_A | CAT_P1 |  | PRIV_ALARMACK | A_P1_SERV | E-stop 01 Activated | B303_LOS01_A | C_LOPRI | B303 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B303
BR4_Tags | B303_LOS02_A | Bore | E-stop 02 Activated | B303_LOS02_A | CAT_P1 |  | PRIV_ALARMACK | A_P1_SERV | E-stop 02 Activated | B303_LOS02_A | C_LOPRI | B303 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B303
BR4_Tags | B303_LSL_A | Bore | Level Switch Low | B303_LSL_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B303_LSL_A | C_LOPRI | B303 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B303
BR4_Tags | B303_LT01_Lo_A | Bore | Level Low | B303_LT01_Lo_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B303_LT01_Lo_A | C_LOPRI | B303 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B303.LT01
BR4_Tags | B303_MC01_A | Bore | Main Contactor Fault | B303_MC01_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B303_MC01_A | C_LOPRI | B303 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B303.MC01
BR4_Tags | B303_SD01Flt_A | Bore | Surge Diverter Fault | B303_SD01Flt_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B303_SD01Flt_A | C_LOPRI | B303 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B303
BR4_Tags | B303_SS01_A | Bore | Soft Starter Fault | B303_SS01_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B303_SS01_A | C_LOPRI | B303 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B303
BR4_Tags | B303_Stt_A | Bore | Excessive Starts | B303_Stt_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B303_Stt_A | C_LOPRI | B303 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B303
BR4_Tags | B303_TS01_Hi_A | Bore | Temp Switch Hi | B303_TS01_Hi_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B303_TS01_Hi_A | C_LOPRI | B303 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B303
BR4_Tags | B303_TT01_Hi_A | Bore | Temperature High | B303_TT01_Hi_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B303_TT01_Hi_A | C_LOPRI | B303 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B303.TT01
BR4_Tags | B304_CommsFlt_A | Bore | Comms Fail | B304_CommsFlt_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B304_CommsFlt_A | C_LOPRI | B304 | Class_Equipment | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B304
BR4_Tags | B304_DCOK01_A | Bore | 24V I/O Supply Fault | B304_DCOK01_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B304_DCOK01_A | C_LOPRI | B304 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B304
BR4_Tags | B304_DCOK02_A | Bore | 24V Supply Fault | B304_DCOK02_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B304_DCOK02_A | C_LOPRI | B304 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B304
BR4_Tags | B304_EARTH_A | Bore | Earth Leakage Fault | B304_EARTH_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B304_EARTH_A | C_LOPRI | B304 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B304
BR4_Tags | B304_ECR_A | Bore | ECR Fault | B304_ECR_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B304_ECR_A | C_LOPRI | B304 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B304
BR4_Tags | B304_FS01_A | Bore | Flow Switch Low | B304_FS01_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B304_FS01_A | C_LOPRI | B304 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B304
BR4_Tags | B304_FT01_Lo_A | Bore | Flow Low | B304_FT01_Lo_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B304_FT01_Lo_A | C_LOPRI | B304 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B304.FT01
BR4_Tags | B304_GenFlt_A | Bore | Generator Alarm | B304_GenFlt_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B304_GenFlt_A | C_LOPRI | B304 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B304
BR4_Tags | B304_GenFuelLow_A | Bore | Generator Fuel Low | B304_GenFuelLow_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B304_GenFuelLow_A | C_LOPRI | B304 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B304
BR4_Tags | B304_GenSttFail_A | Bore | Generator Failed to Start | B304_GenSttFail_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B304_GenSttFail_A | C_LOPRI | B304 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B304
BR4_Tags | B304_LOS01_A | Bore | E-stop 01 Activated | B304_LOS01_A | CAT_P1 |  | PRIV_ALARMACK | A_P1_SERV | E-stop 01 Activated | B304_LOS01_A | C_LOPRI | B304 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B304
BR4_Tags | B304_LOS02_A | Bore | E-stop 02 Activated | B304_LOS02_A | CAT_P1 |  | PRIV_ALARMACK | A_P1_SERV | E-stop 02 Activated | B304_LOS02_A | C_LOPRI | B304 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B304
BR4_Tags | B304_LSL_A | Bore | Level Switch Low | B304_LSL_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B304_LSL_A | C_LOPRI | B304 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B304
BR4_Tags | B304_LT01_Lo_A | Bore | Level Low | B304_LT01_Lo_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B304_LT01_Lo_A | C_LOPRI | B304 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B304.LT01
BR4_Tags | B304_MC01_A | Bore | Main Contactor Fault | B304_MC01_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B304_MC01_A | C_LOPRI | B304 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B304.MC01
BR4_Tags | B304_PS03_Hi_A | Bore | Pressure Hi | B304_PS03_Hi_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B304_PS03_Hi_A | C_LOPRI | B304 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B304
BR4_Tags | B304_PS04_HiHi_A | Bore | Pressure HiHi | B304_PS04_HiHi_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B304_PS04_HiHi_A | C_LOPRI | B304 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B304
BR4_Tags | B304_SD01Flt_A | Bore | Surge Diverter Fault | B304_SD01Flt_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B304_SD01Flt_A | C_LOPRI | B304 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B304
BR4_Tags | B304_SS01_A | Bore | Soft Starter Fault | B304_SS01_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B304_SS01_A | C_LOPRI | B304 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B304
BR4_Tags | B304_Stt_A | Bore | Excessive Starts | B304_Stt_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B304_Stt_A | C_LOPRI | B304 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B304
BR4_Tags | B304_TS01_Hi_A | Bore | Temp Switch Hi | B304_TS01_Hi_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B304_TS01_Hi_A | C_LOPRI | B304 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B304
BR4_Tags | B304_TT01_Hi_A | Bore | Temperature High | B304_TT01_Hi_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B304_TT01_Hi_A | C_LOPRI | B304 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B304.TT01
BR4_Tags | B305_CommsFlt_A | Bore | Comms Fail | B305_CommsFlt_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B305_CommsFlt_A | C_LOPRI | B305 | Class_Equipment | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B305
BR4_Tags | B305_DCOK01_A | Bore | 24V I/O Supply Fault | B305_DCOK01_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B305_DCOK01_A | C_LOPRI | B305 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B305
BR4_Tags | B305_DCOK02_A | Bore | 24V Supply Fault | B305_DCOK02_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B305_DCOK02_A | C_LOPRI | B305 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B305
BR4_Tags | B305_EARTH_A | Bore | Earth Leakage Fault | B305_EARTH_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B305_EARTH_A | C_LOPRI | B305 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B305
BR4_Tags | B305_ECR_A | Bore | ECR Fault | B305_ECR_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B305_ECR_A | C_LOPRI | B305 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B305
BR4_Tags | B305_FS01_A | Bore | Flow Switch Low | B305_FS01_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B305_FS01_A | C_LOPRI | B305 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B305
BR4_Tags | B305_FT01_Lo_A | Bore | Flow Low | B305_FT01_Lo_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B305_FT01_Lo_A | C_LOPRI | B305 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B305.FT01
BR4_Tags | B305_GenFlt_A | Bore | Generator Alarm | B305_GenFlt_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B305_GenFlt_A | C_LOPRI | B305 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B305
BR4_Tags | B305_GenFuelLow_A | Bore | Generator Fuel Low | B305_GenFuelLow_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B305_GenFuelLow_A | C_LOPRI | B305 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B305
BR4_Tags | B305_GenSttFail_A | Bore | Generator Failed to Start | B305_GenSttFail_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B305_GenSttFail_A | C_LOPRI | B305 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B305
BR4_Tags | B305_LOS01_A | Bore | E-stop 01 Activated | B305_LOS01_A | CAT_P1 |  | PRIV_ALARMACK | A_P1_SERV | E-stop 01 Activated | B305_LOS01_A | C_LOPRI | B305 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B305
BR4_Tags | B305_LOS02_A | Bore | E-stop 02 Activated | B305_LOS02_A | CAT_P1 |  | PRIV_ALARMACK | A_P1_SERV | E-stop 02 Activated | B305_LOS02_A | C_LOPRI | B305 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B305
BR4_Tags | B305_LSL_A | Bore | Level Switch Low | B305_LSL_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B305_LSL_A | C_LOPRI | B305 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B305
BR4_Tags | B305_LT01_Lo_A | Bore | Level Low | B305_LT01_Lo_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B305_LT01_Lo_A | C_LOPRI | B305 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B305.LT01
BR4_Tags | B305_MC01_A | Bore | Main Contactor Fault | B305_MC01_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B305_MC01_A | C_LOPRI | B305 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B305.MC01
BR4_Tags | B305_PS03_Hi_A | Bore | Pressure Hi | B305_PS03_Hi_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B305_PS03_Hi_A | C_LOPRI | B305 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B305
BR4_Tags | B305_PS04_HiHi_A | Bore | Pressure HiHi | B305_PS04_HiHi_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B305_PS04_HiHi_A | C_LOPRI | B305 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B305
BR4_Tags | B305_SD01Flt_A | Bore | Surge Diverter Fault | B305_SD01Flt_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B305_SD01Flt_A | C_LOPRI | B305 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B305
BR4_Tags | B305_SS01_A | Bore | Soft Starter Fault | B305_SS01_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B305_SS01_A | C_LOPRI | B305 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B305
BR4_Tags | B305_Stt_A | Bore | Excessive Starts | B305_Stt_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B305_Stt_A | C_LOPRI | B305 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B305
BR4_Tags | B305_TS01_Hi_A | Bore | Temp Switch Hi | B305_TS01_Hi_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B305_TS01_Hi_A | C_LOPRI | B305 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B305
BR4_Tags | B305_TT01_Hi_A | Bore | Temperature High | B305_TT01_Hi_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B305_TT01_Hi_A | C_LOPRI | B305 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B305.TT01
BR4_Tags | B306_CommsFlt_A | Bore | Comms Fail | B306_CommsFlt_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B306_CommsFlt_A | C_LOPRI | B306 | Class_Equipment | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B306
BR4_Tags | B306_DCOK01_A | Bore | 24V I/O Supply Fault | B306_DCOK01_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B306_DCOK01_A | C_LOPRI | B306 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B306
BR4_Tags | B306_DCOK02_A | Bore | 24V Supply Fault | B306_DCOK02_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B306_DCOK02_A | C_LOPRI | B306 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B306
BR4_Tags | B306_EARTH_A | Bore | Earth Leakage Fault | B306_EARTH_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B306_EARTH_A | C_LOPRI | B306 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B306
BR4_Tags | B306_ECR_A | Bore | ECR Fault | B306_ECR_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B306_ECR_A | C_LOPRI | B306 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B306
BR4_Tags | B306_FS01_A | Bore | Flow Switch Low | B306_FS01_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B306_FS01_A | C_LOPRI | B306 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B306
BR4_Tags | B306_FT01_Lo_A | Bore | Flow Low | B306_FT01_Lo_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B306_FT01_Lo_A | C_LOPRI | B306 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B306.FT01
BR4_Tags | B306_GenFlt_A | Bore | Generator Alarm | B306_GenFlt_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B306_GenFlt_A | C_LOPRI | B306 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B306
BR4_Tags | B306_GenFuelLow_A | Bore | Generator Fuel Low | B306_GenFuelLow_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B306_GenFuelLow_A | C_LOPRI | B306 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B306
BR4_Tags | B306_GenSttFail_A | Bore | Generator Failed to Start | B306_GenSttFail_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B306_GenSttFail_A | C_LOPRI | B306 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B306
BR4_Tags | B306_LOS01_A | Bore | E-stop 01 Activated | B306_LOS01_A | CAT_P1 |  | PRIV_ALARMACK | A_P1_SERV | E-stop 01 Activated | B306_LOS01_A | C_LOPRI | B306 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B306
BR4_Tags | B306_LOS02_A | Bore | E-stop 02 Activated | B306_LOS02_A | CAT_P1 |  | PRIV_ALARMACK | A_P1_SERV | E-stop 02 Activated | B306_LOS02_A | C_LOPRI | B306 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B306
BR4_Tags | B306_LSL_A | Bore | Level Switch Low | B306_LSL_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B306_LSL_A | C_LOPRI | B306 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B306
BR4_Tags | B306_LT01_Lo_A | Bore | Level Low | B306_LT01_Lo_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B306_LT01_Lo_A | C_LOPRI | B306 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B306.LT01
BR4_Tags | B306_MC01_A | Bore | Main Contactor Fault | B306_MC01_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B306_MC01_A | C_LOPRI | B306 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B306.MC01
BR4_Tags | B306_PS03_Hi_A | Bore | Pressure Hi | B306_PS03_Hi_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B306_PS03_Hi_A | C_LOPRI | B306 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B306
BR4_Tags | B306_PS04_HiHi_A | Bore | Pressure HiHi | B306_PS04_HiHi_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B306_PS04_HiHi_A | C_LOPRI | B306 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B306
BR4_Tags | B306_SD01Flt_A | Bore | Surge Diverter Fault | B306_SD01Flt_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B306_SD01Flt_A | C_LOPRI | B306 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B306
BR4_Tags | B306_SS01_A | Bore | Soft Starter Fault | B306_SS01_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B306_SS01_A | C_LOPRI | B306 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B306
BR4_Tags | B306_Stt_A | Bore | Excessive Starts | B306_Stt_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B306_Stt_A | C_LOPRI | B306 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B306
BR4_Tags | B306_TS01_Hi_A | Bore | Temp Switch Hi | B306_TS01_Hi_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B306_TS01_Hi_A | C_LOPRI | B306 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B306
BR4_Tags | B306_TT01_Hi_A | Bore | Temperature High | B306_TT01_Hi_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B306_TT01_Hi_A | C_LOPRI | B306 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B306.TT01
BR4_Tags | B307_Commn_E | Bore | Common Warning Alarm | B307_Commn_E | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B307_Commn_E | C_LOPRI | B307 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B307
BR4_Tags | B307_CommnSd_A | Bore | Common Shutdown Alarm | B307_CommnSd_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B307_CommnSd_A | C_LOPRI | B307 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B307
BR4_Tags | B307_CommsFlt_A | Bore | Comms Fail | B307_CommsFlt_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B307_CommsFlt_A | C_LOPRI | B307 | Class_Equipment | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B307
BR4_Tags | B307_CurrUnbal_A | Bore | Phase Current Imbalance | B307_CurrUnbal_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B307_CurrUnbal_A | C_LOPRI | B307 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B307
BR4_Tags | B307_EARTH_A | Bore | Earth Leakage Shutdown | B307_EARTH_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B307_EARTH_A | C_LOPRI | B307 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B307
BR4_Tags | B307_ECR_A | Bore | Earth Continuity Shutdown | B307_ECR_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B307_ECR_A | C_LOPRI | B307 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B307
BR4_Tags | B307_ECR_Overide_A | Bore | ECR Bypass On | B307_ECR_Overide_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B307_ECR_Overide_A | C_LOPRI | B307 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B307
BR4_Tags | B307_ECU_A | Bore | ECU Shutdown Fault | B307_ECU_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B307_ECU_A | C_LOPRI | B307 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B307
BR4_Tags | B307_ECUWarning_E | Bore | ECU Warning Fault | B307_ECUWarning_E | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B307_ECUWarning_E | C_LOPRI | B307 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B307
BR4_Tags | B307_FT01_Lo_A | Bore | Flow Low Warning | B307_FT01_Lo_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B307_FT01_Lo_A | C_LOPRI | B307 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B307.FT01
BR4_Tags | B307_FT01_LoLo_A | Bore | Flow Low Low Shutdown | B307_FT01_LoLo_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B307_FT01_LoLo_A | C_LOPRI | B307 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B307.FT01
BR4_Tags | B307_LOS_A | Bore | Emergency Stop Shutdown | B307_LOS_A | CAT_P1 |  | PRIV_ALARMACK | A_P1_SERV |  | B307_LOS_A | C_LOPRI | B307 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B307
BR4_Tags | B307_LT01_Lo_A | Bore | Low Bore Level Warning | B307_LT01_Lo_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B307_LT01_Lo_A | C_LOPRI | B307 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B307.LT01
BR4_Tags | B307_LT01_LoLo_A | Bore | Low Bore Level Shutdown | B307_LT01_LoLo_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B307_LT01_LoLo_A | C_LOPRI | B307 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B307.LT01
BR4_Tags | B307_LT02_Lo_A | Bore | Low Fuel Warning | B307_LT02_Lo_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B307_LT02_Lo_A | C_LOPRI | B307 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B307.LT02
BR4_Tags | B307_LT02_LoLo_A | Bore | Low Fuel Shutdown | B307_LT02_LoLo_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B307_LT02_LoLo_A | C_LOPRI | B307 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B307.LT02
BR4_Tags | B307_MCB_A | Bore | Main Breaker Tripped | B307_MCB_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B307_MCB_A | C_LOPRI | B307 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B307.MCB
BR4_Tags | B307_OverCurr_A | Bore | Over Current Shutdown | B307_OverCurr_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B307_OverCurr_A | C_LOPRI | B307 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B307
BR4_Tags | B307_OverVolt_A | Bore | Over Voltage Shutdown | B307_OverVolt_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B307_OverVolt_A | C_LOPRI | B307 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B307
BR4_Tags | B307_PT01_Hi_A | Bore | High Upstream Pressure Warning | B307_PT01_Hi_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B307_PT01_Hi_A | C_LOPRI | B307 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B307.PT01
BR4_Tags | B307_PT01_HiHi_A | Bore | High Upstream Pressure Shutdown | B307_PT01_HiHi_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B307_PT01_HiHi_A | C_LOPRI | B307 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B307.PT01
BR4_Tags | B307_PT02_Hi_A | Bore | High Downstream Pressure Warning | B307_PT02_Hi_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B307_PT02_Hi_A | C_LOPRI | B307 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B307.PT02
BR4_Tags | B307_PT02_HiHi_A | Bore | High Downstream Pressure Shutdown | B307_PT02_HiHi_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B307_PT02_HiHi_A | C_LOPRI | B307 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B307.PT02
BR4_Tags | B307_RnngFail_A | Bore | Failed while Running | B307_RnngFail_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B307_RnngFail_A | C_LOPRI | B307 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B307
BR4_Tags | B307_StpFail_A | Bore | Failed to Stop | B307_StpFail_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B307_StpFail_A | C_LOPRI | B307 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B307
BR4_Tags | B307_Stt_A | Bore | Excessive Starts | B307_Stt_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B307_Stt_A | C_LOPRI | B307 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B307
BR4_Tags | B307_SttFail_A | Bore | Failed to Start | B307_SttFail_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B307_SttFail_A | C_LOPRI | B307 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B307
BR4_Tags | B307_TOL01_A | Bore | Thermal Overload Shutdown | B307_TOL01_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B307_TOL01_A | C_LOPRI | B307 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B307
BR4_Tags | B307_TT01_Hi_A | Bore | High Pump Temp Warning | B307_TT01_Hi_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B307_TT01_Hi_A | C_LOPRI | B307 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B307.TT01
BR4_Tags | B307_TT01_HiHi_A | Bore | High Pump Temp Shutdown | B307_TT01_HiHi_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B307_TT01_HiHi_A | C_LOPRI | B307 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B307.TT01
BR4_Tags | B308_Commn_E | Bore | Common Warning Alarm | B308_Commn_E | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B308_Commn_E | C_LOPRI | B308 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B308
BR4_Tags | B308_CommnSd_A | Bore | Common Shutdown Alarm | B308_CommnSd_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B308_CommnSd_A | C_LOPRI | B308 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B308
BR4_Tags | B308_CommsFlt_A | Bore | Comms Fail | B308_CommsFlt_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B308_CommsFlt_A | C_LOPRI | B308 | Class_Equipment | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B308
BR4_Tags | B308_CurrUnbal_A | Bore | Phase Current Imbalance | B308_CurrUnbal_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B308_CurrUnbal_A | C_LOPRI | B308 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B308
BR4_Tags | B308_EARTH_A | Bore | Earth Leakage Shutdown | B308_EARTH_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B308_EARTH_A | C_LOPRI | B308 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B308
BR4_Tags | B308_ECR_A | Bore | Earth Continuity Shutdown | B308_ECR_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B308_ECR_A | C_LOPRI | B308 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B308
BR4_Tags | B308_ECR_Overide_A | Bore | ECR Bypass On | B308_ECR_Overide_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B308_ECR_Overide_A | C_LOPRI | B308 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B308
BR4_Tags | B308_ECU_A | Bore | ECU Shutdown Fault | B308_ECU_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B308_ECU_A | C_LOPRI | B308 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B308
BR4_Tags | B308_ECUWarning_E | Bore | ECU Warning Fault | B308_ECUWarning_E | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B308_ECUWarning_E | C_LOPRI | B308 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B308
BR4_Tags | B308_FT01_Lo_A | Bore | Flow Low Warning | B308_FT01_Lo_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B308_FT01_Lo_A | C_LOPRI | B308 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B308.FT01
BR4_Tags | B308_FT01_LoLo_A | Bore | Flow Low Low Shutdown | B308_FT01_LoLo_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B308_FT01_LoLo_A | C_LOPRI | B308 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B308.FT01
BR4_Tags | B308_LOS_A | Bore | Emergency Stop Shutdown | B308_LOS_A | CAT_P1 |  | PRIV_ALARMACK | A_P1_SERV |  | B308_LOS_A | C_LOPRI | B308 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B308
BR4_Tags | B308_LT01_Lo_A | Bore | Low Bore Level Warning | B308_LT01_Lo_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B308_LT01_Lo_A | C_LOPRI | B308 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B308.LT01
BR4_Tags | B308_LT01_LoLo_A | Bore | Low Bore Level Shutdown | B308_LT01_LoLo_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B308_LT01_LoLo_A | C_LOPRI | B308 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B308.LT01
BR4_Tags | B308_LT02_Lo_A | Bore | Low Fuel Warning | B308_LT02_Lo_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B308_LT02_Lo_A | C_LOPRI | B308 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B308.LT02
BR4_Tags | B308_LT02_LoLo_A | Bore | Low Fuel Shutdown | B308_LT02_LoLo_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B308_LT02_LoLo_A | C_LOPRI | B308 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B308.LT02
BR4_Tags | B308_MCB_A | Bore | Main Breaker Tripped | B308_MCB_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B308_MCB_A | C_LOPRI | B308 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B308.MCB
BR4_Tags | B308_OverCurr_A | Bore | Over Current Shutdown | B308_OverCurr_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B308_OverCurr_A | C_LOPRI | B308 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B308
BR4_Tags | B308_OverVolt_A | Bore | Over Voltage Shutdown | B308_OverVolt_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B308_OverVolt_A | C_LOPRI | B308 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B308
BR4_Tags | B308_PT01_Hi_A | Bore | High Upstream Pressure Warning | B308_PT01_Hi_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B308_PT01_Hi_A | C_LOPRI | B308 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B308.PT01
BR4_Tags | B308_PT01_HiHi_A | Bore | High Upstream Pressure Shutdown | B308_PT01_HiHi_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B308_PT01_HiHi_A | C_LOPRI | B308 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B308.PT01
BR4_Tags | B308_PT02_Hi_A | Bore | High Downstream Pressure Warning | B308_PT02_Hi_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B308_PT02_Hi_A | C_LOPRI | B308 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B308.PT02
BR4_Tags | B308_PT02_HiHi_A | Bore | High Downstream Pressure Shutdown | B308_PT02_HiHi_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B308_PT02_HiHi_A | C_LOPRI | B308 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B308.PT02
BR4_Tags | B308_RnngFail_A | Bore | Failed while Running | B308_RnngFail_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B308_RnngFail_A | C_LOPRI | B308 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B308
BR4_Tags | B308_StpFail_A | Bore | Failed to Stop | B308_StpFail_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B308_StpFail_A | C_LOPRI | B308 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B308
BR4_Tags | B308_Stt_A | Bore | Excessive Starts | B308_Stt_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B308_Stt_A | C_LOPRI | B308 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B308
BR4_Tags | B308_SttFail_A | Bore | Failed to Start | B308_SttFail_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B308_SttFail_A | C_LOPRI | B308 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B308
BR4_Tags | B308_TOL01_A | Bore | Thermal Overload Shutdown | B308_TOL01_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B308_TOL01_A | C_LOPRI | B308 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B308
BR4_Tags | B308_TT01_Hi_A | Bore | High Pump Temp Warning | B308_TT01_Hi_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B308_TT01_Hi_A | C_LOPRI | B308 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B308.TT01
BR4_Tags | B308_TT01_HiHi_A | Bore | High Pump Temp Shutdown | B308_TT01_HiHi_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B308_TT01_HiHi_A | C_LOPRI | B308 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B308.TT01
BR4_Tags | B501_Commn_E | Bore | Common Warning Alarm | B501_Commn_E | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B501_Commn_E | C_LOPRI | B501 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B501
BR4_Tags | B501_CommnSd_A | Bore | Common Shutdown Alarm | B501_CommnSd_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B501_CommnSd_A | C_LOPRI | B501 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B501
BR4_Tags | B501_CommsFlt_A | Bore | Comms Fail | B501_CommsFlt_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B501_CommsFlt_A | C_LOPRI | B501 | Class_Equipment | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B501
BR4_Tags | B501_CurrUnbal_A | Bore | Phase Current Imbalance | B501_CurrUnbal_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B501_CurrUnbal_A | C_LOPRI | B501 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B501
BR4_Tags | B501_EARTH_A | Bore | Earth Leakage Shutdown | B501_EARTH_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B501_EARTH_A | C_LOPRI | B501 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B501
BR4_Tags | B501_ECR_A | Bore | Earth Continuity Shutdown | B501_ECR_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B501_ECR_A | C_LOPRI | B501 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B501
BR4_Tags | B501_ECR_Overide_A | Bore | ECR Bypass On | B501_ECR_Overide_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B501_ECR_Overide_A | C_LOPRI | B501 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B501
BR4_Tags | B501_ECU_A | Bore | ECU Shutdown Fault | B501_ECU_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B501_ECU_A | C_LOPRI | B501 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B501
BR4_Tags | B501_ECUWarning_E | Bore | ECU Warning Fault | B501_ECUWarning_E | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B501_ECUWarning_E | C_LOPRI | B501 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B501
BR4_Tags | B501_FT01_Lo_A | Bore | Flow Low Warning | B501_FT01_Lo_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B501_FT01_Lo_A | C_LOPRI | B501 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B501.FT01
BR4_Tags | B501_FT01_LoLo_A | Bore | Flow Low Low Shutdown | B501_FT01_LoLo_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B501_FT01_LoLo_A | C_LOPRI | B501 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B501.FT01
BR4_Tags | B501_LOS_A | Bore | Emergency Stop Shutdown | B501_LOS_A | CAT_P1 |  | PRIV_ALARMACK | A_P1_SERV |  | B501_LOS_A | C_LOPRI | B501 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B501
BR4_Tags | B501_LT01_Lo_A | Bore | Low Bore Level Warning | B501_LT01_Lo_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B501_LT01_Lo_A | C_LOPRI | B501 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B501.LT01
BR4_Tags | B501_LT01_LoLo_A | Bore | Low Bore Level Shutdown | B501_LT01_LoLo_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B501_LT01_LoLo_A | C_LOPRI | B501 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B501.LT01
BR4_Tags | B501_LT02_Lo_A | Bore | Low Fuel Warning | B501_LT02_Lo_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B501_LT02_Lo_A | C_LOPRI | B501 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B501.LT02
BR4_Tags | B501_LT02_LoLo_A | Bore | Low Fuel Shutdown | B501_LT02_LoLo_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B501_LT02_LoLo_A | C_LOPRI | B501 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B501.LT02
BR4_Tags | B501_MCB_A | Bore | Main Breaker Tripped | B501_MCB_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B501_MCB_A | C_LOPRI | B501 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B501.MCB
BR4_Tags | B501_OverCurr_A | Bore | Over Current Shutdown | B501_OverCurr_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B501_OverCurr_A | C_LOPRI | B501 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B501
BR4_Tags | B501_OverVolt_A | Bore | Over Voltage Shutdown | B501_OverVolt_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B501_OverVolt_A | C_LOPRI | B501 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B501
BR4_Tags | B501_PT01_Hi_A | Bore | High Upstream Pressure Warning | B501_PT01_Hi_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B501_PT01_Hi_A | C_LOPRI | B501 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B501.PT01
BR4_Tags | B501_PT01_HiHi_A | Bore | High Upstream Pressure Shutdown | B501_PT01_HiHi_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B501_PT01_HiHi_A | C_LOPRI | B501 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B501.PT01
BR4_Tags | B501_PT02_Hi_A | Bore | High Downstream Pressure Warning | B501_PT02_Hi_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B501_PT02_Hi_A | C_LOPRI | B501 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B501.PT02
BR4_Tags | B501_PT02_HiHi_A | Bore | High Downstream Pressure Shutdown | B501_PT02_HiHi_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B501_PT02_HiHi_A | C_LOPRI | B501 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B501.PT02
BR4_Tags | B501_RnngFail_A | Bore | Failed while Running | B501_RnngFail_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B501_RnngFail_A | C_LOPRI | B501 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B501
BR4_Tags | B501_StpFail_A | Bore | Failed to Stop | B501_StpFail_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B501_StpFail_A | C_LOPRI | B501 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B501
BR4_Tags | B501_Stt_A | Bore | Excessive Starts | B501_Stt_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B501_Stt_A | C_LOPRI | B501 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B501
BR4_Tags | B501_SttFail_A | Bore | Failed to Start | B501_SttFail_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B501_SttFail_A | C_LOPRI | B501 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B501
BR4_Tags | B501_TOL01_A | Bore | Thermal Overload Shutdown | B501_TOL01_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B501_TOL01_A | C_LOPRI | B501 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B501
BR4_Tags | B501_TT01_Hi_A | Bore | High Pump Temp Warning | B501_TT01_Hi_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B501_TT01_Hi_A | C_LOPRI | B501 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B501.TT01
BR4_Tags | B501_TT01_HiHi_A | Bore | High Pump Temp Shutdown | B501_TT01_HiHi_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B501_TT01_HiHi_A | C_LOPRI | B501 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B501.TT01
BR4_Tags | B503_CommsFlt_A | Bore | Comms Fail | B503_CommsFlt_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B503_CommsFlt_A | C_LOPRI | B503 | Class_Equipment | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B503
BR4_Tags | B503_DCOK01_A | Bore | 24V I/O Supply Fault | B503_DCOK01_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B503_DCOK01_A | C_LOPRI | B503 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B503
BR4_Tags | B503_DCOK02_A | Bore | 24V Supply Fault | B503_DCOK02_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B503_DCOK02_A | C_LOPRI | B503 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B503
BR4_Tags | B503_EARTH_A | Bore | Earth Leakage Fault | B503_EARTH_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B503_EARTH_A | C_LOPRI | B503 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B503
BR4_Tags | B503_ECR_A | Bore | ECR Fault | B503_ECR_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B503_ECR_A | C_LOPRI | B503 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B503
BR4_Tags | B503_FS01_A | Bore | Flow Switch Low | B503_FS01_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B503_FS01_A | C_LOPRI | B503 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B503
BR4_Tags | B503_FT01_Lo_A | Bore | Flow Low | B503_FT01_Lo_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B503_FT01_Lo_A | C_LOPRI | B503 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B503.FT01
BR4_Tags | B503_GenFlt_A | Bore | Generator Alarm | B503_GenFlt_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B503_GenFlt_A | C_LOPRI | B503 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B503
BR4_Tags | B503_GenFuelLow_A | Bore | Generator Fuel Low | B503_GenFuelLow_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B503_GenFuelLow_A | C_LOPRI | B503 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B503
BR4_Tags | B503_GenSttFail_A | Bore | Generator Failed to Start | B503_GenSttFail_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B503_GenSttFail_A | C_LOPRI | B503 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B503
BR4_Tags | B503_LOS01_A | Bore | E-stop 01 Activated | B503_LOS01_A | CAT_P1 |  | PRIV_ALARMACK | A_P1_SERV | E-stop 01 Activated | B503_LOS01_A | C_LOPRI | B503 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B503
BR4_Tags | B503_LOS02_A | Bore | E-stop 02 Activated | B503_LOS02_A | CAT_P1 |  | PRIV_ALARMACK | A_P1_SERV | E-stop 02 Activated | B503_LOS02_A | C_LOPRI | B503 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B503
BR4_Tags | B503_LSL_A | Bore | Level Switch Low | B503_LSL_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B503_LSL_A | C_LOPRI | B503 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B503
BR4_Tags | B503_LT01_Lo_A | Bore | Level Low | B503_LT01_Lo_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B503_LT01_Lo_A | C_LOPRI | B503 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B503.LT01
BR4_Tags | B503_MC01_A | Bore | Main Contactor Fault | B503_MC01_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B503_MC01_A | C_LOPRI | B503 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B503.MC01
BR4_Tags | B503_PT01_Hi_A | Bore | Upstream Pressure Hi | B503_PT01_Hi_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B503_PT01_Hi_A | C_LOPRI | B503 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B503.PT01
BR4_Tags | B503_PT01_HiHi_A | Bore | Upstream Pressure HiHi | B503_PT01_HiHi_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B503_PT01_HiHi_A | C_LOPRI | B503 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B503.PT01
BR4_Tags | B503_PT02_Hi_A | Bore | Downstream Pressure Hi | B503_PT02_Hi_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B503_PT02_Hi_A | C_LOPRI | B503 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B503.PT02
BR4_Tags | B503_PT02_HiHi_A | Bore | Downstream Pressure HiHi | B503_PT02_HiHi_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B503_PT02_HiHi_A | C_LOPRI | B503 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B503.PT02
BR4_Tags | B503_PS03_Hi_A | Bore | Pressure Hi | B503_PS03_Hi_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B503_PS03_Hi_A | C_LOPRI | B503 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B503
BR4_Tags | B503_PS04_HiHi_A | Bore | Pressure HiHi | B503_PS04_HiHi_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B503_PS04_HiHi_A | C_LOPRI | B503 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B503
BR4_Tags | B503_SD01Flt_A | Bore | Surge Diverter Fault | B503_SD01Flt_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B503_SD01Flt_A | C_LOPRI | B503 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B503
BR4_Tags | B503_SS01_A | Bore | Soft Starter Fault | B503_SS01_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B503_SS01_A | C_LOPRI | B503 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B503
BR4_Tags | B503_Stt_A | Bore | Excessive Starts | B503_Stt_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B503_Stt_A | C_LOPRI | B503 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B503
BR4_Tags | B503_TS01_Hi_A | Bore | Temp Switch Hi | B503_TS01_Hi_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B503_TS01_Hi_A | C_LOPRI | B503 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B503
BR4_Tags | B503_TT01_Hi_A | Bore | Temperature High | B503_TT01_Hi_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B503_TT01_Hi_A | C_LOPRI | B503 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B503.TT01
BR4_Tags | B505_Commn_E | Bore | Common Warning Alarm | B505_Commn_E | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B505_Commn_E | C_LOPRI | B505 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B505
BR4_Tags | B505_CommnSd_A | Bore | Common Shutdown Alarm | B505_CommnSd_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B505_CommnSd_A | C_LOPRI | B505 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B505
BR4_Tags | B505_CommsFlt_A | Bore | Comms Fail | B505_CommsFlt_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B505_CommsFlt_A | C_LOPRI | B505 | Class_Equipment | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B505
BR4_Tags | B505_CurrUnbal_A | Bore | Phase Current Imbalance | B505_CurrUnbal_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B505_CurrUnbal_A | C_LOPRI | B505 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B505
BR4_Tags | B505_EARTH_A | Bore | Earth Leakage Shutdown | B505_EARTH_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B505_EARTH_A | C_LOPRI | B505 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B505
BR4_Tags | B505_ECR_A | Bore | Earth Continuity Shutdown | B505_ECR_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B505_ECR_A | C_LOPRI | B505 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B505
BR4_Tags | B505_ECR_Overide_A | Bore | ECR Bypass On | B505_ECR_Overide_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B505_ECR_Overide_A | C_LOPRI | B505 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B505
BR4_Tags | B505_ECU_A | Bore | ECU Shutdown Fault | B505_ECU_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B505_ECU_A | C_LOPRI | B505 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B505
BR4_Tags | B505_ECUWarning_E | Bore | ECU Warning Fault | B505_ECUWarning_E | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B505_ECUWarning_E | C_LOPRI | B505 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B505
BR4_Tags | B505_FT01_Lo_A | Bore | Flow Low Warning | B505_FT01_Lo_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B505_FT01_Lo_A | C_LOPRI | B505 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B505.FT01
BR4_Tags | B505_FT01_LoLo_A | Bore | Flow Low Low Shutdown | B505_FT01_LoLo_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B505_FT01_LoLo_A | C_LOPRI | B505 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B505.FT01
BR4_Tags | B505_LOS_A | Bore | Emergency Stop Shutdown | B505_LOS_A | CAT_P1 |  | PRIV_ALARMACK | A_P1_SERV |  | B505_LOS_A | C_LOPRI | B505 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B505
BR4_Tags | B505_LT01_Lo_A | Bore | Low Bore Level Warning | B505_LT01_Lo_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B505_LT01_Lo_A | C_LOPRI | B505 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B505.LT01
BR4_Tags | B505_LT01_LoLo_A | Bore | Low Bore Level Shutdown | B505_LT01_LoLo_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B505_LT01_LoLo_A | C_LOPRI | B505 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B505.LT01
BR4_Tags | B505_LT02_Lo_A | Bore | Low Fuel Warning | B505_LT02_Lo_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B505_LT02_Lo_A | C_LOPRI | B505 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B505.LT02
BR4_Tags | B505_LT02_LoLo_A | Bore | Low Fuel Shutdown | B505_LT02_LoLo_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B505_LT02_LoLo_A | C_LOPRI | B505 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B505.LT02
BR4_Tags | B505_MCB_A | Bore | Main Breaker Tripped | B505_MCB_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B505_MCB_A | C_LOPRI | B505 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B505.MCB
BR4_Tags | B505_OverCurr_A | Bore | Over Current Shutdown | B505_OverCurr_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B505_OverCurr_A | C_LOPRI | B505 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B505
BR4_Tags | B505_OverVolt_A | Bore | Over Voltage Shutdown | B505_OverVolt_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B505_OverVolt_A | C_LOPRI | B505 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B505
BR4_Tags | B505_PT01_Hi_A | Bore | High Upstream Pressure Warning | B505_PT01_Hi_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B505_PT01_Hi_A | C_LOPRI | B505 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B505.PT01
BR4_Tags | B505_PT01_HiHi_A | Bore | High Upstream Pressure Shutdown | B505_PT01_HiHi_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B505_PT01_HiHi_A | C_LOPRI | B505 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B505.PT01
BR4_Tags | B505_PT02_Hi_A | Bore | High Downstream Pressure Warning | B505_PT02_Hi_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B505_PT02_Hi_A | C_LOPRI | B505 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B505.PT02
BR4_Tags | B505_PT02_HiHi_A | Bore | High Downstream Pressure Shutdown | B505_PT02_HiHi_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B505_PT02_HiHi_A | C_LOPRI | B505 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B505.PT02
BR4_Tags | B505_RnngFail_A | Bore | Failed while Running | B505_RnngFail_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B505_RnngFail_A | C_LOPRI | B505 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B505
BR4_Tags | B505_StpFail_A | Bore | Failed to Stop | B505_StpFail_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B505_StpFail_A | C_LOPRI | B505 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B505
BR4_Tags | B505_Stt_A | Bore | Excessive Starts | B505_Stt_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B505_Stt_A | C_LOPRI | B505 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B505
BR4_Tags | B505_SttFail_A | Bore | Failed to Start | B505_SttFail_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B505_SttFail_A | C_LOPRI | B505 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B505
BR4_Tags | B505_TOL01_A | Bore | Thermal Overload Shutdown | B505_TOL01_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B505_TOL01_A | C_LOPRI | B505 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B505
BR4_Tags | B505_TT01_Hi_A | Bore | High Pump Temp Warning | B505_TT01_Hi_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B505_TT01_Hi_A | C_LOPRI | B505 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B505.TT01
BR4_Tags | B505_TT01_HiHi_A | Bore | High Pump Temp Shutdown | B505_TT01_HiHi_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B505_TT01_HiHi_A | C_LOPRI | B505 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B505.TT01
BR4_Tags | BCP1760NP01DCOK_A | Proc Wtr SwRm Comms Panel | 24VDC Power Supply Trip | BCP1760NP01DCOK_A | CAT_P3 | SWRBSR1760 | PRIV_ALARMACK | A_CM_POWER | Comms Cubicle 24 VDC OK | BCP1760NP01DCOK_A | C_LOPRI | BCP1760NP01 | Class_Process | BR4_Cluster1 | BR4.SRV.PWR.BSR1760.BCP1760NP01
BR4_Tags | BMC1760_ML1CommsOK_A | Water Distribution PLC | MNSiS MLink 1 Communications Faulted Trip | BMC1760_ML1CommsOK_A | CAT_P2 | BPL760 | PRIV_ALARMACK | A_P1_SERV | MNSiS MLink 1 Communications Faulted Trip | BMC1760_ML1CommsOK_A | C_HIPRI | BPL760 | Class_Equipment | BR4_Cluster1 | BR4.SRV.PWR.BSR1760.BMC1760
BR4_Tags | BMC1760DCOK_A | Proc Wtr Swtchrm 415V MCC | Control Circuit 24VDC Power Supply Trip | BMC1760DCOK_A | CAT_P3 | POWERDIST1 | PRIV_ALARMACK | A_CM_POWER | Control Circuit 24 VDC OK | BMC1760DCOK_A | C_LOPRI | BMC1760Inc | Class_Process | BR4_Cluster1 | BR4.SRV.PWR.BSR1760.BMC1760
BR4_Tags | BMC1760Inc_CommsOK_A | Proc Wtr SwRm 415V Incomer | Circuit Breaker Communications Fault | BMC1760Inc_CommsOK_A | CAT_P3 | POWERDIST1 | PRIV_ALARMACK | A_CM_POWER | Incomer Communications Fault | BMC1760Inc_CommsOK_A | C_LOPRI | BMC1760Inc | Class_Equipment | BR4_Cluster1 | BR4.SRV.PWR.BSR1760.BMC1760.Inc
BR4_Tags | B309_BoostPress_A | Bore | Turbo Boost Pressure Alarm | B309_BoostPress_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV | Turbo Boost Pressure Alarm | B309_BoostPress_A | C_LOPRI | B309 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B309
BR4_Tags | B309_Commn_E | Bore | Common Warning Alarm | B309_Commn_E | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV | Common Warning Alarm | B309_Commn_E | C_LOPRI | B309 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B309
BR4_Tags | B309_CommnSd_A | Bore | Common Shutdown Alarm | B309_CommnSd_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV | Common Shutdown Alarm | B309_CommnSd_A | C_LOPRI | B309 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B309
BR4_Tags | B309_CommsFlt_A | Bore | Comms Fail | B309_CommsFlt_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV | Comms Fail | B309_CommsFlt_A | C_LOPRI | B309 | Class_Equipment | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B309
BR4_Tags | B309_CoolantTemp_A | Bore | B309 Coolant Temp Alarm | B309_CoolantTemp_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV | B309 Coolant Temp Alarm | B309_CoolantTemp_A | C_LOPRI | B309 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B309
BR4_Tags | B309_CurrUnbal_A | Bore | Phase Current Imbalance | B309_CurrUnbal_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV | Phase Current Imbalance | B309_CurrUnbal_A | C_LOPRI | B309 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B309
BR4_Tags | B309_EARTH_A | Bore | Earth Leakage Shutdown | B309_EARTH_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV | Earth Leakage Shutdown | B309_EARTH_A | C_LOPRI | B309 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B309
BR4_Tags | B309_ECR_A | Bore | Earth Continuity Shutdown | B309_ECR_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV | Earth Continuity Shutdown | B309_ECR_A | C_LOPRI | B309 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B309
BR4_Tags | B309_ECR_Overide_A | Bore | ECR Bypass On | B309_ECR_Overide_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV | ECR Bypass On | B309_ECR_Overide_A | C_LOPRI | B309 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B309
BR4_Tags | B309_ECU_A | Bore | ECU Shutdown Fault | B309_ECU_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV | ECU Shutdown Fault | B309_ECU_A | C_LOPRI | B309 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B309
BR4_Tags | B309_ECUWarning_E | Bore | ECU Warning Fault | B309_ECUWarning_E | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV | ECU Warning Fault | B309_ECUWarning_E | C_LOPRI | B309 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B309
BR4_Tags | B309_FT01_Lo_A | Bore | Flow Low Warning | B309_FT01_Lo_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV | Flow Low Warning | B309_FT01_Lo_A | C_LOPRI | B309 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B309.FT01
BR4_Tags | B309_FT01_LoLo_A | Bore | Flow Low Low Shutdown | B309_FT01_LoLo_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV | Flow Low Low Shutdown | B309_FT01_LoLo_A | C_LOPRI | B309 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B309.FT01
BR4_Tags | B309_IntakeTemp_A | Bore | B309 Intake Temp Alarm | B309_IntakeTemp_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV | B309 Intake Temp Alarm | B309_IntakeTemp_A | C_LOPRI | B309 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B309
BR4_Tags | B309_LOS_A | Bore | Emergency Stop Shutdown | B309_LOS_A | CAT_P1 |  | PRIV_ALARMACK | A_P1_SERV | Emergency Stop Shutdown | B309_LOS_A | C_LOPRI | B309 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B309
BR4_Tags | B309_LT01_Lo_A | Bore | Low Bore Level Warning | B309_LT01_Lo_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV | Low Bore Level Warning | B309_LT01_Lo_A | C_LOPRI | B309 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B309.LT01
BR4_Tags | B309_LT01_LoLo_A | Bore | Low Bore Level Shutdown | B309_LT01_LoLo_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV | Low Bore Level Shutdown | B309_LT01_LoLo_A | C_LOPRI | B309 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B309.LT01
BR4_Tags | B309_LT02_Lo_A | Bore | Int Fuel Tank Lo Warning | B309_LT02_Lo_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV | Int Fuel Tank Lo Warning | B309_LT02_Lo_A | C_LOPRI | B309 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B309.LT02
BR4_Tags | B309_LT02_LoLo_A | Bore | Int Fuel Tank Lo Lo Shutdown | B309_LT02_LoLo_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV | Int Fuel Tank Lo Lo Shutdown | B309_LT02_LoLo_A | C_LOPRI | B309 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B309.LT02
BR4_Tags | B309_LT03_Lo_A | Bore | B309 Ext Fuel Tank Lo Warning | B309_LT03_Lo_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV | B309 Ext Fuel Tank Lo Warning | B309_LT03_Lo_A | C_LOPRI | B309 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B309.LT03
BR4_Tags | B309_LT03_LoLo_A | Bore | B309 Ext Fuel Tank Lo Lo Shutdown | B309_LT03_LoLo_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV | B309 Ext Fuel Tank Lo Lo Shutdown | B309_LT03_LoLo_A | C_LOPRI | B309 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B309.LT03
BR4_Tags | B309_MCB_A | Bore | Main Breaker Tripped | B309_MCB_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV | Main Breaker Tripped | B309_MCB_A | C_LOPRI | B309 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B309.MCB
BR4_Tags | B309_OilPress_A | Bore | B309 Oil Pressure Alarm | B309_OilPress_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV | B309 Oil Pressure Alarm | B309_OilPress_A | C_LOPRI | B309 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B309
BR4_Tags | B309_OverCurr_A | Bore | Over Current Shutdown | B309_OverCurr_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV | Over Current Shutdown | B309_OverCurr_A | C_LOPRI | B309 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B309
BR4_Tags | B309_OverVolt_A | Bore | Over Voltage Shutdown | B309_OverVolt_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV | Over Voltage Shutdown | B309_OverVolt_A | C_LOPRI | B309 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B309
BR4_Tags | B309_PT01_Hi_A | Bore | High Upstream Pressure Warning | B309_PT01_Hi_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV | High Upstream Pressure Warning | B309_PT01_Hi_A | C_LOPRI | B309 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B309.PT01
BR4_Tags | B309_PT01_HiHi_A | Bore | High Upstream Pressure Shutdown | B309_PT01_HiHi_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV | High Upstream Pressure Shutdown | B309_PT01_HiHi_A | C_LOPRI | B309 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B309.PT01
BR4_Tags | B309_PT02_Hi_A | Bore | High Downstream Pressure Warning | B309_PT02_Hi_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV | High Downstream Pressure Warning | B309_PT02_Hi_A | C_LOPRI | B309 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B309.PT02
BR4_Tags | B309_PT02_HiHi_A | Bore | High Downstream Pressure Shutdown | B309_PT02_HiHi_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV | High Downstream Pressure Shutdown | B309_PT02_HiHi_A | C_LOPRI | B309 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B309.PT02
BR4_Tags | B309_RnngFail_A | Bore | Failed while Running | B309_RnngFail_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV | Failed while Running | B309_RnngFail_A | C_LOPRI | B309 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B309
BR4_Tags | B309_StpFail_A | Bore | Failed to Stop | B309_StpFail_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV | Failed to Stop | B309_StpFail_A | C_LOPRI | B309 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B309
BR4_Tags | B309_Stt_A | Bore | Excessive Starts | B309_Stt_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV | Excessive Starts | B309_Stt_A | C_LOPRI | B309 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B309
BR4_Tags | B309_SttFail_A | Bore | Failed to Start | B309_SttFail_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV | Failed to Start | B309_SttFail_A | C_LOPRI | B309 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B309
BR4_Tags | B309_TOL01_A | Bore | Thermal Overload Shutdown | B309_TOL01_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV | Thermal Overload Shutdown | B309_TOL01_A | C_LOPRI | B309 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B309
BR4_Tags | B309_TT01_Hi_A | Bore | High Pump Temp Warning | B309_TT01_Hi_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV | High Pump Temp Warning | B309_TT01_Hi_A | C_LOPRI | B309 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B309.TT01
BR4_Tags | B309_TT01_HiHi_A | Bore | High Pump Temp Shutdown | B309_TT01_HiHi_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV | High Pump Temp Shutdown | B309_TT01_HiHi_A | C_LOPRI | B309 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B309.TT01
BR4_Tags | BP1543_CommsFlt_A | Bore | Comms Fail | BP1543_CommsFlt_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | BP1543_CommsFlt_A | C_LOPRI | BP1543 | Class_Equipment | BR4_Cluster1 | BR4.UTILITIES.WATER.EBBWD.BP1543
BR4_Tags | BP1543_DCOK01_A | Bore | 24V I/O Supply Fault | BP1543_DCOK01_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | BP1543_DCOK01_A | C_LOPRI | BP1543 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.EBBWD.BP1543
BR4_Tags | BP1543_DCOK02_A | Bore | 24V Supply Fault | BP1543_DCOK02_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | BP1543_DCOK02_A | C_LOPRI | BP1543 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.EBBWD.BP1543
BR4_Tags | BP1543_EARTH_A | Bore | Earth Leakage Fault | BP1543_EARTH_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | BP1543_EARTH_A | C_LOPRI | BP1543 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.EBBWD.BP1543
BR4_Tags | BP1543_ECR_A | Bore | ECR Fault | BP1543_ECR_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | BP1543_ECR_A | C_LOPRI | BP1543 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.EBBWD.BP1543
BR4_Tags | BP1543_FS01_A | Bore | Flow Switch Low | BP1543_FS01_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | BP1543_FS01_A | C_LOPRI | BP1543 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.EBBWD.BP1543
BR4_Tags | BP1543_FT01_Lo_A | Bore | Flow Low | BP1543_FT01_Lo_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | BP1543_FT01_Lo_A | C_LOPRI | BP1543 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.EBBWD.BP1543.FT01
BR4_Tags | BP1543_GenFlt_A | Bore | Generator Alarm | BP1543_GenFlt_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | BP1543_GenFlt_A | C_LOPRI | BP1543 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.EBBWD.BP1543
BR4_Tags | BP1543_GenFuelLow_A | Bore | Generator Fuel Low | BP1543_GenFuelLow_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | BP1543_GenFuelLow_A | C_LOPRI | BP1543 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.EBBWD.BP1543
BR4_Tags | BP1543_GenSttFail_A | Bore | Generator Failed to Start | BP1543_GenSttFail_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | BP1543_GenSttFail_A | C_LOPRI | BP1543 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.EBBWD.BP1543
BR4_Tags | BP1543_LOS01_A | Bore | E-stop 01 Activated | BP1543_LOS01_A | CAT_P1 |  | PRIV_ALARMACK | A_P1_SERV | E-stop 01 Activated | BP1543_LOS01_A | C_LOPRI | BP1543 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.EBBWD.BP1543.LOS01
BR4_Tags | BP1543_LOS02_A | Bore | E-stop 02 Activated | BP1543_LOS02_A | CAT_P1 |  | PRIV_ALARMACK | A_P1_SERV | E-stop 02 Activated | BP1543_LOS02_A | C_LOPRI | BP1543 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.EBBWD.BP1543.LOS02
BR4_Tags | BP1543_LSL_A | Bore | Level Switch Low | BP1543_LSL_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | BP1543_LSL_A | C_LOPRI | BP1543 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.EBBWD.BP1543
BR4_Tags | BP1543_LT01_Lo_A | Bore | Level Low | BP1543_LT01_Lo_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | BP1543_LT01_Lo_A | C_LOPRI | BP1543 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.EBBWD.BP1543.LT01
BR4_Tags | BP1543_MC01_A | Bore | Main Contactor Fault | BP1543_MC01_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | BP1543_MC01_A | C_LOPRI | BP1543 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.EBBWD.BP1543.MC01
BR4_Tags | BP1543_PS03_Hi_A | Bore | Pressure Hi | BP1543_PS03_Hi_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | BP1543_PS03_Hi_A | C_LOPRI | BP1543 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.EBBWD.BP1543
BR4_Tags | BP1543_PS04_HiHi_A | Bore | Pressure HiHi | BP1543_PS04_HiHi_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | BP1543_PS04_HiHi_A | C_LOPRI | BP1543 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.EBBWD.BP1543
BR4_Tags | BP1543_SD01Flt_A | Bore | Surge Diverter Fault | BP1543_SD01Flt_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | BP1543_SD01Flt_A | C_LOPRI | BP1543 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.EBBWD.BP1543
BR4_Tags | BP1543_SS01_A | Bore | Soft Starter Fault | BP1543_SS01_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | BP1543_SS01_A | C_LOPRI | BP1543 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.EBBWD.BP1543
BR4_Tags | BP1543_Stt_A | Bore | Excessive Starts | BP1543_Stt_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | BP1543_Stt_A | C_LOPRI | BP1543 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.EBBWD.BP1543
BR4_Tags | BP1543_TS01_Hi_A | Bore | Temp Switch Hi | BP1543_TS01_Hi_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | BP1543_TS01_Hi_A | C_LOPRI | BP1543 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.EBBWD.BP1543
BR4_Tags | BP1543_TT01_Hi_A | Bore | Temperature High | BP1543_TT01_Hi_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | BP1543_TT01_Hi_A | C_LOPRI | BP1543 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.EBBWD.BP1543.TT01
BR4_Tags | BPL201C18_AICh1OK_A | PLC 201 Drop C - BCV210MB01 | Slot 18 Channel 1 General Fault | BPL201C18_AICh1OK_A | CAT_P3 | BPL201 | PRIV_ALARMACK | A_P1_SERV | Slot 18 Channel 1 General Fault | BPL201C18_AICh1OK_A | C_LOPRI | BPL201DropC | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL201.DropC
BR4_Tags | BPL201C18_AICh2OK_A | PLC 201 Drop C - BCV210MB01 | Slot 18 Channel 2 General Fault | BPL201C18_AICh2OK_A | CAT_P3 | BPL201 | PRIV_ALARMACK | A_P1_SERV | Slot 18 Channel 2 General Fault | BPL201C18_AICh2OK_A | C_LOPRI | BPL201DropC | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL201.DropC
BR4_Tags | BPL201C18_OK_A | PLC 201 Drop C - BCV210MB01 | Slot 18 Module Fault | BPL201C18_OK_A | CAT_P3 | BPL201 | PRIV_ALARMACK | A_P1_SERV | Slot 18 Module Fault | BPL201C18_OK_A | C_LOPRI | BPL201DropC | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL201.DropC | Slot18_A
BR4_Tags | BPL201C19_CntrlPwrOK_A | PLC 201 Drop C - BCV210MB01 | Slot 19 Module General Fault | BPL201C19_CntrlPwrOK_A | CAT_P3 | BPL201 | PRIV_ALARMACK | A_P1_SERV | Slot 19 Module General Fault | BPL201C19_CntrlPwrOK_A | C_LOPRI | BPL201DropC | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL201.DropC
BR4_Tags | BPL201C19_OK_A | PLC 201 Drop C - BCV210MB01 | Slot 19 Module Fault | BPL201C19_OK_A | CAT_P3 | BPL201 | PRIV_ALARMACK | A_P1_SERV | Slot 19 Module Fault | BPL201C19_OK_A | C_LOPRI | BPL201DropC | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL201.DropC | Slot19_A
BR4_Tags | BPL201C20_CntrlPwrOK_A | PLC 201 Drop C - BCV210MB01 | Slot 20 Module General Fault | BPL201C20_CntrlPwrOK_A | CAT_P3 | BPL201 | PRIV_ALARMACK | A_P1_SERV | Slot 20 Module General Fault | BPL201C20_CntrlPwrOK_A | C_LOPRI | BPL201DropC | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL201.DropC
BR4_Tags | BPL201C20_OK_A | PLC 201 Drop C - BCV210MB01 | Slot 20 Module Fault | BPL201C20_OK_A | CAT_P3 | BPL201 | PRIV_ALARMACK | A_P1_SERV | Slot 20 Module Fault | BPL201C20_OK_A | C_LOPRI | BPL201DropC | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL201.DropC | Slot20_A
BR4_Tags | BPL751_BPL751D10CommsFlt_A | East Bore Transfer Pumps PLC | InterPLC Bore D10 Communications Faulted | BPL751_BPL751D10CommsFlt_A | CAT_P3 | BPL751 | PRIV_ALARMACK | A_P1_SERV | BPL751D10 Comms Fault Alarm | BPL751_BPL751D10CommsFlt_A | C_LOPRI | BPL751 | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL751
BR4_Tags | BPL751_BPL761CommsFlt_A | East Borefield PLC | East Bore 751 to EBFT 761 Communications Fault | BPL751_BPL761CommsFlt_A | CAT_P3 | BPL751 | PRIV_ALARMACK | A_P1_SERV | East Bore 751 to EBFT 761 Communications Fault | BPL751_BPL761CommsFlt_A | C_LOPRI | BPL751 | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL751
BR4_Tags | BPL751_CPUEthModLinkOK_A | East Bore Transfer Pumps PLC | CPU Module Ethernet Link Fault | BPL751_CPUEthModLinkOK_A | CAT_P2 | BPL751 | PRIV_ALARMACK | A_P1_SERV | CPU Module Ethernet Link Fault | BPL751_CPUEthModLinkOK_A | C_HIPRI | BPL751 | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL751
BR4_Tags | BPL751_CPUEthModRnng_A | East Bore Transfer Pumps PLC | CPU Module Ethernet Port Not Running Fault | BPL751_CPUEthModRnng_A | CAT_P2 | BPL751 | PRIV_ALARMACK | A_P1_SERV | CPU Module Ethernet Port Not Running Fault | BPL751_CPUEthModRnng_A | C_HIPRI | BPL751 | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL751
BR4_Tags | BPL751_NOE1LinkOK_A | East Bore Transfer Pumps PLC | NOE1 Ethernet Link Status Fault | BPL751_NOE1LinkOK_A | CAT_P2 | BPL751 | PRIV_ALARMACK | A_P1_SERV | NOE1 Ethernet Link Status Fault | BPL751_NOE1LinkOK_A | C_HIPRI | BPL751 | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL751
BR4_Tags | BPL751_NOE1Rnng_A | East Bore Transfer Pumps PLC | NOE1 Ethernet Module Not Running | BPL751_NOE1Rnng_A | CAT_P2 | BPL751 | PRIV_ALARMACK | A_P1_SERV | NOE1 Ethernet Module Not Running | BPL751_NOE1Rnng_A | C_HIPRI | BPL751 | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL751 | Slot7_A
BR4_Tags | BPL751_R0S1OK_A | East Bore Transfer Pumps PLC | Rack 0 Slot 1 Module Fault | BPL751_R0S1OK_A | CAT_P3 | BPL751 | PRIV_ALARMACK | A_P1_SERV | Rack 0 Slot 1 Module Fault | BPL751_R0S1OK_A | C_LOPRI | BPL751 | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL751 | Slot1_A
BR4_Tags | BPL751_R0S2OK_A | East Bore Transfer Pumps PLC | Rack 0 Slot 2 Module Fault | BPL751_R0S2OK_A | CAT_P3 | BPL751 | PRIV_ALARMACK | A_P1_SERV | Rack 0 Slot 2 Module Fault | BPL751_R0S2OK_A | C_LOPRI | BPL751 | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL751 | Slot2_A
BR4_Tags | BPL751_R0S3OK_A | East Bore Transfer Pumps PLC | Rack 0 Slot 3 Module Fault | BPL751_R0S3OK_A | CAT_P3 | BPL751 | PRIV_ALARMACK | A_P1_SERV | Rack 0 Slot 3 Module Fault | BPL751_R0S3OK_A | C_LOPRI | BPL751 | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL751 | Slot3_A
BR4_Tags | BPL751_R0S4OK_A | East Bore Transfer Pumps PLC | Rack 0 Slot 4 Module Fault | BPL751_R0S4OK_A | CAT_P3 | BPL751 | PRIV_ALARMACK | A_P1_SERV | Rack 0 Slot 4 Module Fault | BPL751_R0S4OK_A | C_LOPRI | BPL751 | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL751 | Slot4_A
BR4_Tags | BPL751_R0S5Ch0OK_A | East Bore Transfer Pumps PLC | Rack 0 Slot 5 Channel 0 Fault | BPL751_R0S5Ch0OK_A | CAT_P3 | BPL751 | PRIV_ALARMACK | A_P1_SERV | Rack 0 Slot 5 Channel 0 Fault | BPL751_R0S5Ch0OK_A | C_LOPRI | BPL751 | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL751
BR4_Tags | BPL751_R0S5Ch0ROVF_E | East Bore Transfer Pumps PLC | Rack 0 Slot 5 Channel 0 Range Overflow | BPL751_R0S5Ch0ROVF_E | CAT_P4 | BPL751 | PRIV_ALARMACK | A_P1_SERV | Rack 0 Slot 5 Channel 0 Overflow Error | BPL751_R0S5Ch0ROVF_E | C_EVENT | BPL751 | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL751
BR4_Tags | BPL751_R0S5Ch0RUNF_E | East Bore Transfer Pumps PLC | Rack 0 Slot 5 Channel 0 Range Underflow | BPL751_R0S5Ch0RUNF_E | CAT_P4 | BPL751 | PRIV_ALARMACK | A_P1_SERV | Rack 0 Slot 5 Channel 0 Underflow Error | BPL751_R0S5Ch0RUNF_E | C_EVENT | BPL751 | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL751
BR4_Tags | BPL751_R0S5Ch1OK_A | East Bore Transfer Pumps PLC | Rack 0 Slot 5 Channel 1 Fault | BPL751_R0S5Ch1OK_A | CAT_P3 | BPL751 | PRIV_ALARMACK | A_P1_SERV | Rack 0 Slot 5 Channel 1 Fault | BPL751_R0S5Ch1OK_A | C_LOPRI | BPL751 | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL751
BR4_Tags | BPL751_R0S5Ch1ROVF_E | East Bore Transfer Pumps PLC | Rack 0 Slot 5 Channel 1 Range Overflow | BPL751_R0S5Ch1ROVF_E | CAT_P4 | BPL751 | PRIV_ALARMACK | A_P1_SERV | Rack 0 Slot 5 Channel 1 Overflow Error | BPL751_R0S5Ch1ROVF_E | C_EVENT | BPL751 | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL751
BR4_Tags | BPL751_R0S5Ch1RUNF_E | East Bore Transfer Pumps PLC | Rack 0 Slot 5 Channel 1 Range Underflow | BPL751_R0S5Ch1RUNF_E | CAT_P4 | BPL751 | PRIV_ALARMACK | A_P1_SERV | Rack 0 Slot 5 Channel 1 Underflow Error | BPL751_R0S5Ch1RUNF_E | C_EVENT | BPL751 | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL751
BR4_Tags | BPL751_R0S5Ch2OK_A | East Bore Transfer Pumps PLC | Rack 0 Slot 5 Channel 2 Fault | BPL751_R0S5Ch2OK_A | CAT_P3 | BPL751 | PRIV_ALARMACK | A_P1_SERV | Rack 0 Slot 5 Channel 2 Fault | BPL751_R0S5Ch2OK_A | C_LOPRI | BPL751 | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL751
BR4_Tags | BPL751_R0S5Ch2ROVF_E | East Bore Transfer Pumps PLC | Rack 0 Slot 5 Channel 2 Range Overflow | BPL751_R0S5Ch2ROVF_E | CAT_P4 | BPL751 | PRIV_ALARMACK | A_P1_SERV | Rack 0 Slot 5 Channel 2 Overflow Error | BPL751_R0S5Ch2ROVF_E | C_EVENT | BPL751 | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL751
BR4_Tags | BPL751_R0S5Ch2RUNF_E | East Bore Transfer Pumps PLC | Rack 0 Slot 5 Channel 2 Range Underflow | BPL751_R0S5Ch2RUNF_E | CAT_P4 | BPL751 | PRIV_ALARMACK | A_P1_SERV | Rack 0 Slot 5 Channel 2 Underflow Error | BPL751_R0S5Ch2RUNF_E | C_EVENT | BPL751 | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL751
BR4_Tags | BPL751_R0S5OK_A | East Bore Transfer Pumps PLC | Rack 0 Slot 5 Module Fault | BPL751_R0S5OK_A | CAT_P3 | BPL751 | PRIV_ALARMACK | A_P1_SERV | Rack 0 Slot 5 Module Fault | BPL751_R0S5OK_A | C_LOPRI | BPL751 | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL751 | Slot5_A
BR4_Tags | BPL751D10_BPL751CommsFlt_A | East Dewatering Bore 10 PLC | InterPLC BPL751 Communications Faulted | BPL751D10_BPL751CommsFlt_A | CAT_P3 | BPL751 | PRIV_ALARMACK | A_P1_SERV | DWB10 East Bore to East Bore 751 Comms Fault | BPL751D10_BPL751CommsFlt_A | C_LOPRI | BPL751D10 | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL751.D10
BR4_Tags | BPL751D10_CPUEthModLinkOK_A | East Dewatering Bore 10 PLC | CPU Module Ethernet Link Fault | BPL751D10_CPUEthModLinkOK_A | CAT_P2 | BPL751 | PRIV_ALARMACK | A_P1_SERV | CPU Module Ethernet Link Fault | BPL751D10_CPUEthModLinkOK_A | C_HIPRI | BPL751D10 | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL751.D10
BR4_Tags | BPL751D10_CPUEthModRnng_A | East Dewatering Bore 10 PLC | CPU Module Ethernet Port Not Running Fault | BPL751D10_CPUEthModRnng_A | CAT_P2 | BPL751 | PRIV_ALARMACK | A_P1_SERV | CPU Module Ethernet Port Not Running Fault | BPL751D10_CPUEthModRnng_A | C_HIPRI | BPL751D10 | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL751.D10
BR4_Tags | BPL751D10_NOE1LinkOK_A | East Dewatering Bore 10 PLC | NOE1 Ethernet Link Status Fault | BPL751D10_NOE1LinkOK_A | CAT_P2 | BPL751 | PRIV_ALARMACK | A_P1_SERV | NOE1 Ethernet Link Status Fault | BPL751D10_NOE1LinkOK_A | C_HIPRI | BPL751D10 | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL751.D10
BR4_Tags | BPL751D10_NOE1Rnng_A | East Dewatering Bore 10 PLC | NOE1 Ethernet Module Not Running | BPL751D10_NOE1Rnng_A | CAT_P2 | BPL751 | PRIV_ALARMACK | A_P1_SERV | NOE1 Ethernet Module Not Running | BPL751D10_NOE1Rnng_A | C_HIPRI | BPL751D10 | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL751.D10 | Slot7_A
BR4_Tags | BPL751D10_R0S1OK_A | East Dewatering Bore 10 PLC | Rack 0 Slot 1 Module Fault | BPL751D10_R0S1OK_A | CAT_P3 | BPL751 | PRIV_ALARMACK | A_P1_SERV | Rack 0 Slot 1 Module Fault | BPL751D10_R0S1OK_A | C_LOPRI | BPL751D10 | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL751.D10 | Slot1_A
BR4_Tags | BPL751D10_R0S2OK_A | East Dewatering Bore 10 PLC | Rack 0 Slot 2 Module Fault | BPL751D10_R0S2OK_A | CAT_P3 | BPL751 | PRIV_ALARMACK | A_P1_SERV | Rack 0 Slot 2 Module Fault | BPL751D10_R0S2OK_A | C_LOPRI | BPL751D10 | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL751.D10 | Slot2_A
BR4_Tags | BPL751D10_R0S3Ch0OK_A | East Dewatering Bore 10 PLC | Rack 0 Slot 3 Channel 0 Fault | BPL751D10_R0S3Ch0OK_A | CAT_P3 | BPL751 | PRIV_ALARMACK | A_P1_SERV | Rack 0 Slot 3 Channel 0 Fault | BPL751D10_R0S3Ch0OK_A | C_LOPRI | BPL751D10 | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL751.D10
BR4_Tags | BPL751D10_R0S3Ch0ROVF_E | East Dewatering Bore 10 PLC | Rack 0 Slot 3 Channel 0 Range Overflow | BPL751D10_R0S3Ch0ROVF_E | CAT_P4 | BPL751 | PRIV_ALARMACK | A_P1_SERV | Rack 0 Slot 3 Channel 0 Overflow Error | BPL751D10_R0S3Ch0ROVF_E | C_EVENT | BPL751D10 | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL751.D10
BR4_Tags | BPL751D10_R0S3Ch0RUNF_E | East Dewatering Bore 10 PLC | Rack 0 Slot 3 Channel 0 Range Underflow | BPL751D10_R0S3Ch0RUNF_E | CAT_P4 | BPL751 | PRIV_ALARMACK | A_P1_SERV | Rack 0 Slot 3 Channel 0 Underflow Error | BPL751D10_R0S3Ch0RUNF_E | C_EVENT | BPL751D10 | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL751.D10
BR4_Tags | BPL751D10_R0S3OK_A | East Dewatering Bore 10 PLC | Rack 0 Slot 3 Module Fault | BPL751D10_R0S3OK_A | CAT_P3 | BPL751 | PRIV_ALARMACK | A_P1_SERV | Rack 0 Slot 3 Module Fault | BPL751D10_R0S3OK_A | C_LOPRI | BPL751D10 | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL751.D10 | Slot3_A
BR4_Tags | BPL752_BPL101CommsFlt_A | West Bore Transfer Pumps PLC | InterPLC BPL101 Communications Faulted | BPL752_BPL101CommsFlt_A | CAT_P3 | BPL752 | PRIV_ALARMACK | A_P1_SERV | InterPLC BPL101 Communications Faulted | BPL752_BPL101CommsFlt_A | C_LOPRI | BPL752 | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL752
BR4_Tags | BPL752_BPL330CommsFlt_A | West Borefield PLC | West Bore 752 to Nest 330 Communications Fault | BPL752_BPL330CommsFlt_A | CAT_P3 | BPL752 | PRIV_ALARMACK | A_P1_SERV | West Bore 752 to Nest 330 Communications Fault | BPL752_BPL330CommsFlt_A | C_LOPRI | BPL752 | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL752
BR4_Tags | BPL752_BPL4101CommsFlt_A | West Borefield PLC | West Bore 752 to Nest 4101 Communications Fault | BPL752_BPL4101CommsFlt_A | CAT_P3 | BPL752 | PRIV_ALARMACK | A_P1_SERV | West Bore 752 to Nest 4101 Communications Fault | BPL752_BPL4101CommsFlt_A | C_LOPRI | BPL752 | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL752
BR4_Tags | BPL752_BPL601CommsFlt_A | West Bore Transfer Pumps PLC | InterPLC BPL601 Communications Faulted | BPL752_BPL601CommsFlt_A | CAT_P3 | BPL752 | PRIV_ALARMACK | A_P1_SERV | InterPLC BPL601 Communications Faulted | BPL752_BPL601CommsFlt_A | C_LOPRI | BPL752 | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL752
BR4_Tags | BPL752_BPL752TelCommsFlt_A | West Bore Transfer Pumps PLC | West Bore 752 to Telemetry Communications Fault | BPL752_BPL752TelCommsFlt_A | CAT_P2 | BPL752 | PRIV_ALARMACK | A_P1_SERV | West Bore 752 to Telemetry Communications Fault | BPL752_BPL752TelCommsFlt_A | C_HIPRI | BPL752 | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL752
BR4_Tags | BPL752_BPL760CommsFlt_A | West Bore Transfer Pumps PLC | InterPLC BPL760 Communications Faulted | BPL752_BPL760CommsFlt_A | CAT_P3 | BPL752 | PRIV_ALARMACK | A_P1_SERV | InterPLC BPL760 Communications Faulted | BPL752_BPL760CommsFlt_A | C_LOPRI | BPL752 | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL752
BR4_Tags | BPL752_BPL761CommsFlt_A | West Borefield PLC | West Bore 752 to EBFT 761 Communications Fault | BPL752_BPL761CommsFlt_A | CAT_P3 | BPL752 | PRIV_ALARMACK | A_P1_SERV | West Bore 752 to EBFT 761 Communications Fault | BPL752_BPL761CommsFlt_A | C_LOPRI | BPL752 | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL752
BR4_Tags | BPL752_BPL801CommsFlt_A | West Bore Transfer Pumps PLC | InterPLC BPL801 Communications Faulted | BPL752_BPL801CommsFlt_A | CAT_P2 | BPL752 | PRIV_ALARMACK | A_P1_SERV | InterPLC BPL801 Communications Faulted | BPL752_BPL801CommsFlt_A | C_HIPRI | BPL752 | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL752
BR4_Tags | BPL752_CPUEthModLinkOK_A | West Bore Transfer Pumps PLC | CPU Module Ethernet Link Fault | BPL752_CPUEthModLinkOK_A | CAT_P2 | BPL752 | PRIV_ALARMACK | A_P1_SERV | CPU Module Ethernet Link Fault | BPL752_CPUEthModLinkOK_A | C_HIPRI | BPL752 | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL752
BR4_Tags | BPL752_CPUEthModRnng_A | West Bore Transfer Pumps PLC | CPU Module Ethernet Port Not Running Fault | BPL752_CPUEthModRnng_A | CAT_P2 | BPL752 | PRIV_ALARMACK | A_P1_SERV | CPU Module Ethernet Port Not Running Fault | BPL752_CPUEthModRnng_A | C_HIPRI | BPL752 | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL752
BR4_Tags | BPL752_D0R0S3OK_A | West Bore Transfer Pumps PLC | Rack 0 Slot 3 Module Fault | BPL752_D0R0S3OK_A | CAT_P3 | BPL752 | PRIV_ALARMACK | A_P1_SERV | Rack 0 Slot 3 Module Fault | BPL752_D0R0S3OK_A | C_LOPRI | BPL752 | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL752 | Slot3_A
BR4_Tags | BPL752_D0R0S4OK_A | West Bore Transfer Pumps PLC | Rack 0 Slot 4 Module Fault | BPL752_D0R0S4OK_A | CAT_P3 | BPL752 | PRIV_ALARMACK | A_P1_SERV | Rack 0 Slot 4 Module Fault | BPL752_D0R0S4OK_A | C_LOPRI | BPL752 | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL752 | Slot4_A
BR4_Tags | BPL752_D0R0S5OK_A | West Bore Transfer Pumps PLC | Rack 0 Slot 5 Module Fault | BPL752_D0R0S5OK_A | CAT_P3 | BPL752 | PRIV_ALARMACK | A_P1_SERV | Rack 0 Slot 5 Module Fault | BPL752_D0R0S5OK_A | C_LOPRI | BPL752 | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL752 | Slot5_A
BR4_Tags | BPL752_D0R0S6OK_A | West Bore Transfer Pumps PLC | Rack 0 Slot 6 Module Fault | BPL752_D0R0S6OK_A | CAT_P3 | BPL752 | PRIV_ALARMACK | A_P1_SERV | Rack 0 Slot 6 Module Fault | BPL752_D0R0S6OK_A | C_LOPRI | BPL752 | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL752 | Slot6_A
BR4_Tags | BPL752_D0R0S7OK_A | West Bore Transfer Pumps PLC | Rack 0 Slot 7 Module Fault | BPL752_D0R0S7OK_A | CAT_P3 | BPL752 | PRIV_ALARMACK | A_P1_SERV | Rack 0 Slot 7 Module Fault | BPL752_D0R0S7OK_A | C_LOPRI | BPL752 | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL752 | Slot7_A
BR4_Tags | BPL752_D0R0S8OK_A | West Bore Transfer Pumps PLC | Rack 0 Slot 8 Module Fault | BPL752_D0R0S8OK_A | CAT_P3 | BPL752 | PRIV_ALARMACK | A_P1_SERV | Rack 0 Slot 8 Module Fault | BPL752_D0R0S8OK_A | C_LOPRI | BPL752 | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL752 | Slot8_A
BR4_Tags | BPL752_DropAOK_A | PLC 752 Drop A - BTK702PN01 | Island NIP Module Or Island Fault | BPL752_DropAOK_A | CAT_P3 | BPL752 | PRIV_ALARMACK | A_P1_SERV | Island NIP Module Or Island Fault | BPL752_DropAOK_A | C_LOPRI | BPL752DropA | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL752
BR4_Tags | BPL752_NOE1LinkOK_A | West Bore Transfer Pumps PLC | NOE1 Ethernet Link Status Fault | BPL752_NOE1LinkOK_A | CAT_P2 | BPL752 | PRIV_ALARMACK | A_P1_SERV | NOE1 Ethernet Link Status Fault | BPL752_NOE1LinkOK_A | C_HIPRI | BPL752 | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL752
BR4_Tags | BPL752_NOE1Rnng_A | West Bore Transfer Pumps PLC | NOE1 Ethernet Module Not Running | BPL752_NOE1Rnng_A | CAT_P2 | BPL752 | PRIV_ALARMACK | A_P1_SERV | NOE1 Ethernet Module Not Running | BPL752_NOE1Rnng_A | C_HIPRI | BPL752 | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL752 | Slot1_A
BR4_Tags | BPL752_NOE2LinkOK_A | West Bore Transfer Pumps PLC | NOE2 Ethernet Link Status Fault | BPL752_NOE2LinkOK_A | CAT_P2 | BPL752 | PRIV_ALARMACK | A_P1_SERV | NOE2 Ethernet Link Status Fault | BPL752_NOE2LinkOK_A | C_HIPRI | BPL752 | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL752
BR4_Tags | BPL752_NOE2Rnng_A | West Bore Transfer Pumps PLC | NOE2 Ethernet Module Not Running | BPL752_NOE2Rnng_A | CAT_P2 | BPL752 | PRIV_ALARMACK | A_P1_SERV | NOE2 Ethernet Module Not Running | BPL752_NOE2Rnng_A | C_HIPRI | BPL752 | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL752 | Slot2_A
BR4_Tags | BPL752A03_AICh1OCE_E | PLC 752 Drop A - BTK702PN01 | Slot 3 Channel 1 Overcurrent Error | BPL752A03_AICh1OCE_E | CAT_P4 | BPL752 | PRIV_ALARMACK | A_P1_SERV | Slot 3 Channel 1 Overcurrent Error | BPL752A03_AICh1OCE_E | C_EVENT | BPL752DropA | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL752.DropA
BR4_Tags | BPL752A03_AICh1OK_A | PLC 752 Drop A - BTK702PN01 | Slot 3 Channel 1 General Fault | BPL752A03_AICh1OK_A | CAT_P3 | BPL752 | PRIV_ALARMACK | A_P1_SERV | Slot 3 Channel 1 General Fault | BPL752A03_AICh1OK_A | C_LOPRI | BPL752DropA | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL752.DropA
BR4_Tags | BPL752A03_AICh1UCE_E | PLC 752 Drop A - BTK702PN01 | Slot 3 Channel 1 Undercurrent Error | BPL752A03_AICh1UCE_E | CAT_P4 | BPL752 | PRIV_ALARMACK | A_P1_SERV | Slot 3 Channel 1 Undercurrent Error | BPL752A03_AICh1UCE_E | C_EVENT | BPL752DropA | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL752.DropA
BR4_Tags | BPL752A03_AICh2OCE_E | PLC 752 Drop A - BTK702PN01 | Slot 3 Channel 2 Overcurrent Error | BPL752A03_AICh2OCE_E | CAT_P4 | BPL752 | PRIV_ALARMACK | A_P1_SERV | Slot 3 Channel 2 Overcurrent Error | BPL752A03_AICh2OCE_E | C_EVENT | BPL752DropA | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL752.DropA
BR4_Tags | BPL752A03_AICh2OK_A | PLC 752 Drop A - BTK702PN01 | Slot 3 Channel 2 General Fault | BPL752A03_AICh2OK_A | CAT_P4 | BPL752 | PRIV_ALARMACK | A_P1_SERV | Slot 3 Channel 2 General Fault | BPL752A03_AICh2OK_A | C_EVENT | BPL752DropA | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL752.DropA
BR4_Tags | BPL752A03_AICh2UCE_E | PLC 752 Drop A - BTK702PN01 | Slot 3 Channel 2 Undercurrent Error | BPL752A03_AICh2UCE_E | CAT_P4 | BPL752 | PRIV_ALARMACK | A_P1_SERV | Slot 3 Channel 2 Undercurrent Error | BPL752A03_AICh2UCE_E | C_EVENT | BPL752DropA | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL752.DropA
BR4_Tags | BPL752A03_AICh3OCE_E | PLC 752 Drop A - BTK702PN01 | Slot 3 Channel 3 Overcurrent Error | BPL752A03_AICh3OCE_E | CAT_P4 | BPL752 | PRIV_ALARMACK | A_P1_SERV | Slot 3 Channel 3 Overcurrent Error | BPL752A03_AICh3OCE_E | C_EVENT | BPL752DropA | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL752.DropA
BR4_Tags | BPL752A03_AICh3UCE_E | PLC 752 Drop A - BTK702PN01 | Slot 3 Channel 3 Undercurrent Error | BPL752A03_AICh3UCE_E | CAT_P4 | BPL752 | PRIV_ALARMACK | A_P1_SERV | Slot 3 Channel 3 Undercurrent Error | BPL752A03_AICh3UCE_E | C_EVENT | BPL752DropA | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL752.DropA
BR4_Tags | BPL752A03_AICh4OCE_E | PLC 752 Drop A - BTK702PN01 | Slot 3 Channel 4 Overcurrent Error | BPL752A03_AICh4OCE_E | CAT_P4 | BPL752 | PRIV_ALARMACK | A_P1_SERV | Slot 3 Channel 4 Overcurrent Error | BPL752A03_AICh4OCE_E | C_EVENT | BPL752DropA | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL752.DropA
BR4_Tags | BPL752A03_AICh4UCE_E | PLC 752 Drop A - BTK702PN01 | Slot 3 Channel 4 Undercurrent Error | BPL752A03_AICh4UCE_E | CAT_P4 | BPL752 | PRIV_ALARMACK | A_P1_SERV | Slot 3 Channel 4 Undercurrent Error | BPL752A03_AICh4UCE_E | C_EVENT | BPL752DropA | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL752.DropA
BR4_Tags | BPL752A03_OK_A | PLC 752 Drop A - BTK702PN01 | Slot 03 Module Fault | BPL752A03_OK_A | CAT_P3 | BPL752 | PRIV_ALARMACK | A_P1_SERV | Slot 03 Module Fault | BPL752A03_OK_A | C_LOPRI | BPL752DropA | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL752.DropA | Slot3_A
BR4_Tags | BPL752WB12B1_BPL752WB12B1TelCommsFlt_A | West Dewatering Bore WB12BS4B001 PLC | BPL752WB12B1 Telemetry Comms Fault Alarm | BPL752WB12B1_BPL752WB12B1TelCommsFlt_A | CAT_P3 | WBBWD-1750B004 | PRIV_ALARMACK | A_P1_SERV | BPL752WB12B1 Telemetry Comms Fault Alarm | BPL752WB12B1_BPL752WB12B1TelCommsFlt_A | C_LOPRI | BPL752WB12B1 | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL752WB12B1
BR4_Tags | BPL752WB12B1_CPUEthModLinkOK_A | West Dewatering Bore WB12BS4B001 PLC | CPU Ethernet Module Link Alarm | BPL752WB12B1_CPUEthModLinkOK_A | CAT_P2 | WBBWD-1750B004 | PRIV_ALARMACK | A_P1_SERV | CPU Ethernet Module Link Alarm | BPL752WB12B1_CPUEthModLinkOK_A | C_HIPRI | BPL752WB12B1 | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL752WB12B1
BR4_Tags | BPL752WB12B1_CPUEthModRnng_A | West Dewatering Bore WB12BS4B001 PLC | CPU Ethernet Module NOT Running Alarm | BPL752WB12B1_CPUEthModRnng_A | CAT_P2 | WBBWD-1750B004 | PRIV_ALARMACK | A_P1_SERV | CPU Ethernet Module NOT Running Alarm | BPL752WB12B1_CPUEthModRnng_A | C_HIPRI | BPL752WB12B1 | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL752WB12B1
BR4_Tags | BPL752WB12B1_Mod1OK_A | West Dewatering Bore WB12BS4B001 PLC | DDI Module 1 Alarm | BPL752WB12B1_Mod1OK_A | CAT_P3 | WBBWD-1750B004 | PRIV_ALARMACK | A_P1_SERV | DDI Module 1 Alarm | BPL752WB12B1_Mod1OK_A | C_LOPRI | BPL752WB12B1 | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL752WB12B1 | Slot1_A
BR4_Tags | BPL752WB12B1_Mod2OK_A | West Dewatering Bore WB12BS4B001 PLC | DDI Module 2 Alarm | BPL752WB12B1_Mod2OK_A | CAT_P3 | WBBWD-1750B004 | PRIV_ALARMACK | A_P1_SERV | DDI Module 2 Alarm | BPL752WB12B1_Mod2OK_A | C_LOPRI | BPL752WB12B1 | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL752WB12B1 | Slot2_A
BR4_Tags | BPL752WB12B1_Mod3OK_A | West Dewatering Bore WB12BS4B001 PLC | DDI Module 3 Alarm | BPL752WB12B1_Mod3OK_A | CAT_P3 | WBBWD-1750B004 | PRIV_ALARMACK | A_P1_SERV | DDI Module 3 Alarm | BPL752WB12B1_Mod3OK_A | C_LOPRI | BPL752WB12B1 | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL752WB12B1 | Slot3_A
BR4_Tags | BPL752WB12B1_Mod4OK_A | West Dewatering Bore WB12BS4B001 PLC | DRA Module 4 Alarm | BPL752WB12B1_Mod4OK_A | CAT_P3 | WBBWD-1750B004 | PRIV_ALARMACK | A_P1_SERV | DRA Module 4 Alarm | BPL752WB12B1_Mod4OK_A | C_LOPRI | BPL752WB12B1 | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL752WB12B1 | Slot4_A
BR4_Tags | BPL752WB12B1_Mod5OK_A | West Dewatering Bore WB12BS4B001 PLC | DRA Module 5 Alarm | BPL752WB12B1_Mod5OK_A | CAT_P3 | WBBWD-1750B004 | PRIV_ALARMACK | A_P1_SERV | DRA Module 5 Alarm | BPL752WB12B1_Mod5OK_A | C_LOPRI | BPL752WB12B1 | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL752WB12B1 | Slot5_A
BR4_Tags | BPL752WB12B1_Mod6OK_A | West Dewatering Bore WB12BS4B001 PLC | AMI Module 6 Alarm | BPL752WB12B1_Mod6OK_A | CAT_P3 | WBBWD-1750B004 | PRIV_ALARMACK | A_P1_SERV | AMI Module 6 Alarm | BPL752WB12B1_Mod6OK_A | C_LOPRI | BPL752WB12B1 | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL752WB12B1 | Slot6_A
BR4_Tags | BPL752WB12B1_NOE1LinkOK_A | West Dewatering Bore WB12BS4B001 PLC | NOE1 Slot Link Alarm | BPL752WB12B1_NOE1LinkOK_A | CAT_P2 | WBBWD-1750B004 | PRIV_ALARMACK | A_P1_SERV | NOE1 Slot Link Alarm | BPL752WB12B1_NOE1LinkOK_A | C_HIPRI | BPL752WB12B1 | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL752WB12B1
BR4_Tags | BPL752WB12B1_NOE1Rnng_A | West Dewatering Bore WB12BS4B001 PLC | NOE1 Slot NOT Running Alarm | BPL752WB12B1_NOE1Rnng_A | CAT_P2 | WBBWD-1750B004 | PRIV_ALARMACK | A_P1_SERV | NOE1 Slot NOT Running Alarm | BPL752WB12B1_NOE1Rnng_A | C_HIPRI | BPL752WB12B1 | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL752WB12B1 | Slot7_A
BR4_Tags | BPL752WB12B1_NOE2LinkOK_A | West Dewatering Bore WB12BS4B001 PLC | NOE2 Slot Link Alarm | BPL752WB12B1_NOE2LinkOK_A | CAT_P2 | WBBWD-1750B004 | PRIV_ALARMACK | A_P1_SERV | NOE2 Slot Link Alarm | BPL752WB12B1_NOE2LinkOK_A | C_HIPRI | BPL752WB12B1 | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL752WB12B1
BR4_Tags | BPL752WB12B1_NOE2Rnng_A | West Dewatering Bore WB12BS4B001 PLC | NOE2 Slot NOT Running Alarm | BPL752WB12B1_NOE2Rnng_A | CAT_P2 | WBBWD-1750B004 | PRIV_ALARMACK | A_P1_SERV | NOE2 Slot NOT Running Alarm | BPL752WB12B1_NOE2Rnng_A | C_HIPRI | BPL752WB12B1 | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL752WB12B1 | Slot8_A
BR4_Tags | BPL752WB12B1RTU_DCV_A | West Dewatering Bore WB12BS4B001 PLC | RTU DCV Low Alarm | BPL752WB12B1RTU_DCV_A | CAT_P3 | WBBWD-1750B004 | PRIV_ALARMACK | A_P1_SERV | RTU DCV Low Alarm | BPL752WB12B1RTU_DCV_A | C_LOPRI | BPL752WB12B1 | Class_Process | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL752WB12B1.DCV
BR4_Tags | BPL752WB12B1Tel_BPL752WB12B1Comms_A | West Dewatering Bore WB12BS4B001 PLC | Telemetry to BPL752WB12B1 Comms Alarm | BPL752WB12B1Tel_BPL752WB12B1Comms_A | CAT_P2 | WBBWD-1750B004 | PRIV_ALARMACK | A_P1_SERV | Telemetry to BPL752WB12B1 Comms Alarm | BPL752WB12B1Tel_BPL752WB12B1Comms_A | C_HIPRI | BPL752WB12B1 | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL752WB12B1
BR4_Tags | BPL752WB12B2_BPL752WB12B2TelCommsFlt_A | West Dewatering Bore WB12BS4B002 PLC | BPL752WB12B2 Telemetry Comms Fault Alarm | BPL752WB12B2_BPL752WB12B2TelCommsFlt_A | CAT_P3 | WBBWD-1750B004 | PRIV_ALARMACK | A_P1_SERV | BPL752WB12B2 Telemetry Comms Fault Alarm | BPL752WB12B2_BPL752WB12B2TelCommsFlt_A | C_LOPRI | BPL752WB12B2 | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL752WB12B2
BR4_Tags | BPL752WB12B2_CPUEthModLinkOK_A | West Dewatering Bore WB12BS4B002 PLC | CPU Ethernet Module Link Alarm | BPL752WB12B2_CPUEthModLinkOK_A | CAT_P2 | WBBWD-1750B004 | PRIV_ALARMACK | A_P1_SERV | CPU Ethernet Module Link Alarm | BPL752WB12B2_CPUEthModLinkOK_A | C_HIPRI | BPL752WB12B2 | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL752WB12B2
BR4_Tags | BPL752WB12B2_CPUEthModRnng_A | West Dewatering Bore WB12BS4B002 PLC | CPU Ethernet Module NOT Running Alarm | BPL752WB12B2_CPUEthModRnng_A | CAT_P2 | WBBWD-1750B004 | PRIV_ALARMACK | A_P1_SERV | CPU Ethernet Module NOT Running Alarm | BPL752WB12B2_CPUEthModRnng_A | C_HIPRI | BPL752WB12B2 | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL752WB12B2
BR4_Tags | BPL752WB12B2_Mod1OK_A | West Dewatering Bore WB12BS4B002 PLC | DDI Module 1 Alarm | BPL752WB12B2_Mod1OK_A | CAT_P3 | WBBWD-1750B004 | PRIV_ALARMACK | A_P1_SERV | DDI Module 1 Alarm | BPL752WB12B2_Mod1OK_A | C_LOPRI | BPL752WB12B2 | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL752WB12B2 | Slot1_A
BR4_Tags | BPL752WB12B2_Mod2OK_A | West Dewatering Bore WB12BS4B002 PLC | DDI Module 2 Alarm | BPL752WB12B2_Mod2OK_A | CAT_P3 | WBBWD-1750B004 | PRIV_ALARMACK | A_P1_SERV | DDI Module 2 Alarm | BPL752WB12B2_Mod2OK_A | C_LOPRI | BPL752WB12B2 | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL752WB12B2 | Slot2_A
BR4_Tags | BPL752WB12B2_Mod3OK_A | West Dewatering Bore WB12BS4B002 PLC | DDI Module 3 Alarm | BPL752WB12B2_Mod3OK_A | CAT_P3 | WBBWD-1750B004 | PRIV_ALARMACK | A_P1_SERV | DDI Module 3 Alarm | BPL752WB12B2_Mod3OK_A | C_LOPRI | BPL752WB12B2 | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL752WB12B2 | Slot3_A
BR4_Tags | BPL752WB12B2_Mod4OK_A | West Dewatering Bore WB12BS4B002 PLC | DRA Module 4 Alarm | BPL752WB12B2_Mod4OK_A | CAT_P3 | WBBWD-1750B004 | PRIV_ALARMACK | A_P1_SERV | DRA Module 4 Alarm | BPL752WB12B2_Mod4OK_A | C_LOPRI | BPL752WB12B2 | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL752WB12B2 | Slot4_A
BR4_Tags | BPL752WB12B2_Mod5OK_A | West Dewatering Bore WB12BS4B002 PLC | DRA Module 5 Alarm | BPL752WB12B2_Mod5OK_A | CAT_P3 | WBBWD-1750B004 | PRIV_ALARMACK | A_P1_SERV | DRA Module 5 Alarm | BPL752WB12B2_Mod5OK_A | C_LOPRI | BPL752WB12B2 | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL752WB12B2 | Slot5_A
BR4_Tags | BPL752WB12B2_Mod6OK_A | West Dewatering Bore WB12BS4B002 PLC | AMI Module 6 Alarm | BPL752WB12B2_Mod6OK_A | CAT_P3 | WBBWD-1750B004 | PRIV_ALARMACK | A_P1_SERV | AMI Module 6 Alarm | BPL752WB12B2_Mod6OK_A | C_LOPRI | BPL752WB12B2 | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL752WB12B2 | Slot6_A
BR4_Tags | BPL752WB12B2_NOE1LinkOK_A | West Dewatering Bore WB12BS4B002 PLC | NOE1 Slot Link Alarm | BPL752WB12B2_NOE1LinkOK_A | CAT_P2 | WBBWD-1750B004 | PRIV_ALARMACK | A_P1_SERV | NOE1 Slot Link Alarm | BPL752WB12B2_NOE1LinkOK_A | C_HIPRI | BPL752WB12B2 | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL752WB12B2
BR4_Tags | BPL752WB12B2_NOE1Rnng_A | West Dewatering Bore WB12BS4B002 PLC | NOE1 Slot NOT Running Alarm | BPL752WB12B2_NOE1Rnng_A | CAT_P2 | WBBWD-1750B004 | PRIV_ALARMACK | A_P1_SERV | NOE1 Slot NOT Running Alarm | BPL752WB12B2_NOE1Rnng_A | C_HIPRI | BPL752WB12B2 | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL752WB12B2 | Slot7_A
BR4_Tags | BPL752WB12B2_NOE2LinkOK_A | West Dewatering Bore WB12BS4B002 PLC | NOE2 Slot Link Alarm | BPL752WB12B2_NOE2LinkOK_A | CAT_P2 | WBBWD-1750B004 | PRIV_ALARMACK | A_P1_SERV | NOE2 Slot Link Alarm | BPL752WB12B2_NOE2LinkOK_A | C_HIPRI | BPL752WB12B2 | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL752WB12B2
BR4_Tags | BPL752WB12B2_NOE2Rnng_A | West Dewatering Bore WB12BS4B002 PLC | NOE2 Slot NOT Running Alarm | BPL752WB12B2_NOE2Rnng_A | CAT_P2 | WBBWD-1750B004 | PRIV_ALARMACK | A_P1_SERV | NOE2 Slot NOT Running Alarm | BPL752WB12B2_NOE2Rnng_A | C_HIPRI | BPL752WB12B2 | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL752WB12B2 | Slot8_A
BR4_Tags | BPL752WB12B2RTU_DCV_A | West Dewatering Bore WB12BS4B002 PLC | RTU DCV Low Alarm | BPL752WB12B2RTU_DCV_A | CAT_P3 | WBBWD-1750B004 | PRIV_ALARMACK | A_P1_SERV | RTU DCV Low Alarm | BPL752WB12B2RTU_DCV_A | C_LOPRI | BPL752WB12B2 | Class_Process | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL752WB12B2.DCV
BR4_Tags | BPL752WB12B2Tel_BPL752WB12B2Comms_A | West Dewatering Bore WB12BS4B002 PLC | Telemetry to BPL752WB12B2 Comms Alarm | BPL752WB12B2Tel_BPL752WB12B2Comms_A | CAT_P2 | WBBWD-1750B004 | PRIV_ALARMACK | A_P1_SERV | Telemetry to BPL752WB12B2 Comms Alarm | BPL752WB12B2Tel_BPL752WB12B2Comms_A | C_HIPRI | BPL752WB12B2 | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL752WB12B2
BR4_Tags | BPL752WB12B4_BPL752WB12B4TelCommsFlt_A | West Dewatering Bore WB12BS4B004 PLC | BPL752WB12B4 Telemetry Comms Fault Alarm | BPL752WB12B4_BPL752WB12B4TelCommsFlt_A | CAT_P3 | WBBWD-1750B004 | PRIV_ALARMACK | A_P1_SERV | BPL752WB12B4 Telemetry Comms Fault Alarm | BPL752WB12B4_BPL752WB12B4TelCommsFlt_A | C_LOPRI | BPL752WB12B4 | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL752WB12B4
BR4_Tags | BPL752WB12B4_CPUEthModLinkOK_A | West Dewatering Bore WB12BS4B004 PLC | CPU Ethernet Module Link Alarm | BPL752WB12B4_CPUEthModLinkOK_A | CAT_P2 | WBBWD-1750B004 | PRIV_ALARMACK | A_P1_SERV | CPU Ethernet Module Link Alarm | BPL752WB12B4_CPUEthModLinkOK_A | C_HIPRI | BPL752WB12B4 | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL752WB12B4
BR4_Tags | BPL752WB12B4_CPUEthModRnng_A | West Dewatering Bore WB12BS4B004 PLC | CPU Ethernet Module NOT Running Alarm | BPL752WB12B4_CPUEthModRnng_A | CAT_P2 | WBBWD-1750B004 | PRIV_ALARMACK | A_P1_SERV | CPU Ethernet Module NOT Running Alarm | BPL752WB12B4_CPUEthModRnng_A | C_HIPRI | BPL752WB12B4 | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL752WB12B4
BR4_Tags | BPL752WB12B4_Mod1OK_A | West Dewatering Bore WB12BS4B004 PLC | DDI Module 1 Alarm | BPL752WB12B4_Mod1OK_A | CAT_P3 | WBBWD-1750B004 | PRIV_ALARMACK | A_P1_SERV | DDI Module 1 Alarm | BPL752WB12B4_Mod1OK_A | C_LOPRI | BPL752WB12B4 | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL752WB12B4 | Slot1_A
BR4_Tags | BPL752WB12B4_Mod2OK_A | West Dewatering Bore WB12BS4B004 PLC | DDI Module 2 Alarm | BPL752WB12B4_Mod2OK_A | CAT_P3 | WBBWD-1750B004 | PRIV_ALARMACK | A_P1_SERV | DDI Module 2 Alarm | BPL752WB12B4_Mod2OK_A | C_LOPRI | BPL752WB12B4 | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL752WB12B4 | Slot2_A
BR4_Tags | BPL752WB12B4_Mod3OK_A | West Dewatering Bore WB12BS4B004 PLC | DDI Module 3 Alarm | BPL752WB12B4_Mod3OK_A | CAT_P3 | WBBWD-1750B004 | PRIV_ALARMACK | A_P1_SERV | DDI Module 3 Alarm | BPL752WB12B4_Mod3OK_A | C_LOPRI | BPL752WB12B4 | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL752WB12B4 | Slot3_A
BR4_Tags | BPL752WB12B4_Mod4OK_A | West Dewatering Bore WB12BS4B004 PLC | DRA Module 4 Alarm | BPL752WB12B4_Mod4OK_A | CAT_P3 | WBBWD-1750B004 | PRIV_ALARMACK | A_P1_SERV | DRA Module 4 Alarm | BPL752WB12B4_Mod4OK_A | C_LOPRI | BPL752WB12B4 | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL752WB12B4 | Slot4_A
BR4_Tags | BPL752WB12B4_Mod5OK_A | West Dewatering Bore WB12BS4B004 PLC | DRA Module 5 Alarm | BPL752WB12B4_Mod5OK_A | CAT_P3 | WBBWD-1750B004 | PRIV_ALARMACK | A_P1_SERV | DRA Module 5 Alarm | BPL752WB12B4_Mod5OK_A | C_LOPRI | BPL752WB12B4 | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL752WB12B4 | Slot5_A
BR4_Tags | BPL752WB12B4_Mod6OK_A | West Dewatering Bore WB12BS4B004 PLC | AMI Module 6 Alarm | BPL752WB12B4_Mod6OK_A | CAT_P3 | WBBWD-1750B004 | PRIV_ALARMACK | A_P1_SERV | AMI Module 6 Alarm | BPL752WB12B4_Mod6OK_A | C_LOPRI | BPL752WB12B4 | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL752WB12B4 | Slot6_A
BR4_Tags | BPL752WB12B4_NOE1LinkOK_A | West Dewatering Bore WB12BS4B004 PLC | NOE1 Slot Link Alarm | BPL752WB12B4_NOE1LinkOK_A | CAT_P2 | WBBWD-1750B004 | PRIV_ALARMACK | A_P1_SERV | NOE1 Slot Link Alarm | BPL752WB12B4_NOE1LinkOK_A | C_HIPRI | BPL752WB12B4 | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL752WB12B4
BR4_Tags | BPL752WB12B4_NOE1Rnng_A | West Dewatering Bore WB12BS4B004 PLC | NOE1 Slot NOT Running Alarm | BPL752WB12B4_NOE1Rnng_A | CAT_P2 | WBBWD-1750B004 | PRIV_ALARMACK | A_P1_SERV | NOE1 Slot NOT Running Alarm | BPL752WB12B4_NOE1Rnng_A | C_HIPRI | BPL752WB12B4 | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL752WB12B4 | Slot7_A
BR4_Tags | BPL752WB12B4_NOE2LinkOK_A | West Dewatering Bore WB12BS4B004 PLC | NOE2 Slot Link Alarm | BPL752WB12B4_NOE2LinkOK_A | CAT_P2 | WBBWD-1750B004 | PRIV_ALARMACK | A_P1_SERV | NOE2 Slot Link Alarm | BPL752WB12B4_NOE2LinkOK_A | C_HIPRI | BPL752WB12B4 | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL752WB12B4
BR4_Tags | BPL752WB12B4_NOE2Rnng_A | West Dewatering Bore WB12BS4B004 PLC | NOE2 Slot NOT Running Alarm | BPL752WB12B4_NOE2Rnng_A | CAT_P2 | WBBWD-1750B004 | PRIV_ALARMACK | A_P1_SERV | NOE2 Slot NOT Running Alarm | BPL752WB12B4_NOE2Rnng_A | C_HIPRI | BPL752WB12B4 | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL752WB12B4 | Slot8_A
BR4_Tags | BPL752WB12B4RTU_DCV_A | West Dewatering Bore WB12BS4B004 PLC | RTU DCV Low Alarm | BPL752WB12B4RTU_DCV_A | CAT_P3 | WBBWD-1750B004 | PRIV_ALARMACK | A_P1_SERV | RTU DCV Low Alarm | BPL752WB12B4RTU_DCV_A | C_LOPRI | BPL752WB12B4 | Class_Process | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL752WB12B4.DCV
BR4_Tags | BPL752WB12B4Tel_BPL752WB12B4Comms_A | West Dewatering Bore WB12BS4B004 PLC | Telemetry to BPL752WB12B4 Comms Alarm | BPL752WB12B4Tel_BPL752WB12B4Comms_A | CAT_P2 | WBBWD-1750B004 | PRIV_ALARMACK | A_P1_SERV | Telemetry to BPL752WB12B4 Comms Alarm | BPL752WB12B4Tel_BPL752WB12B4Comms_A | C_HIPRI | BPL752WB12B4 | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL752WB12B4
BR4_Tags | BPL752WB12B5_BPL752WB12B5TelCommsFlt_A | West Dewatering Bore WB12BS4B005 PLC | BPL752WB12B5 Telemetry Comms Fault Alarm | BPL752WB12B5_BPL752WB12B5TelCommsFlt_A | CAT_P3 | WBBWD-1750B004 | PRIV_ALARMACK | A_P1_SERV | BPL752WB12B5 Telemetry Comms Fault Alarm | BPL752WB12B5_BPL752WB12B5TelCommsFlt_A | C_LOPRI | BPL752WB12B5 | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL752WB12B5
BR4_Tags | BPL752WB12B5_CPUEthModLinkOK_A | West Dewatering Bore WB12BS4B005 PLC | CPU Ethernet Module Link Alarm | BPL752WB12B5_CPUEthModLinkOK_A | CAT_P2 | WBBWD-1750B004 | PRIV_ALARMACK | A_P1_SERV | CPU Ethernet Module Link Alarm | BPL752WB12B5_CPUEthModLinkOK_A | C_HIPRI | BPL752WB12B5 | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL752WB12B5
BR4_Tags | BPL752WB12B5_CPUEthModRnng_A | West Dewatering Bore WB12BS4B005 PLC | CPU Ethernet Module NOT Running Alarm | BPL752WB12B5_CPUEthModRnng_A | CAT_P2 | WBBWD-1750B004 | PRIV_ALARMACK | A_P1_SERV | CPU Ethernet Module NOT Running Alarm | BPL752WB12B5_CPUEthModRnng_A | C_HIPRI | BPL752WB12B5 | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL752WB12B5
BR4_Tags | BPL752WB12B5_Mod1OK_A | West Dewatering Bore WB12BS4B005 PLC | DDI Module 1 Alarm | BPL752WB12B5_Mod1OK_A | CAT_P3 | WBBWD-1750B004 | PRIV_ALARMACK | A_P1_SERV | DDI Module 1 Alarm | BPL752WB12B5_Mod1OK_A | C_LOPRI | BPL752WB12B5 | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL752WB12B5 | Slot1_A
BR4_Tags | BPL752WB12B5_Mod2OK_A | West Dewatering Bore WB12BS4B005 PLC | DDI Module 2 Alarm | BPL752WB12B5_Mod2OK_A | CAT_P3 | WBBWD-1750B004 | PRIV_ALARMACK | A_P1_SERV | DDI Module 2 Alarm | BPL752WB12B5_Mod2OK_A | C_LOPRI | BPL752WB12B5 | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL752WB12B5 | Slot2_A
BR4_Tags | BPL752WB12B5_Mod3OK_A | West Dewatering Bore WB12BS4B005 PLC | DDI Module 3 Alarm | BPL752WB12B5_Mod3OK_A | CAT_P3 | WBBWD-1750B004 | PRIV_ALARMACK | A_P1_SERV | DDI Module 3 Alarm | BPL752WB12B5_Mod3OK_A | C_LOPRI | BPL752WB12B5 | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL752WB12B5 | Slot3_A
BR4_Tags | BPL752WB12B5_Mod4OK_A | West Dewatering Bore WB12BS4B005 PLC | DRA Module 4 Alarm | BPL752WB12B5_Mod4OK_A | CAT_P3 | WBBWD-1750B004 | PRIV_ALARMACK | A_P1_SERV | DRA Module 4 Alarm | BPL752WB12B5_Mod4OK_A | C_LOPRI | BPL752WB12B5 | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL752WB12B5 | Slot4_A
BR4_Tags | BPL752WB12B5_Mod5OK_A | West Dewatering Bore WB12BS4B005 PLC | DRA Module 5 Alarm | BPL752WB12B5_Mod5OK_A | CAT_P3 | WBBWD-1750B004 | PRIV_ALARMACK | A_P1_SERV | DRA Module 5 Alarm | BPL752WB12B5_Mod5OK_A | C_LOPRI | BPL752WB12B5 | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL752WB12B5 | Slot5_A
BR4_Tags | BPL752WB12B5_Mod6OK_A | West Dewatering Bore WB12BS4B005 PLC | AMI Module 6 Alarm | BPL752WB12B5_Mod6OK_A | CAT_P3 | WBBWD-1750B004 | PRIV_ALARMACK | A_P1_SERV | AMI Module 6 Alarm | BPL752WB12B5_Mod6OK_A | C_LOPRI | BPL752WB12B5 | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL752WB12B5 | Slot6_A
BR4_Tags | BPL752WB12B5_NOE1LinkOK_A | West Dewatering Bore WB12BS4B005 PLC | NOE1 Slot Link Alarm | BPL752WB12B5_NOE1LinkOK_A | CAT_P2 | WBBWD-1750B004 | PRIV_ALARMACK | A_P1_SERV | NOE1 Slot Link Alarm | BPL752WB12B5_NOE1LinkOK_A | C_HIPRI | BPL752WB12B5 | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL752WB12B5
BR4_Tags | BPL752WB12B5_NOE1Rnng_A | West Dewatering Bore WB12BS4B005 PLC | NOE1 Slot NOT Running Alarm | BPL752WB12B5_NOE1Rnng_A | CAT_P2 | WBBWD-1750B004 | PRIV_ALARMACK | A_P1_SERV | NOE1 Slot NOT Running Alarm | BPL752WB12B5_NOE1Rnng_A | C_HIPRI | BPL752WB12B5 | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL752WB12B5 | Slot7_A
BR4_Tags | BPL752WB12B5_NOE2LinkOK_A | West Dewatering Bore WB12BS4B005 PLC | NOE2 Slot Link Alarm | BPL752WB12B5_NOE2LinkOK_A | CAT_P2 | WBBWD-1750B004 | PRIV_ALARMACK | A_P1_SERV | NOE2 Slot Link Alarm | BPL752WB12B5_NOE2LinkOK_A | C_HIPRI | BPL752WB12B5 | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL752WB12B5
BR4_Tags | BPL752WB12B5_NOE2Rnng_A | West Dewatering Bore WB12BS4B005 PLC | NOE2 Slot NOT Running Alarm | BPL752WB12B5_NOE2Rnng_A | CAT_P2 | WBBWD-1750B004 | PRIV_ALARMACK | A_P1_SERV | NOE2 Slot NOT Running Alarm | BPL752WB12B5_NOE2Rnng_A | C_HIPRI | BPL752WB12B5 | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL752WB12B5 | Slot8_A
BR4_Tags | BPL752WB12B5RTU_DCV_A | West Dewatering Bore WB12BS4B005 PLC | RTU DCV Low Alarm | BPL752WB12B5RTU_DCV_A | CAT_P3 | WBBWD-1750B004 | PRIV_ALARMACK | A_P1_SERV | RTU DCV Low Alarm | BPL752WB12B5RTU_DCV_A | C_LOPRI | BPL752WB12B5 | Class_Process | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL752WB12B5.DCV
BR4_Tags | BPL752WB12B5Tel_BPL752WB12B5Comms_A | West Dewatering Bore WB12BS4B005 PLC | Telemetry to BPL752WB12B5 Comms Alarm | BPL752WB12B5Tel_BPL752WB12B5Comms_A | CAT_P2 | WBBWD-1750B004 | PRIV_ALARMACK | A_P1_SERV | Telemetry to BPL752WB12B5 Comms Alarm | BPL752WB12B5Tel_BPL752WB12B5Comms_A | C_HIPRI | BPL752WB12B5 | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL752WB12B5
BR4_Tags | BPL752WB13B1_BPL752WB13B1TelCommsFlt_A | West Dewatering Bore WB13BS4B001 PLC | BPL752WB13B1 Telemetry Comms Fault Alarm | BPL752WB13B1_BPL752WB13B1TelCommsFlt_A | CAT_P3 | WBBWD-1750B004 | PRIV_ALARMACK | A_P1_SERV | BPL752WB13B1 Telemetry Comms Fault Alarm | BPL752WB13B1_BPL752WB13B1TelCommsFlt_A | C_LOPRI | BPL752WB13B1 | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL752WB13B1
BR4_Tags | BPL752WB13B1_CPUEthModLinkOK_A | West Dewatering Bore WB13BS4B001 PLC | CPU Ethernet Module Link Alarm | BPL752WB13B1_CPUEthModLinkOK_A | CAT_P2 | WBBWD-1750B004 | PRIV_ALARMACK | A_P1_SERV | CPU Ethernet Module Link Alarm | BPL752WB13B1_CPUEthModLinkOK_A | C_HIPRI | BPL752WB13B1 | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL752WB13B1
BR4_Tags | BPL752WB13B1_CPUEthModRnng_A | West Dewatering Bore WB13BS4B001 PLC | CPU Ethernet Module NOT Running Alarm | BPL752WB13B1_CPUEthModRnng_A | CAT_P2 | WBBWD-1750B004 | PRIV_ALARMACK | A_P1_SERV | CPU Ethernet Module NOT Running Alarm | BPL752WB13B1_CPUEthModRnng_A | C_HIPRI | BPL752WB13B1 | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL752WB13B1
BR4_Tags | BPL752WB13B1_Mod1OK_A | West Dewatering Bore WB13BS4B001 PLC | DDI Module 1 Alarm | BPL752WB13B1_Mod1OK_A | CAT_P3 | WBBWD-1750B004 | PRIV_ALARMACK | A_P1_SERV | DDI Module 1 Alarm | BPL752WB13B1_Mod1OK_A | C_LOPRI | BPL752WB13B1 | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL752WB13B1 | Slot1_A
BR4_Tags | BPL752WB13B1_Mod2OK_A | West Dewatering Bore WB13BS4B001 PLC | DDI Module 2 Alarm | BPL752WB13B1_Mod2OK_A | CAT_P3 | WBBWD-1750B004 | PRIV_ALARMACK | A_P1_SERV | DDI Module 2 Alarm | BPL752WB13B1_Mod2OK_A | C_LOPRI | BPL752WB13B1 | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL752WB13B1 | Slot2_A
BR4_Tags | BPL752WB13B1_Mod3OK_A | West Dewatering Bore WB13BS4B001 PLC | DDI Module 3 Alarm | BPL752WB13B1_Mod3OK_A | CAT_P3 | WBBWD-1750B004 | PRIV_ALARMACK | A_P1_SERV | DDI Module 3 Alarm | BPL752WB13B1_Mod3OK_A | C_LOPRI | BPL752WB13B1 | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL752WB13B1 | Slot3_A
BR4_Tags | BPL752WB13B1_Mod4OK_A | West Dewatering Bore WB13BS4B001 PLC | DRA Module 4 Alarm | BPL752WB13B1_Mod4OK_A | CAT_P3 | WBBWD-1750B004 | PRIV_ALARMACK | A_P1_SERV | DRA Module 4 Alarm | BPL752WB13B1_Mod4OK_A | C_LOPRI | BPL752WB13B1 | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL752WB13B1 | Slot4_A
BR4_Tags | BPL752WB13B1_Mod5OK_A | West Dewatering Bore WB13BS4B001 PLC | DRA Module 5 Alarm | BPL752WB13B1_Mod5OK_A | CAT_P3 | WBBWD-1750B004 | PRIV_ALARMACK | A_P1_SERV | DRA Module 5 Alarm | BPL752WB13B1_Mod5OK_A | C_LOPRI | BPL752WB13B1 | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL752WB13B1 | Slot5_A
BR4_Tags | BPL752WB13B1_Mod6OK_A | West Dewatering Bore WB13BS4B001 PLC | AMI Module 6 Alarm | BPL752WB13B1_Mod6OK_A | CAT_P3 | WBBWD-1750B004 | PRIV_ALARMACK | A_P1_SERV | AMI Module 6 Alarm | BPL752WB13B1_Mod6OK_A | C_LOPRI | BPL752WB13B1 | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL752WB13B1 | Slot6_A
BR4_Tags | BPL752WB13B1_NOE1LinkOK_A | West Dewatering Bore WB13BS4B001 PLC | NOE1 Slot Link Alarm | BPL752WB13B1_NOE1LinkOK_A | CAT_P2 | WBBWD-1750B004 | PRIV_ALARMACK | A_P1_SERV | NOE1 Slot Link Alarm | BPL752WB13B1_NOE1LinkOK_A | C_HIPRI | BPL752WB13B1 | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL752WB13B1
BR4_Tags | BPL752WB13B1_NOE1Rnng_A | West Dewatering Bore WB13BS4B001 PLC | NOE1 Slot NOT Running Alarm | BPL752WB13B1_NOE1Rnng_A | CAT_P2 | WBBWD-1750B004 | PRIV_ALARMACK | A_P1_SERV | NOE1 Slot NOT Running Alarm | BPL752WB13B1_NOE1Rnng_A | C_HIPRI | BPL752WB13B1 | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL752WB13B1 | Slot7_A
BR4_Tags | BPL752WB13B1_NOE2LinkOK_A | West Dewatering Bore WB13BS4B001 PLC | NOE2 Slot Link Alarm | BPL752WB13B1_NOE2LinkOK_A | CAT_P2 | WBBWD-1750B004 | PRIV_ALARMACK | A_P1_SERV | NOE2 Slot Link Alarm | BPL752WB13B1_NOE2LinkOK_A | C_HIPRI | BPL752WB13B1 | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL752WB13B1
BR4_Tags | BPL752WB13B1_NOE2Rnng_A | West Dewatering Bore WB13BS4B001 PLC | NOE2 Slot NOT Running Alarm | BPL752WB13B1_NOE2Rnng_A | CAT_P2 | WBBWD-1750B004 | PRIV_ALARMACK | A_P1_SERV | NOE2 Slot NOT Running Alarm | BPL752WB13B1_NOE2Rnng_A | C_HIPRI | BPL752WB13B1 | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL752WB13B1 | Slot8_A
BR4_Tags | BPL752WB13B1RTU_DCV_A | West Dewatering Bore WB13BS4B001 PLC | RTU DCV Low Alarm | BPL752WB13B1RTU_DCV_A | CAT_P3 | WBBWD-1750B004 | PRIV_ALARMACK | A_P1_SERV | RTU DCV Low Alarm | BPL752WB13B1RTU_DCV_A | C_LOPRI | BPL752WB13B1 | Class_Process | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL752WB13B1.DCV
BR4_Tags | BPL752WB13B1Tel_BPL752WB13B1Comms_A | West Dewatering Bore WB13BS4B001 PLC | Telemetry to BPL752WB13B1 Comms Alarm | BPL752WB13B1Tel_BPL752WB13B1Comms_A | CAT_P2 | WBBWD-1750B004 | PRIV_ALARMACK | A_P1_SERV | Telemetry to BPL752WB13B1 Comms Alarm | BPL752WB13B1Tel_BPL752WB13B1Comms_A | C_HIPRI | BPL752WB13B1 | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL752WB13B1
BR4_Tags | BPL752WB13B3_BPL752WB13B3TelCommsFlt_A | West Dewatering Bore WB13BS4B003 PLC | BPL752WB13B3 Telemetry Comms Fault Alarm | BPL752WB13B3_BPL752WB13B3TelCommsFlt_A | CAT_P3 | WBBWD-1750B004 | PRIV_ALARMACK | A_P1_SERV | BPL752WB13B3 Telemetry Comms Fault Alarm | BPL752WB13B3_BPL752WB13B3TelCommsFlt_A | C_LOPRI | BPL752WB13B3 | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL752WB13B3
BR4_Tags | BPL752WB13B3_CPUEthModLinkOK_A | West Dewatering Bore WB13BS4B003 PLC | CPU Ethernet Module Link Alarm | BPL752WB13B3_CPUEthModLinkOK_A | CAT_P2 | WBBWD-1750B004 | PRIV_ALARMACK | A_P1_SERV | CPU Ethernet Module Link Alarm | BPL752WB13B3_CPUEthModLinkOK_A | C_HIPRI | BPL752WB13B3 | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL752WB13B3
BR4_Tags | BPL752WB13B3_CPUEthModRnng_A | West Dewatering Bore WB13BS4B003 PLC | CPU Ethernet Module NOT Running Alarm | BPL752WB13B3_CPUEthModRnng_A | CAT_P2 | WBBWD-1750B004 | PRIV_ALARMACK | A_P1_SERV | CPU Ethernet Module NOT Running Alarm | BPL752WB13B3_CPUEthModRnng_A | C_HIPRI | BPL752WB13B3 | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL752WB13B3
BR4_Tags | BPL752WB13B3_Mod1OK_A | West Dewatering Bore WB13BS4B003 PLC | DDI Module 1 Alarm | BPL752WB13B3_Mod1OK_A | CAT_P3 | WBBWD-1750B004 | PRIV_ALARMACK | A_P1_SERV | DDI Module 1 Alarm | BPL752WB13B3_Mod1OK_A | C_LOPRI | BPL752WB13B3 | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL752WB13B3 | Slot1_A
BR4_Tags | BPL752WB13B3_Mod2OK_A | West Dewatering Bore WB13BS4B003 PLC | DDI Module 2 Alarm | BPL752WB13B3_Mod2OK_A | CAT_P3 | WBBWD-1750B004 | PRIV_ALARMACK | A_P1_SERV | DDI Module 2 Alarm | BPL752WB13B3_Mod2OK_A | C_LOPRI | BPL752WB13B3 | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL752WB13B3 | Slot2_A
BR4_Tags | BPL752WB13B3_Mod3OK_A | West Dewatering Bore WB13BS4B003 PLC | DDI Module 3 Alarm | BPL752WB13B3_Mod3OK_A | CAT_P3 | WBBWD-1750B004 | PRIV_ALARMACK | A_P1_SERV | DDI Module 3 Alarm | BPL752WB13B3_Mod3OK_A | C_LOPRI | BPL752WB13B3 | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL752WB13B3 | Slot3_A
BR4_Tags | BPL752WB13B3_Mod4OK_A | West Dewatering Bore WB13BS4B003 PLC | DRA Module 4 Alarm | BPL752WB13B3_Mod4OK_A | CAT_P3 | WBBWD-1750B004 | PRIV_ALARMACK | A_P1_SERV | DRA Module 4 Alarm | BPL752WB13B3_Mod4OK_A | C_LOPRI | BPL752WB13B3 | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL752WB13B3 | Slot4_A
BR4_Tags | BPL752WB13B3_Mod5OK_A | West Dewatering Bore WB13BS4B003 PLC | DRA Module 5 Alarm | BPL752WB13B3_Mod5OK_A | CAT_P3 | WBBWD-1750B004 | PRIV_ALARMACK | A_P1_SERV | DRA Module 5 Alarm | BPL752WB13B3_Mod5OK_A | C_LOPRI | BPL752WB13B3 | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL752WB13B3 | Slot5_A
BR4_Tags | BPL752WB13B3_Mod6OK_A | West Dewatering Bore WB13BS4B003 PLC | AMI Module 6 Alarm | BPL752WB13B3_Mod6OK_A | CAT_P3 | WBBWD-1750B004 | PRIV_ALARMACK | A_P1_SERV | AMI Module 6 Alarm | BPL752WB13B3_Mod6OK_A | C_LOPRI | BPL752WB13B3 | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL752WB13B3 | Slot6_A
BR4_Tags | BPL752WB13B3_NOE1LinkOK_A | West Dewatering Bore WB13BS4B003 PLC | NOE1 Slot Link Alarm | BPL752WB13B3_NOE1LinkOK_A | CAT_P2 | WBBWD-1750B004 | PRIV_ALARMACK | A_P1_SERV | NOE1 Slot Link Alarm | BPL752WB13B3_NOE1LinkOK_A | C_HIPRI | BPL752WB13B3 | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL752WB13B3
BR4_Tags | BPL752WB13B3_NOE1Rnng_A | West Dewatering Bore WB13BS4B003 PLC | NOE1 Slot NOT Running Alarm | BPL752WB13B3_NOE1Rnng_A | CAT_P2 | WBBWD-1750B004 | PRIV_ALARMACK | A_P1_SERV | NOE1 Slot NOT Running Alarm | BPL752WB13B3_NOE1Rnng_A | C_HIPRI | BPL752WB13B3 | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL752WB13B3 | Slot7_A
BR4_Tags | BPL752WB13B3_NOE2LinkOK_A | West Dewatering Bore WB13BS4B003 PLC | NOE2 Slot Link Alarm | BPL752WB13B3_NOE2LinkOK_A | CAT_P2 | WBBWD-1750B004 | PRIV_ALARMACK | A_P1_SERV | NOE2 Slot Link Alarm | BPL752WB13B3_NOE2LinkOK_A | C_HIPRI | BPL752WB13B3 | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL752WB13B3
BR4_Tags | BPL752WB13B3_NOE2Rnng_A | West Dewatering Bore WB13BS4B003 PLC | NOE2 Slot NOT Running Alarm | BPL752WB13B3_NOE2Rnng_A | CAT_P2 | WBBWD-1750B004 | PRIV_ALARMACK | A_P1_SERV | NOE2 Slot NOT Running Alarm | BPL752WB13B3_NOE2Rnng_A | C_HIPRI | BPL752WB13B3 | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL752WB13B3 | Slot8_A
BR4_Tags | BPL752WB13B3RTU_DCV_A | West Dewatering Bore WB13BS4B003 PLC | RTU DCV Low Alarm | BPL752WB13B3RTU_DCV_A | CAT_P3 | WBBWD-1750B004 | PRIV_ALARMACK | A_P1_SERV | RTU DCV Low Alarm | BPL752WB13B3RTU_DCV_A | C_LOPRI | BPL752WB13B3 | Class_Process | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL752WB13B3.DCV
BR4_Tags | BPL752WB13B3Tel_BPL752WB13B3Comms_A | West Dewatering Bore WB13BS4B003 PLC | Telemetry to BPL752WB13B3 Comms Alarm | BPL752WB13B3Tel_BPL752WB13B3Comms_A | CAT_P2 | WBBWD-1750B004 | PRIV_ALARMACK | A_P1_SERV | Telemetry to BPL752WB13B3 Comms Alarm | BPL752WB13B3Tel_BPL752WB13B3Comms_A | C_HIPRI | BPL752WB13B3 | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL752WB13B3
BR4_Tags | BPL752WB13B4_BPL752WB13B4TelCommsFlt_A | West Dewatering Bore WB13BS4B004 PLC | BPL752WB13B4 Telemetry Comms Fault Alarm | BPL752WB13B4_BPL752WB13B4TelCommsFlt_A | CAT_P3 | WBBWD-1750B004 | PRIV_ALARMACK | A_P1_SERV | BPL752WB13B4 Telemetry Comms Fault Alarm | BPL752WB13B4_BPL752WB13B4TelCommsFlt_A | C_LOPRI | BPL752WB13B4 | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL752WB13B4
BR4_Tags | BPL752WB13B4_CPUEthModLinkOK_A | West Dewatering Bore WB13BS4B004 PLC | CPU Ethernet Module Link Alarm | BPL752WB13B4_CPUEthModLinkOK_A | CAT_P2 | WBBWD-1750B004 | PRIV_ALARMACK | A_P1_SERV | CPU Ethernet Module Link Alarm | BPL752WB13B4_CPUEthModLinkOK_A | C_HIPRI | BPL752WB13B4 | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL752WB13B4
BR4_Tags | BPL752WB13B4_CPUEthModRnng_A | West Dewatering Bore WB13BS4B004 PLC | CPU Ethernet Module NOT Running Alarm | BPL752WB13B4_CPUEthModRnng_A | CAT_P2 | WBBWD-1750B004 | PRIV_ALARMACK | A_P1_SERV | CPU Ethernet Module NOT Running Alarm | BPL752WB13B4_CPUEthModRnng_A | C_HIPRI | BPL752WB13B4 | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL752WB13B4
BR4_Tags | BPL752WB13B4_Mod1OK_A | West Dewatering Bore WB13BS4B004 PLC | DDI Module 1 Alarm | BPL752WB13B4_Mod1OK_A | CAT_P3 | WBBWD-1750B004 | PRIV_ALARMACK | A_P1_SERV | DDI Module 1 Alarm | BPL752WB13B4_Mod1OK_A | C_LOPRI | BPL752WB13B4 | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL752WB13B4 | Slot1_A
BR4_Tags | BPL752WB13B4_Mod2OK_A | West Dewatering Bore WB13BS4B004 PLC | DDI Module 2 Alarm | BPL752WB13B4_Mod2OK_A | CAT_P3 | WBBWD-1750B004 | PRIV_ALARMACK | A_P1_SERV | DDI Module 2 Alarm | BPL752WB13B4_Mod2OK_A | C_LOPRI | BPL752WB13B4 | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL752WB13B4 | Slot2_A
BR4_Tags | BPL752WB13B4_Mod3OK_A | West Dewatering Bore WB13BS4B004 PLC | DDI Module 3 Alarm | BPL752WB13B4_Mod3OK_A | CAT_P3 | WBBWD-1750B004 | PRIV_ALARMACK | A_P1_SERV | DDI Module 3 Alarm | BPL752WB13B4_Mod3OK_A | C_LOPRI | BPL752WB13B4 | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL752WB13B4 | Slot3_A
BR4_Tags | BPL752WB13B4_Mod4OK_A | West Dewatering Bore WB13BS4B004 PLC | DRA Module 4 Alarm | BPL752WB13B4_Mod4OK_A | CAT_P3 | WBBWD-1750B004 | PRIV_ALARMACK | A_P1_SERV | DRA Module 4 Alarm | BPL752WB13B4_Mod4OK_A | C_LOPRI | BPL752WB13B4 | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL752WB13B4 | Slot4_A
BR4_Tags | BPL752WB13B4_Mod5OK_A | West Dewatering Bore WB13BS4B004 PLC | DRA Module 5 Alarm | BPL752WB13B4_Mod5OK_A | CAT_P3 | WBBWD-1750B004 | PRIV_ALARMACK | A_P1_SERV | DRA Module 5 Alarm | BPL752WB13B4_Mod5OK_A | C_LOPRI | BPL752WB13B4 | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL752WB13B4 | Slot5_A
BR4_Tags | BPL752WB13B4_Mod6OK_A | West Dewatering Bore WB13BS4B004 PLC | AMI Module 6 Alarm | BPL752WB13B4_Mod6OK_A | CAT_P3 | WBBWD-1750B004 | PRIV_ALARMACK | A_P1_SERV | AMI Module 6 Alarm | BPL752WB13B4_Mod6OK_A | C_LOPRI | BPL752WB13B4 | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL752WB13B4 | Slot6_A
BR4_Tags | BPL752WB13B4_NOE1LinkOK_A | West Dewatering Bore WB13BS4B004 PLC | NOE1 Slot Link Alarm | BPL752WB13B4_NOE1LinkOK_A | CAT_P2 | WBBWD-1750B004 | PRIV_ALARMACK | A_P1_SERV | NOE1 Slot Link Alarm | BPL752WB13B4_NOE1LinkOK_A | C_HIPRI | BPL752WB13B4 | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL752WB13B4
BR4_Tags | BPL752WB13B4_NOE1Rnng_A | West Dewatering Bore WB13BS4B004 PLC | NOE1 Slot NOT Running Alarm | BPL752WB13B4_NOE1Rnng_A | CAT_P2 | WBBWD-1750B004 | PRIV_ALARMACK | A_P1_SERV | NOE1 Slot NOT Running Alarm | BPL752WB13B4_NOE1Rnng_A | C_HIPRI | BPL752WB13B4 | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL752WB13B4 | Slot7_A
BR4_Tags | BPL752WB13B4_NOE2LinkOK_A | West Dewatering Bore WB13BS4B004 PLC | NOE2 Slot Link Alarm | BPL752WB13B4_NOE2LinkOK_A | CAT_P2 | WBBWD-1750B004 | PRIV_ALARMACK | A_P1_SERV | NOE2 Slot Link Alarm | BPL752WB13B4_NOE2LinkOK_A | C_HIPRI | BPL752WB13B4 | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL752WB13B4
BR4_Tags | BPL752WB13B4_NOE2Rnng_A | West Dewatering Bore WB13BS4B004 PLC | NOE2 Slot NOT Running Alarm | BPL752WB13B4_NOE2Rnng_A | CAT_P2 | WBBWD-1750B004 | PRIV_ALARMACK | A_P1_SERV | NOE2 Slot NOT Running Alarm | BPL752WB13B4_NOE2Rnng_A | C_HIPRI | BPL752WB13B4 | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL752WB13B4 | Slot8_A
BR4_Tags | BPL752WB13B4RTU_DCV_A | West Dewatering Bore WB13BS4B004 PLC | RTU DCV Low Alarm | BPL752WB13B4RTU_DCV_A | CAT_P3 | WBBWD-1750B004 | PRIV_ALARMACK | A_P1_SERV | RTU DCV Low Alarm | BPL752WB13B4RTU_DCV_A | C_LOPRI | BPL752WB13B4 | Class_Process | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL752WB13B4.DCV
BR4_Tags | BPL752WB13B4Tel_BPL752WB13B4Comms_A | West Dewatering Bore WB13BS4B004 PLC | Telemetry to BPL752WB13B4 Comms Alarm | BPL752WB13B4Tel_BPL752WB13B4Comms_A | CAT_P2 | WBBWD-1750B004 | PRIV_ALARMACK | A_P1_SERV | Telemetry to BPL752WB13B4 Comms Alarm | BPL752WB13B4Tel_BPL752WB13B4Comms_A | C_HIPRI | BPL752WB13B4 | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL752WB13B4
BR4_Tags | BPL752WB13B5_BPL752WB13B5TelCommsFlt_A | West Dewatering Bore WB13BS4B005 PLC | BPL752WB13B5 Telemetry Comms Fault Alarm | BPL752WB13B5_BPL752WB13B5TelCommsFlt_A | CAT_P3 | WBBWD-1750B004 | PRIV_ALARMACK | A_P1_SERV | BPL752WB13B5 Telemetry Comms Fault Alarm | BPL752WB13B5_BPL752WB13B5TelCommsFlt_A | C_LOPRI | BPL752WB13B5 | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL752WB13B5
BR4_Tags | BPL752WB13B5_CPUEthModLinkOK_A | West Dewatering Bore WB13BS4B005 PLC | CPU Ethernet Module Link Alarm | BPL752WB13B5_CPUEthModLinkOK_A | CAT_P2 | WBBWD-1750B004 | PRIV_ALARMACK | A_P1_SERV | CPU Ethernet Module Link Alarm | BPL752WB13B5_CPUEthModLinkOK_A | C_HIPRI | BPL752WB13B5 | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL752WB13B5
BR4_Tags | BPL752WB13B5_CPUEthModRnng_A | West Dewatering Bore WB13BS4B005 PLC | CPU Ethernet Module NOT Running Alarm | BPL752WB13B5_CPUEthModRnng_A | CAT_P2 | WBBWD-1750B004 | PRIV_ALARMACK | A_P1_SERV | CPU Ethernet Module NOT Running Alarm | BPL752WB13B5_CPUEthModRnng_A | C_HIPRI | BPL752WB13B5 | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL752WB13B5
BR4_Tags | BPL752WB13B5_Mod1OK_A | West Dewatering Bore WB13BS4B005 PLC | DDI Module 1 Alarm | BPL752WB13B5_Mod1OK_A | CAT_P3 | WBBWD-1750B004 | PRIV_ALARMACK | A_P1_SERV | DDI Module 1 Alarm | BPL752WB13B5_Mod1OK_A | C_LOPRI | BPL752WB13B5 | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL752WB13B5 | Slot1_A
BR4_Tags | BPL752WB13B5_Mod2OK_A | West Dewatering Bore WB13BS4B005 PLC | DDI Module 2 Alarm | BPL752WB13B5_Mod2OK_A | CAT_P3 | WBBWD-1750B004 | PRIV_ALARMACK | A_P1_SERV | DDI Module 2 Alarm | BPL752WB13B5_Mod2OK_A | C_LOPRI | BPL752WB13B5 | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL752WB13B5 | Slot2_A
BR4_Tags | BPL752WB13B5_Mod3OK_A | West Dewatering Bore WB13BS4B005 PLC | DDI Module 3 Alarm | BPL752WB13B5_Mod3OK_A | CAT_P3 | WBBWD-1750B004 | PRIV_ALARMACK | A_P1_SERV | DDI Module 3 Alarm | BPL752WB13B5_Mod3OK_A | C_LOPRI | BPL752WB13B5 | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL752WB13B5 | Slot3_A
BR4_Tags | BPL752WB13B5_Mod4OK_A | West Dewatering Bore WB13BS4B005 PLC | DRA Module 4 Alarm | BPL752WB13B5_Mod4OK_A | CAT_P3 | WBBWD-1750B004 | PRIV_ALARMACK | A_P1_SERV | DRA Module 4 Alarm | BPL752WB13B5_Mod4OK_A | C_LOPRI | BPL752WB13B5 | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL752WB13B5 | Slot4_A
BR4_Tags | BPL752WB13B5_Mod5OK_A | West Dewatering Bore WB13BS4B005 PLC | DRA Module 5 Alarm | BPL752WB13B5_Mod5OK_A | CAT_P3 | WBBWD-1750B004 | PRIV_ALARMACK | A_P1_SERV | DRA Module 5 Alarm | BPL752WB13B5_Mod5OK_A | C_LOPRI | BPL752WB13B5 | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL752WB13B5 | Slot5_A
BR4_Tags | BPL752WB13B5_Mod6OK_A | West Dewatering Bore WB13BS4B005 PLC | AMI Module 6 Alarm | BPL752WB13B5_Mod6OK_A | CAT_P3 | WBBWD-1750B004 | PRIV_ALARMACK | A_P1_SERV | AMI Module 6 Alarm | BPL752WB13B5_Mod6OK_A | C_LOPRI | BPL752WB13B5 | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL752WB13B5 | Slot6_A
BR4_Tags | BPL752WB13B5_NOE1LinkOK_A | West Dewatering Bore WB13BS4B005 PLC | NOE1 Slot Link Alarm | BPL752WB13B5_NOE1LinkOK_A | CAT_P2 | WBBWD-1750B004 | PRIV_ALARMACK | A_P1_SERV | NOE1 Slot Link Alarm | BPL752WB13B5_NOE1LinkOK_A | C_HIPRI | BPL752WB13B5 | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL752WB13B5
BR4_Tags | BPL752WB13B5_NOE1Rnng_A | West Dewatering Bore WB13BS4B005 PLC | NOE1 Slot NOT Running Alarm | BPL752WB13B5_NOE1Rnng_A | CAT_P2 | WBBWD-1750B004 | PRIV_ALARMACK | A_P1_SERV | NOE1 Slot NOT Running Alarm | BPL752WB13B5_NOE1Rnng_A | C_HIPRI | BPL752WB13B5 | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL752WB13B5 | Slot7_A
BR4_Tags | BPL752WB13B5_NOE2LinkOK_A | West Dewatering Bore WB13BS4B005 PLC | NOE2 Slot Link Alarm | BPL752WB13B5_NOE2LinkOK_A | CAT_P2 | WBBWD-1750B004 | PRIV_ALARMACK | A_P1_SERV | NOE2 Slot Link Alarm | BPL752WB13B5_NOE2LinkOK_A | C_HIPRI | BPL752WB13B5 | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL752WB13B5
BR4_Tags | BPL752WB13B5_NOE2Rnng_A | West Dewatering Bore WB13BS4B005 PLC | NOE2 Slot NOT Running Alarm | BPL752WB13B5_NOE2Rnng_A | CAT_P2 | WBBWD-1750B004 | PRIV_ALARMACK | A_P1_SERV | NOE2 Slot NOT Running Alarm | BPL752WB13B5_NOE2Rnng_A | C_HIPRI | BPL752WB13B5 | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL752WB13B5 | Slot8_A
BR4_Tags | BPL752WB13B5RTU_DCV_A | West Dewatering Bore WB13BS4B005 PLC | RTU DCV Low Alarm | BPL752WB13B5RTU_DCV_A | CAT_P3 | WBBWD-1750B004 | PRIV_ALARMACK | A_P1_SERV | RTU DCV Low Alarm | BPL752WB13B5RTU_DCV_A | C_LOPRI | BPL752WB13B5 | Class_Process | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL752WB13B5.DCV
BR4_Tags | BPL752WB13B5Tel_BPL752WB13B5Comms_A | West Dewatering Bore WB13BS4B005 PLC | Telemetry to BPL752WB13B5 Comms Alarm | BPL752WB13B5Tel_BPL752WB13B5Comms_A | CAT_P2 | WBBWD-1750B004 | PRIV_ALARMACK | A_P1_SERV | Telemetry to BPL752WB13B5 Comms Alarm | BPL752WB13B5Tel_BPL752WB13B5Comms_A | C_HIPRI | BPL752WB13B5 | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL752WB13B5
BR4_Tags | BPL760_BPL101CommsFlt_A | Water Distribution PLC | InterPLC BPL101 Communications Faulted | BPL760_BPL101CommsFlt_A | CAT_P3 | BPL760 | PRIV_ALARMACK | A_P1_SERV | InterPLC BPL101 Communications Faulted | BPL760_BPL101CommsFlt_A | C_LOPRI | BPL760 | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL760
BR4_Tags | BPL760_BPL601CommsFlt_A | Water Distribution PLC | InterPLC BPL601 Communications Faulted | BPL760_BPL601CommsFlt_A | CAT_P3 | BPL760 | PRIV_ALARMACK | A_P1_SERV | InterPLC BPL601 Communications Faulted | BPL760_BPL601CommsFlt_A | C_LOPRI | BPL760 | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL760
BR4_Tags | BPL760_BPL801CommsFlt_A | Water Distribution PLC | InterPLC BPL801 Communications Faulted | BPL760_BPL801CommsFlt_A | CAT_P2 | BPL760 | PRIV_ALARMACK | A_P1_SERV | InterPLC BPL801 Communications Faulted | BPL760_BPL801CommsFlt_A | C_HIPRI | BPL760 | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL760
BR4_Tags | BPL760_CPUEthModLinkOK_A | Water Distribution PLC | CPU Module Ethernet Link Fault | BPL760_CPUEthModLinkOK_A | CAT_P2 | BPL760 | PRIV_ALARMACK | A_P1_SERV | CPU Module Ethernet Link Fault | BPL760_CPUEthModLinkOK_A | C_HIPRI | BPL760 | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL760
BR4_Tags | BPL760_CPUEthModRnng_A | Water Distribution PLC | CPU Module Ethernet Port Not Running Fault | BPL760_CPUEthModRnng_A | CAT_P2 | BPL760 | PRIV_ALARMACK | A_P1_SERV | CPU Module Ethernet Port Not Running Fault | BPL760_CPUEthModRnng_A | C_HIPRI | BPL760 | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL760 | Slot0_A
BR4_Tags | BPL760_NOE1LinkOK_A | Water Distribution PLC | NOE1 Ethernet Link Status Fault | BPL760_NOE1LinkOK_A | CAT_P2 | BPL760 | PRIV_ALARMACK | A_P1_SERV | NOE1 Ethernet Link Status Fault | BPL760_NOE1LinkOK_A | C_HIPRI | BPL760 | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL760
BR4_Tags | BPL760_NOE1Rnng_A | Water Distribution PLC | NOE1 Ethernet Module Not Running | BPL760_NOE1Rnng_A | CAT_P2 | BPL760 | PRIV_ALARMACK | A_P1_SERV | NOE1 Ethernet Module Not Running | BPL760_NOE1Rnng_A | C_HIPRI | BPL760 | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL760 | Slot1_A
BR4_Tags | BPL760_R0S2OK_A | Water Distribution PLC | Rack 0 Slot 2 Module Fault | BPL760_R0S2OK_A | CAT_P3 | BPL760 | PRIV_ALARMACK | A_P1_SERV | Rack 0 Slot 2 Module Fault | BPL760_R0S2OK_A | C_LOPRI | BPL760 | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL760 | Slot2_A
BR4_Tags | BPL760_R0S3OK_A | Water Distribution PLC | Rack 0 Slot 3 Module Fault | BPL760_R0S3OK_A | CAT_P3 | BPL760 | PRIV_ALARMACK | A_P1_SERV | Rack 0 Slot 3 Module Fault | BPL760_R0S3OK_A | C_LOPRI | BPL760 | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL760 | Slot3_A
BR4_Tags | BPL760_R0S4OK_A | Water Distribution PLC | Rack 0 Slot 4 Module Fault | BPL760_R0S4OK_A | CAT_P3 | BPL760 | PRIV_ALARMACK | A_P1_SERV | Rack 0 Slot 4 Module Fault | BPL760_R0S4OK_A | C_LOPRI | BPL760 | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL760 | Slot4_A
BR4_Tags | BPL760_R0S5OK_A | Water Distribution PLC | Rack 0 Slot 5 Module Fault | BPL760_R0S5OK_A | CAT_P3 | BPL760 | PRIV_ALARMACK | A_P1_SERV | Rack 0 Slot 5 Module Fault | BPL760_R0S5OK_A | C_LOPRI | BPL760 | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL760 | Slot5_A
BR4_Tags | BPL760_R0S6OK_A | Water Distribution PLC | Rack 0 Slot 6 Module Fault | BPL760_R0S6OK_A | CAT_P3 | BPL760 | PRIV_ALARMACK | A_P1_SERV | Rack 0 Slot 6 Module Fault | BPL760_R0S6OK_A | C_LOPRI | BPL760 | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL760 | Slot6_A
BR4_Tags | BPL760_R1S0OK_A | Water Distribution PLC | Rack 1 Slot 0 Module Fault | BPL760_R1S0OK_A | CAT_P3 | BPL760 | PRIV_ALARMACK | A_P1_SERV | Rack 1 Slot 0 Module Fault | BPL760_R1S0OK_A | C_LOPRI | BPL760 | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL760.Rack1 | Slot0_A
BR4_Tags | BPL760_R1S1OK_A | Water Distribution PLC | Rack 1 Slot 1 Module Fault | BPL760_R1S1OK_A | CAT_P3 | BPL760 | PRIV_ALARMACK | A_P1_SERV | Rack 1 Slot 1 Module Fault | BPL760_R1S1OK_A | C_LOPRI | BPL760 | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL760.Rack1 | Slot1_A
BR4_Tags | BPL760_R1S2Ch0OK_A | Water Distribution PLC | Rack 1 Slot 2 Channel 0 Fault | BPL760_R1S2Ch0OK_A | CAT_P3 | BPL760 | PRIV_ALARMACK | A_P1_SERV | Rack 1 Slot 2 Channel 0 Fault | BPL760_R1S2Ch0OK_A | C_LOPRI | BPL760 | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL760.Rack1
BR4_Tags | BPL760_R1S2Ch0ROVF_E | Water Distribution PLC | Rack 1 Slot 2 Channel 0 Overflow Error | BPL760_R1S2Ch0ROVF_E | CAT_P4 | BPL760 | PRIV_ALARMACK | A_P1_SERV | Rack 1 Slot 2 Channel 0 Overflow Error | BPL760_R1S2Ch0ROVF_E | C_EVENT | BPL760 | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL760.Rack1
BR4_Tags | BPL760_R1S2Ch0RUNF_E | Water Distribution PLC | Rack 1 Slot 2 Channel 0 Underflow Error | BPL760_R1S2Ch0RUNF_E | CAT_P4 | BPL760 | PRIV_ALARMACK | A_P1_SERV | Rack 1 Slot 2 Channel 0 Underflow Error | BPL760_R1S2Ch0RUNF_E | C_EVENT | BPL760 | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL760.Rack1
BR4_Tags | BPL760_R1S2Ch1OK_A | Water Distribution PLC | Rack 1 Slot 2 Channel 1 Fault | BPL760_R1S2Ch1OK_A | CAT_P3 | BPL760 | PRIV_ALARMACK | A_P1_SERV | Rack 1 Slot 2 Channel 1 Fault | BPL760_R1S2Ch1OK_A | C_LOPRI | BPL760 | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL760.Rack1
BR4_Tags | BPL760_R1S2Ch1ROVF_E | Water Distribution PLC | Rack 1 Slot 2 Channel 1 Overflow Error | BPL760_R1S2Ch1ROVF_E | CAT_P4 | BPL760 | PRIV_ALARMACK | A_P1_SERV | Rack 1 Slot 2 Channel 1 Overflow Error | BPL760_R1S2Ch1ROVF_E | C_EVENT | BPL760 | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL760.Rack1
BR4_Tags | BPL760_R1S2Ch1RUNF_E | Water Distribution PLC | Rack 1 Slot 2 Channel 1 Underflow Error | BPL760_R1S2Ch1RUNF_E | CAT_P4 | BPL760 | PRIV_ALARMACK | A_P1_SERV | Rack 1 Slot 2 Channel 1 Underflow Error | BPL760_R1S2Ch1RUNF_E | C_EVENT | BPL760 | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL760.Rack1
BR4_Tags | BPL760_R1S2Ch2OK_A | Water Distribution PLC | Rack 1 Slot 2 Channel 2 Fault | BPL760_R1S2Ch2OK_A | CAT_P3 | BPL760 | PRIV_ALARMACK | A_P1_SERV | Rack 1 Slot 2 Channel 2 Fault | BPL760_R1S2Ch2OK_A | C_LOPRI | BPL760 | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL760.Rack1
BR4_Tags | BPL760_R1S2Ch2ROVF_E | Water Distribution PLC | Rack 1 Slot 2 Channel 2 Overflow Error | BPL760_R1S2Ch2ROVF_E | CAT_P4 | BPL760 | PRIV_ALARMACK | A_P1_SERV | Rack 1 Slot 2 Channel 2 Overflow Error | BPL760_R1S2Ch2ROVF_E | C_EVENT | BPL760 | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL760.Rack1
BR4_Tags | BPL760_R1S2Ch2RUNF_E | Water Distribution PLC | Rack 1 Slot 2 Channel 2 Underflow Error | BPL760_R1S2Ch2RUNF_E | CAT_P4 | BPL760 | PRIV_ALARMACK | A_P1_SERV | Rack 1 Slot 2 Channel 2 Underflow Error | BPL760_R1S2Ch2RUNF_E | C_EVENT | BPL760 | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL760.Rack1
BR4_Tags | BPL760_R1S2OK_A | Water Distribution PLC | Rack 1 Slot 2 Module Fault | BPL760_R1S2OK_A | CAT_P3 | BPL760 | PRIV_ALARMACK | A_P1_SERV | Rack 1 Slot 2 Module Fault | BPL760_R1S2OK_A | C_LOPRI | BPL760 | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL760.Rack1 | Slot2_A
BR4_Tags | BPL760_R1S3Ch0OK_A | Water Distribution PLC | Rack 1 Slot 3 Channel 0 Fault | BPL760_R1S3Ch0OK_A | CAT_P3 | BPL760 | PRIV_ALARMACK | A_P1_SERV | Rack 1 Slot 3 Channel 0 Fault | BPL760_R1S3Ch0OK_A | C_LOPRI | BPL760 | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL760.Rack1
BR4_Tags | BPL760_R1S3Ch0ROVF_E | Water Distribution PLC | Rack 1 Slot 3 Channel 0 Overflow Error | BPL760_R1S3Ch0ROVF_E | CAT_P4 | BPL760 | PRIV_ALARMACK | A_P1_SERV | Rack 1 Slot 3 Channel 0 Overflow Error | BPL760_R1S3Ch0ROVF_E | C_EVENT | BPL760 | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL760.Rack1
BR4_Tags | BPL760_R1S3Ch0RUNF_E | Water Distribution PLC | Rack 1 Slot 3 Channel 0 Underflow Error | BPL760_R1S3Ch0RUNF_E | CAT_P4 | BPL760 | PRIV_ALARMACK | A_P1_SERV | Rack 1 Slot 3 Channel 0 Underflow Error | BPL760_R1S3Ch0RUNF_E | C_EVENT | BPL760 | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL760.Rack1
BR4_Tags | BPL760_R1S3Ch1OK_A | Water Distribution PLC | Rack 1 Slot 3 Channel 1 Fault | BPL760_R1S3Ch1OK_A | CAT_P3 | BPL760 | PRIV_ALARMACK | A_P1_SERV | Rack 1 Slot 3 Channel 1 Fault | BPL760_R1S3Ch1OK_A | C_LOPRI | BPL760 | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL760.Rack1
BR4_Tags | BPL760_R1S3Ch1ROVF_E | Water Distribution PLC | Rack 1 Slot 3 Channel 1 Overflow Error | BPL760_R1S3Ch1ROVF_E | CAT_P4 | BPL760 | PRIV_ALARMACK | A_P1_SERV | Rack 1 Slot 3 Channel 1 Overflow Error | BPL760_R1S3Ch1ROVF_E | C_EVENT | BPL760 | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL760.Rack1
BR4_Tags | BPL760_R1S3Ch1RUNF_E | Water Distribution PLC | Rack 1 Slot 3 Channel 1 Underflow Error | BPL760_R1S3Ch1RUNF_E | CAT_P4 | BPL760 | PRIV_ALARMACK | A_P1_SERV | Rack 1 Slot 3 Channel 1 Underflow Error | BPL760_R1S3Ch1RUNF_E | C_EVENT | BPL760 | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL760.Rack1
BR4_Tags | BPL760_R1S3Ch2OK_A | Water Distribution PLC | Rack 1 Slot 3 Channel 2 Fault | BPL760_R1S3Ch2OK_A | CAT_P3 | BPL760 | PRIV_ALARMACK | A_P1_SERV | Rack 1 Slot 3 Channel 2 Fault | BPL760_R1S3Ch2OK_A | C_LOPRI | BPL760 | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL760.Rack1
BR4_Tags | BPL760_R1S3Ch2ROVF_E | Water Distribution PLC | Rack 1 Slot 3 Channel 2 Overflow Error | BPL760_R1S3Ch2ROVF_E | CAT_P3 | BPL760 | PRIV_ALARMACK | A_P1_SERV | Rack 1 Slot 3 Channel 2 Overflow Error | BPL760_R1S3Ch2ROVF_E | C_LOPRI | BPL760 | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL760.Rack1
BR4_Tags | BPL760_R1S3Ch2RUNF_E | Water Distribution PLC | Rack 1 Slot 3 Channel 2 Underflow Error | BPL760_R1S3Ch2RUNF_E | CAT_P3 | BPL760 | PRIV_ALARMACK | A_P1_SERV | Rack 1 Slot 3 Channel 2 Underflow Error | BPL760_R1S3Ch2RUNF_E | C_LOPRI | BPL760 | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL760.Rack1
BR4_Tags | BPL760_R1S3OK_A | Water Distribution PLC | Rack 1 Slot 3 Module Fault | BPL760_R1S3OK_A | CAT_P3 | BPL760 | PRIV_ALARMACK | A_P1_SERV | Rack 1 Slot 3 Module Fault | BPL760_R1S3OK_A | C_LOPRI | BPL760 | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL760.Rack1 | Slot3_A
BR4_Tags | BPL760_R1S4Ch0OK_A | Water Distribution PLC | Rack 1 Slot 4 Channel 0 Fault | BPL760_R1S4Ch0OK_A | CAT_P3 | BPL760 | PRIV_ALARMACK | A_P1_SERV | Rack 1 Slot 4 Channel 0 Fault | BPL760_R1S4Ch0OK_A | C_LOPRI | BPL760 | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL760.Rack1
BR4_Tags | BPL760_R1S4Ch0ROVF_E | Water Distribution PLC | Rack 1 Slot 4 Channel 0 Overflow Error | BPL760_R1S4Ch0ROVF_E | CAT_P3 | BPL760 | PRIV_ALARMACK | A_P1_SERV | Rack 1 Slot 4 Channel 0 Overflow Error | BPL760_R1S4Ch0ROVF_E | C_LOPRI | BPL760 | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL760.Rack1
BR4_Tags | BPL760_R1S4Ch0RUNF_E | Water Distribution PLC | Rack 1 Slot 4 Channel 0 Underflow Error | BPL760_R1S4Ch0RUNF_E | CAT_P3 | BPL760 | PRIV_ALARMACK | A_P1_SERV | Rack 1 Slot 4 Channel 0 Underflow Error | BPL760_R1S4Ch0RUNF_E | C_LOPRI | BPL760 | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL760.Rack1
BR4_Tags | BPL760_R1S4Ch1OK_A | Water Distribution PLC | Rack 1 Slot 4 Channel 1 Fault | BPL760_R1S4Ch1OK_A | CAT_P3 | BPL760 | PRIV_ALARMACK | A_P1_SERV | Rack 1 Slot 4 Channel 1 Fault | BPL760_R1S4Ch1OK_A | C_LOPRI | BPL760 | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL760.Rack1
BR4_Tags | BPL760_R1S4Ch1ROVF_E | Water Distribution PLC | Rack 1 Slot 4 Channel 1 Overflow Error | BPL760_R1S4Ch1ROVF_E | CAT_P3 | BPL760 | PRIV_ALARMACK | A_P1_SERV | Rack 1 Slot 4 Channel 1 Overflow Error | BPL760_R1S4Ch1ROVF_E | C_LOPRI | BPL760 | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL760.Rack1
BR4_Tags | BPL760_R1S4Ch1RUNF_E | Water Distribution PLC | Rack 1 Slot 4 Channel 1 Underflow Error | BPL760_R1S4Ch1RUNF_E | CAT_P3 | BPL760 | PRIV_ALARMACK | A_P1_SERV | Rack 1 Slot 4 Channel 1 Underflow Error | BPL760_R1S4Ch1RUNF_E | C_LOPRI | BPL760 | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL760.Rack1
BR4_Tags | BPL760_R1S4Ch2OK_A | Water Distribution PLC | Rack 1 Slot 4 Channel 2 Fault | BPL760_R1S4Ch2OK_A | CAT_P3 | BPL760 | PRIV_ALARMACK | A_P1_SERV | Rack 1 Slot 4 Channel 2 Fault | BPL760_R1S4Ch2OK_A | C_LOPRI | BPL760 | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL760.Rack1
BR4_Tags | BPL760_R1S4Ch2ROVF_E | Water Distribution PLC | Rack 1 Slot 4 Channel 2 Overflow Error | BPL760_R1S4Ch2ROVF_E | CAT_P3 | BPL760 | PRIV_ALARMACK | A_P1_SERV | Rack 1 Slot 4 Channel 2 Overflow Error | BPL760_R1S4Ch2ROVF_E | C_LOPRI | BPL760 | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL760.Rack1
BR4_Tags | BPL760_R1S4Ch2RUNF_E | Water Distribution PLC | Rack 1 Slot 4 Channel 2 Underflow Error | BPL760_R1S4Ch2RUNF_E | CAT_P3 | BPL760 | PRIV_ALARMACK | A_P1_SERV | Rack 1 Slot 4 Channel 2 Underflow Error | BPL760_R1S4Ch2RUNF_E | C_LOPRI | BPL760 | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL760.Rack1
BR4_Tags | BPL760_R1S4Ch3OK_A | Water Distribution PLC | Rack 1 Slot 4 Channel 3 Fault | BPL760_R1S4Ch3OK_A | CAT_P3 | BPL760 | PRIV_ALARMACK | A_P1_SERV | Rack 1 Slot 4 Channel 3 Fault | BPL760_R1S4Ch3OK_A | C_LOPRI | BPL760 | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL760.Rack1
BR4_Tags | BPL760_R1S4Ch3ROVF_E | Water Distribution PLC | Rack 1 Slot 4 Channel 3 Overflow Error | BPL760_R1S4Ch3ROVF_E | CAT_P3 | BPL760 | PRIV_ALARMACK | A_P1_SERV | Rack 1 Slot 4 Channel 3 Overflow Error | BPL760_R1S4Ch3ROVF_E | C_LOPRI | BPL760 | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL760.Rack1
BR4_Tags | BPL760_R1S4Ch3RUNF_E | Water Distribution PLC | Rack 1 Slot 4 Channel 3 Underflow Error | BPL760_R1S4Ch3RUNF_E | CAT_P3 | BPL760 | PRIV_ALARMACK | A_P1_SERV | Rack 1 Slot 4 Channel 3 Underflow Error | BPL760_R1S4Ch3RUNF_E | C_LOPRI | BPL760 | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL760.Rack1
BR4_Tags | BPL760_R1S4OK_A | Water Distribution PLC | Rack 1 Slot 4 Module Fault | BPL760_R1S4OK_A | CAT_P3 | BPL760 | PRIV_ALARMACK | A_P1_SERV | Rack 1 Slot 4 Module Fault | BPL760_R1S4OK_A | C_LOPRI | BPL760 | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL760.Rack1 | Slot4_A
BR4_Tags | BPL760_R1S5Ch0OK_A | Water Distribution PLC | Rack 1 Slot 5 Channel 0 Fault | BPL760_R1S5Ch0OK_A | CAT_P3 | BPL760 | PRIV_ALARMACK | A_P1_SERV | Rack 1 Slot 5 Channel 0 Fault | BPL760_R1S5Ch0OK_A | C_LOPRI | BPL760 | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL760.Rack1
BR4_Tags | BPL760_R1S5Ch0ROVF_E | Water Distribution PLC | Rack 1 Slot 5 Channel 0 Overflow Error | BPL760_R1S5Ch0ROVF_E | CAT_P3 | BPL760 | PRIV_ALARMACK | A_P1_SERV | Rack 1 Slot 5 Channel 0 Overflow Error | BPL760_R1S5Ch0ROVF_E | C_LOPRI | BPL760 | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL760.Rack1
BR4_Tags | BPL760_R1S5Ch0RUNF_E | Water Distribution PLC | Rack 1 Slot 5 Channel 0 Underflow Error | BPL760_R1S5Ch0RUNF_E | CAT_P3 | BPL760 | PRIV_ALARMACK | A_P1_SERV | Rack 1 Slot 5 Channel 0 Underflow Error | BPL760_R1S5Ch0RUNF_E | C_LOPRI | BPL760 | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL760.Rack1
BR4_Tags | BPL760_R1S5OK_A | Water Distribution PLC | Rack 1 Slot 5 Module Fault | BPL760_R1S5OK_A | CAT_P3 | BPL760 | PRIV_ALARMACK | A_P1_SERV | Rack 1 Slot 5 Module Fault | BPL760_R1S5OK_A | C_LOPRI | BPL760 | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL760.Rack1 | Slot5_A
BR4_Tags | BPL760_R1S6Ch0OK_A | Water Distribution PLC | Rack 1 Slot 6 Channel 0 Fault | BPL760_R1S6Ch0OK_A | CAT_P3 | BPL760 | PRIV_ALARMACK | A_P1_SERV | Rack 1 Slot 3 Channel 2 Fault | BPL760_R1S6Ch0OK_A | C_LOPRI | BPL760 | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL760.Rack1
BR4_Tags | BPL760_R1S6Ch0ROVF_E | Water Distribution PLC | Rack 1 Slot 6 Channel 0 Overflow Error | BPL760_R1S6Ch0ROVF_E | CAT_P3 | BPL760 | PRIV_ALARMACK | A_P1_SERV | Rack 1 Slot 3 Channel 2 Overflow Error | BPL760_R1S6Ch0ROVF_E | C_LOPRI | BPL760 | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL760.Rack1
BR4_Tags | BPL760_R1S6Ch0RUNF_E | Water Distribution PLC | Rack 1 Slot 6 Channel 0 Underflow Error | BPL760_R1S6Ch0RUNF_E | CAT_P3 | BPL760 | PRIV_ALARMACK | A_P1_SERV | Rack 1 Slot 5 Channel 2 Underflow Error | BPL760_R1S6Ch0RUNF_E | C_LOPRI | BPL760 | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL760.Rack1
BR4_Tags | BPL760_R1S6OK_A | Water Distribution PLC | Rack 1 Slot 6 Module Fault | BPL760_R1S6OK_A | CAT_P3 | BPL760 | PRIV_ALARMACK | A_P1_SERV | Rack 1 Slot 6 Module Fault | BPL760_R1S6OK_A | C_LOPRI | BPL760 | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL760.Rack1 | Slot6_A
BR4_Tags | BPP103_ACFlt_E | ROM Sprays Pump 103 | MNSiS AC Control voltage fault | BPP103_ACFlt_E | CAT_EVENT | WBWD-1750B012 | PRIV_ALARMACK | A_P1_SERV | MNSiS AC Control voltage fault | BPP103_ACFlt_E | C_EVENT | BPP103 | Class_Equipment | BR4_Cluster1 | BR4.UTILITIES.WATER.WBWD.BPP103_104.BPP103
BR4_Tags | BPP103_CARemote_E | ROM Sprays Pump 103 | MNSiS Control Access not in remote | BPP103_CARemote_E | CAT_EVENT | WBWD-1750B012 | PRIV_ALARMACK | A_P1_SERV | MNSiS Control Access not in remote | BPP103_CARemote_E | C_EVENT | BPP103 | Class_Equipment | BR4_Cluster1 | BR4.UTILITIES.WATER.WBWD.BPP103_104.BPP103
BR4_Tags | BPP103_DCOK_E | ROM Sprays Pump 103 | MNSiS DC Control voltage fault | BPP103_DCOK_E | CAT_EVENT | WBWD-1750B012 | PRIV_ALARMACK | A_P1_SERV | MNSiS DC Control voltage fault | BPP103_DCOK_E | C_EVENT | BPP103 | Class_Equipment | BR4_Cluster1 | BR4.UTILITIES.WATER.WBWD.BPP103_104.BPP103
BR4_Tags | BPP103_EStop_E | ROM Sprays Pump 103 | MNSiS Emergency stop active | BPP103_EStop_E | CAT_EVENT | WBWD-1750B012 | PRIV_ALARMACK | A_P1_SERV | MNSiS Emergency stop active | BPP103_EStop_E | C_EVENT | BPP103 | Class_Equipment | BR4_Cluster1 | BR4.UTILITIES.WATER.WBWD.BPP103_104.BPP103
BR4_Tags | BPP103_FailSafe_E | ROM Sprays Pump 103 | MNSiS MControl in fail safe mode | BPP103_FailSafe_E | CAT_EVENT | WBWD-1750B012 | PRIV_ALARMACK | A_P1_SERV | MNSiS MControl in fail safe mode | BPP103_FailSafe_E | C_EVENT | BPP103 | Class_Equipment | BR4_Cluster1 | BR4.UTILITIES.WATER.WBWD.BPP103_104.BPP103
BR4_Tags | BPP103_FwdCls_E | ROM Sprays Pump 103 | MNSiS Forward contractor failed to close | BPP103_FwdCls_E | CAT_EVENT | WBWD-1750B012 | PRIV_ALARMACK | A_P1_SERV | MNSiS Forward contractor failed to close | BPP103_FwdCls_E | C_EVENT | BPP103 | Class_Equipment | BR4_Cluster1 | BR4.UTILITIES.WATER.WBWD.BPP103_104.BPP103
BR4_Tags | BPP103_IRFHard_E | ROM Sprays Pump 103 | MNSiS Internal relay h/w fault trip | BPP103_IRFHard_E | CAT_EVENT | WBWD-1750B012 | PRIV_ALARMACK | A_P1_SERV | MNSiS Internal relay h/w fault trip | BPP103_IRFHard_E | C_EVENT | BPP103 | Class_Equipment | BR4_Cluster1 | BR4.UTILITIES.WATER.WBWD.BPP103_104.BPP103
BR4_Tags | BPP103_IRFSoft_E | ROM Sprays Pump 103 | MNSiS Internal relay s/w fault trip | BPP103_IRFSoft_E | CAT_EVENT | WBWD-1750B012 | PRIV_ALARMACK | A_P1_SERV | MNSiS Internal relay s/w fault trip | BPP103_IRFSoft_E | C_EVENT | BPP103 | Class_Equipment | BR4_Cluster1 | BR4.UTILITIES.WATER.WBWD.BPP103_104.BPP103
BR4_Tags | BPP103_IS01Opn_E | ROM Sprays Pump 103 | MNSiS MStart isolated | BPP103_IS01Opn_E | CAT_EVENT | WBWD-1750B012 | PRIV_ALARMACK | A_P1_SERV | MNSiS MStart isolated | BPP103_IS01Opn_E | C_EVENT | BPP103 | Class_Equipment | BR4_Cluster1 | BR4.UTILITIES.WATER.WBWD.BPP103_104.BPP103.IS01
BR4_Tags | BPP103_IS01Test_E | ROM Sprays Pump 103 | MNSiS Isolator in test position | BPP103_IS01Test_E | CAT_EVENT | WBWD-1750B012 | PRIV_ALARMACK | A_P1_SERV | MNSiS Isolator in test position | BPP103_IS01Test_E | C_EVENT | BPP103 | Class_Equipment | BR4_Cluster1 | BR4.UTILITIES.WATER.WBWD.BPP103_104.BPP103.IS01
BR4_Tags | BPP103_MContID_E | ROM Sprays Pump 103 | MNSiS Location supervision trip | BPP103_MContID_E | CAT_EVENT | WBWD-1750B012 | PRIV_ALARMACK | A_P1_SERV | MNSiS Location supervision trip | BPP103_MContID_E | C_EVENT | BPP103 | Class_Equipment | BR4_Cluster1 | BR4.UTILITIES.WATER.WBWD.BPP103_104.BPP103
BR4_Tags | BPP103_MContLife_E | ROM Sprays Pump 103 | MNSiS MControl life bit not healthy | BPP103_MContLife_E | CAT_EVENT | WBWD-1750B012 | PRIV_ALARMACK | A_P1_SERV | MNSiS MControl life bit not healthy | BPP103_MContLife_E | C_EVENT | BPP103 | Class_Equipment | BR4_Cluster1 | BR4.UTILITIES.WATER.WBWD.BPP103_104.BPP103
BR4_Tags | BPP103_MNSiSMainCont_A | ROM Sprays Pump 103 | MNSiS Main Contactor Faulted Trip | BPP103_MNSiSMainCont_A | CAT_P3 | WBWD-1750B012 | PRIV_ALARMACK | A_P1_SERV | MNSiS Main Contactor Faulted Trip | BPP103_MNSiSMainCont_A | C_LOPRI | BPP103 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBWD.BPP103_104.BPP103
BR4_Tags | BPP103_MNSiSOK_A | ROM Sprays Pump 103 | MCC Starter/Motor Electrical Fault Trip | BPP103_MNSiSOK_A | CAT_P2 | WBWD-1750B012 | PRIV_ALARMACK | A_P1_SERV | MCC Starter/Motor Electrical Fault Trip | BPP103_MNSiSOK_A | C_HIPRI | BPP103 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBWD.BPP103_104.BPP103
BR4_Tags | BPP103_MNSiSTrip_E | ROM Sprays Pump 103 | MNSiS General trip alarm | BPP103_MNSiSTrip_E | CAT_EVENT | WBWD-1750B012 | PRIV_ALARMACK | A_P1_SERV | MNSiS General trip alarm | BPP103_MNSiSTrip_E | C_EVENT | BPP103 | Class_Equipment | BR4_Cluster1 | BR4.UTILITIES.WATER.WBWD.BPP103_104.BPP103
BR4_Tags | BPP103_MNSiSWarning_E | ROM Sprays Pump 103 | MNSiS General warning alarm | BPP103_MNSiSWarning_E | CAT_EVENT | WBWD-1750B012 | PRIV_ALARMACK | A_P1_SERV | MNSiS General warning alarm | BPP103_MNSiSWarning_E | C_EVENT | BPP103 | Class_Equipment | BR4_Cluster1 | BR4.UTILITIES.WATER.WBWD.BPP103_104.BPP103
BR4_Tags | BPP103_MStartComms_E | ROM Sprays Pump 103 | MNSiS Power module comms error | BPP103_MStartComms_E | CAT_EVENT | WBWD-1750B012 | PRIV_ALARMACK | A_P1_SERV | MNSiS Power module comms error | BPP103_MStartComms_E | C_EVENT | BPP103 | Class_Equipment | BR4_Cluster1 | BR4.UTILITIES.WATER.WBWD.BPP103_104.BPP103
BR4_Tags | BPP103_MStartID_E | ROM Sprays Pump 103 | MNSiS Power module ID error | BPP103_MStartID_E | CAT_EVENT | WBWD-1750B012 | PRIV_ALARMACK | A_P1_SERV | MNSiS Power module ID error | BPP103_MStartID_E | C_EVENT | BPP103 | Class_Equipment | BR4_Cluster1 | BR4.UTILITIES.WATER.WBWD.BPP103_104.BPP103
BR4_Tags | BPP103_NoLoad_E | ROM Sprays Pump 103 | MNSiS No load trip level reached | BPP103_NoLoad_E | CAT_EVENT | WBWD-1750B012 | PRIV_ALARMACK | A_P1_SERV | MNSiS No load trip level reached | BPP103_NoLoad_E | C_EVENT | BPP103 | Class_Equipment | BR4_Cluster1 | BR4.UTILITIES.WATER.WBWD.BPP103_104.BPP103
BR4_Tags | BPP103_PrmStg1_A | ROM Sprays Pump Priming Seq | Required Drives and Valves Not Healthy Trip | BPP103_PrmStg1_A | CAT_P3 | WBWD-1750B012 | PRIV_ALARMACK | A_P1_SERV | Required Drives and Valves Not Healthy | BPP103_PrmStg1_A | C_LOPRI | BPP103YV01 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBWD.BPP103_104.BPP103
BR4_Tags | BPP103_PrmStg2_A | ROM Sprays Pump Priming Seq | Required Drives and Valves Faulted Trip | BPP103_PrmStg2_A | CAT_P3 | WBWD-1750B012 | PRIV_ALARMACK | A_P1_SERV | Required Drives and Valves Fault | BPP103_PrmStg2_A | C_LOPRI | BPP103YV01 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBWD.BPP103_104.BPP103
BR4_Tags | BPP103_PrmStg3_A | ROM Sprays Pump Priming Seq | Stage 3 Start Pressure Low Trip | BPP103_PrmStg3_A | CAT_P3 | WBWD-1750B012 | PRIV_ALARMACK | A_P1_SERV | Min Pressure for Pump Start Not Reached | BPP103_PrmStg3_A | C_LOPRI | BPP103YV01 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBWD.BPP103_104.BPP103
BR4_Tags | BPP103_PrmStg4_A | ROM Sprays Pump Priming Seq | Stage 4 Operating Pressure Low Trip | BPP103_PrmStg4_A | CAT_P3 | WBWD-1750B012 | PRIV_ALARMACK | A_P1_SERV | Operating Press Not Reached Priming Failed | BPP103_PrmStg4_A | C_LOPRI | BPP103YV01 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBWD.BPP103_104.BPP103
BR4_Tags | BPP103_PrmStg6_A | ROM Sprays Pump Priming Seq | Stage 6 Operating Pressure Low Trip | BPP103_PrmStg6_A | CAT_P3 | WBWD-1750B012 | PRIV_ALARMACK | A_P1_SERV | Operating Press Not Reached Priming Failed | BPP103_PrmStg6_A | C_LOPRI | BPP103YV01 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBWD.BPP103_104.BPP103
BR4_Tags | BPP103_PTCFlt_E | ROM Sprays Pump 103 | MNSiS PTC trip | BPP103_PTCFlt_E | CAT_EVENT | WBWD-1750B012 | PRIV_ALARMACK | A_P1_SERV | MNSiS PTC trip | BPP103_PTCFlt_E | C_EVENT | BPP103 | Class_Equipment | BR4_Cluster1 | BR4.UTILITIES.WATER.WBWD.BPP103_104.BPP103
BR4_Tags | BPP103_RevCls_E | ROM Sprays Pump 103 | MNSiS Reverse contractor failed to close | BPP103_RevCls_E | CAT_EVENT | WBWD-1750B012 | PRIV_ALARMACK | A_P1_SERV | MNSiS Reverse contractor failed to close | BPP103_RevCls_E | C_EVENT | BPP103 | Class_Equipment | BR4_Cluster1 | BR4.UTILITIES.WATER.WBWD.BPP103_104.BPP103
BR4_Tags | BPP103_RunFlt1_E | ROM Sprays Pump 103 | MNSiS Motor still running fault | BPP103_RunFlt1_E | CAT_EVENT | WBWD-1750B012 | PRIV_ALARMACK | A_P1_SERV | MNSiS Motor still running fault | BPP103_RunFlt1_E | C_EVENT | BPP103 | Class_Equipment | BR4_Cluster1 | BR4.UTILITIES.WATER.WBWD.BPP103_104.BPP103
BR4_Tags | BPP103_RunFlt2_E | ROM Sprays Pump 103 | MNSiS Contactor welded | BPP103_RunFlt2_E | CAT_EVENT | WBWD-1750B012 | PRIV_ALARMACK | A_P1_SERV | MNSiS Contactor welded | BPP103_RunFlt2_E | C_EVENT | BPP103 | Class_Equipment | BR4_Cluster1 | BR4.UTILITIES.WATER.WBWD.BPP103_104.BPP103
BR4_Tags | BPP103_RunFlt3_E | ROM Sprays Pump 103 | MNSiS Motor not running fault | BPP103_RunFlt3_E | CAT_EVENT | WBWD-1750B012 | PRIV_ALARMACK | A_P1_SERV | MNSiS Motor not running fault | BPP103_RunFlt3_E | C_EVENT | BPP103 | Class_Equipment | BR4_Cluster1 | BR4.UTILITIES.WATER.WBWD.BPP103_104.BPP103
BR4_Tags | BPP103_Stall_E | ROM Sprays Pump 103 | MNSiS Motor stall trip level reached | BPP103_Stall_E | CAT_EVENT | WBWD-1750B012 | PRIV_ALARMACK | A_P1_SERV | MNSiS Motor stall trip level reached | BPP103_Stall_E | C_EVENT | BPP103 | Class_Equipment | BR4_Cluster1 | BR4.UTILITIES.WATER.WBWD.BPP103_104.BPP103
BR4_Tags | BPP103_SttLmt_E | ROM Sprays Pump 103 | MNSiS Starting limitation trip | BPP103_SttLmt_E | CAT_EVENT | WBWD-1750B012 | PRIV_ALARMACK | A_P1_SERV | MNSiS Starting limitation trip | BPP103_SttLmt_E | C_EVENT | BPP103 | Class_Equipment | BR4_Cluster1 | BR4.UTILITIES.WATER.WBWD.BPP103_104.BPP103
BR4_Tags | BPP103_TOL_E | ROM Sprays Pump 103 | MNSiS Thermal overload fault | BPP103_TOL_E | CAT_EVENT | WBWD-1750B012 | PRIV_ALARMACK | A_P1_SERV | MNSiS Thermal overload fault | BPP103_TOL_E | C_EVENT | BPP103 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBWD.BPP103_104.BPP103
BR4_Tags | BPP103_Underload_E | ROM Sprays Pump 103 | MNSiS Under load trip level reached | BPP103_Underload_E | CAT_EVENT | WBWD-1750B012 | PRIV_ALARMACK | A_P1_SERV | MNSiS Under load trip level reached | BPP103_Underload_E | C_EVENT | BPP103 | Class_Equipment | BR4_Cluster1 | BR4.UTILITIES.WATER.WBWD.BPP103_104.BPP103
BR4_Tags | BPP103_VSDACS800Temp_E | ROM Sprays Pump 103 | VSD Drive IGBT temperature is excessive | BPP103_VSDACS800Temp_E | CAT_EVENT | WBWD-1750B012 | PRIV_ALARMACK | A_P1_SERV | VSD Drive IGBT temperature is excessive | BPP103_VSDACS800Temp_E | C_EVENT | BPP103 | Class_Equipment | BR4_Cluster1 | BR4.UTILITIES.WATER.WBWD.BPP103_104.BPP103.VSD
BR4_Tags | BPP103_VSDAILow_E | ROM Sprays Pump 103 | VSD Analogue control signal below min | BPP103_VSDAILow_E | CAT_EVENT | WBWD-1750B012 | PRIV_ALARMACK | A_P1_SERV | VSD Analogue control signal below min | BPP103_VSDAILow_E | C_EVENT | BPP103 | Class_Equipment | BR4_Cluster1 | BR4.UTILITIES.WATER.WBWD.BPP103_104.BPP103.VSD
BR4_Tags | BPP103_VSDBCOverheat_E | ROM Sprays Pump 103 | VSD Brake chopper overload | BPP103_VSDBCOverheat_E | CAT_EVENT | WBWD-1750B012 | PRIV_ALARMACK | A_P1_SERV | VSD Brake chopper overload | BPP103_VSDBCOverheat_E | C_EVENT | BPP103 | Class_Equipment | BR4_Cluster1 | BR4.UTILITIES.WATER.WBWD.BPP103_104.BPP103.VSD
BR4_Tags | BPP103_VSDBCShortCircuit_E | ROM Sprays Pump 103 | VSD SC in brake chopper IGBTs | BPP103_VSDBCShortCircuit_E | CAT_EVENT | WBWD-1750B012 | PRIV_ALARMACK | A_P1_SERV | VSD SC in brake chopper IGBTs | BPP103_VSDBCShortCircuit_E | C_EVENT | BPP103 | Class_Equipment | BR4_Cluster1 | BR4.UTILITIES.WATER.WBWD.BPP103_104.BPP103.VSD
BR4_Tags | BPP103_VSDBrakeAckn_E | ROM Sprays Pump 103 | VSD Brake ack signal incorrect | BPP103_VSDBrakeAckn_E | CAT_EVENT | WBWD-1750B012 | PRIV_ALARMACK | A_P1_SERV | VSD Brake ack signal incorrect | BPP103_VSDBrakeAckn_E | C_EVENT | BPP103 | Class_Equipment | BR4_Cluster1 | BR4.UTILITIES.WATER.WBWD.BPP103_104.BPP103.VSD
BR4_Tags | BPP103_VSDBRBroken_E | ROM Sprays Pump 103 | VSD Brake resistor disconnected or high | BPP103_VSDBRBroken_E | CAT_EVENT | WBWD-1750B012 | PRIV_ALARMACK | A_P1_SERV | VSD Brake resistor disconnected or high | BPP103_VSDBRBroken_E | C_EVENT | BPP103 | Class_Equipment | BR4_Cluster1 | BR4.UTILITIES.WATER.WBWD.BPP103_104.BPP103.VSD
BR4_Tags | BPP103_VSDBROverheat_E | ROM Sprays Pump 103 | VSD Brake resistor overload | BPP103_VSDBROverheat_E | CAT_EVENT | WBWD-1750B012 | PRIV_ALARMACK | A_P1_SERV | VSD Brake resistor overload | BPP103_VSDBROverheat_E | C_EVENT | BPP103 | Class_Equipment | BR4_Cluster1 | BR4.UTILITIES.WATER.WBWD.BPP103_104.BPP103.VSD
BR4_Tags | BPP103_VSDBRWiring_E | ROM Sprays Pump 103 | VSD Wrong connection of brake resistor | BPP103_VSDBRWiring_E | CAT_EVENT | WBWD-1750B012 | PRIV_ALARMACK | A_P1_SERV | VSD Wrong connection of brake resistor | BPP103_VSDBRWiring_E | C_EVENT | BPP103 | Class_Equipment | BR4_Cluster1 | BR4.UTILITIES.WATER.WBWD.BPP103_104.BPP103.VSD
BR4_Tags | BPP103_VSDChokeOtemp_E | ROM Sprays Pump 103 | VSD Excess temp ofDrive output filter | BPP103_VSDChokeOtemp_E | CAT_EVENT | WBWD-1750B012 | PRIV_ALARMACK | A_P1_SERV | VSD Excess temp ofDrive output filter | BPP103_VSDChokeOtemp_E | C_EVENT | BPP103 | Class_Equipment | BR4_Cluster1 | BR4.UTILITIES.WATER.WBWD.BPP103_104.BPP103.VSD
BR4_Tags | BPP103_VSDCommModule_E | ROM Sprays Pump 103 | VSD Comms fault btwnDrive and master | BPP103_VSDCommModule_E | CAT_EVENT | WBWD-1750B012 | PRIV_ALARMACK | A_P1_SERV | VSD Comms fault btwnDrive and master | BPP103_VSDCommModule_E | C_EVENT | BPP103 | Class_Equipment | BR4_Cluster1 | BR4.UTILITIES.WATER.WBWD.BPP103_104.BPP103.VSD
BR4_Tags | BPP103_VSDCommsOK_A | ROM Sprays Pump 103 | VSD Communications Faulted Trip | BPP103_VSDCommsOK_A | CAT_P3 | WBWD-1750B012 | PRIV_ALARMACK | A_P1_SERV | VSD Communications Faulted Trip | BPP103_VSDCommsOK_A | C_LOPRI | BPP103 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBWD.BPP103_104.BPP103.VSD
BR4_Tags | BPP103_VSDCtrlBTemp_E | ROM Sprays Pump 103 | VSD Control board temp is above 88 degC | BPP103_VSDCtrlBTemp_E | CAT_EVENT | WBWD-1750B012 | PRIV_ALARMACK | A_P1_SERV | VSD Control board temp is above 88 degC | BPP103_VSDCtrlBTemp_E | C_EVENT | BPP103 | Class_Equipment | BR4_Cluster1 | BR4.UTILITIES.WATER.WBWD.BPP103_104.BPP103.VSD
BR4_Tags | BPP103_VSDDCOvervolt_E | ROM Sprays Pump 103 | VSD Excess interm circuit DC voltage | BPP103_VSDDCOvervolt_E | CAT_EVENT | WBWD-1750B012 | PRIV_ALARMACK | A_P1_SERV | VSD Excess interm circuit DC voltage | BPP103_VSDDCOvervolt_E | C_EVENT | BPP103 | Class_Equipment | BR4_Cluster1 | BR4.UTILITIES.WATER.WBWD.BPP103_104.BPP103.VSD
BR4_Tags | BPP103_VSDDCUndervolt_E | ROM Sprays Pump 103 | VSD Interm circuit DC volts insufficient | BPP103_VSDDCUndervolt_E | CAT_EVENT | WBWD-1750B012 | PRIV_ALARMACK | A_P1_SERV | VSD Interm circuit DC volts insufficient | BPP103_VSDDCUndervolt_E | C_EVENT | BPP103 | Class_Equipment | BR4_Cluster1 | BR4.UTILITIES.WATER.WBWD.BPP103_104.BPP103.VSD
BR4_Tags | BPP103_VSDEarthFault_E | ROM Sprays Pump 103 | VSD Drive has detected an earth fault | BPP103_VSDEarthFault_E | CAT_EVENT | WBWD-1750B012 | PRIV_ALARMACK | A_P1_SERV | VSD Drive has detected an earth fault | BPP103_VSDEarthFault_E | C_EVENT | BPP103 | Class_Equipment | BR4_Cluster1 | BR4.UTILITIES.WATER.WBWD.BPP103_104.BPP103.VSD
BR4_Tags | BPP103_VSDEncoderErr_E | ROM Sprays Pump 103 | VSD Pulse encoder communication fault | BPP103_VSDEncoderErr_E | CAT_EVENT | WBWD-1750B012 | PRIV_ALARMACK | A_P1_SERV | VSD Pulse encoder communication fault | BPP103_VSDEncoderErr_E | C_EVENT | BPP103 | Class_Equipment | BR4_Cluster1 | BR4.UTILITIES.WATER.WBWD.BPP103_104.BPP103.VSD
BR4_Tags | BPP103_VSDExternalFault_E | ROM Sprays Pump 103 | VSD Fault in external device | BPP103_VSDExternalFault_E | CAT_EVENT | WBWD-1750B012 | PRIV_ALARMACK | A_P1_SERV | VSD Fault in external device | BPP103_VSDExternalFault_E | C_EVENT | BPP103 | Class_Equipment | BR4_Cluster1 | BR4.UTILITIES.WATER.WBWD.BPP103_104.BPP103.VSD
BR4_Tags | BPP103_VSDFlt_A | ROM Sprays Pump 103 | VSD Fault Trip | BPP103_VSDFlt_A | CAT_P2 | WBWD-1750B012 | PRIV_ALARMACK | A_P1_SERV | VSD Fault Trip | BPP103_VSDFlt_A | C_HIPRI | BPP103 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBWD.BPP103_104.BPP103.VSD
BR4_Tags | BPP103_VSDInChokeTemp_E | ROM Sprays Pump 103 | VSD Excess input choke temp | BPP103_VSDInChokeTemp_E | CAT_EVENT | WBWD-1750B012 | PRIV_ALARMACK | A_P1_SERV | VSD Excess input choke temp | BPP103_VSDInChokeTemp_E | C_EVENT | BPP103 | Class_Equipment | BR4_Cluster1 | BR4.UTILITIES.WATER.WBWD.BPP103_104.BPP103.VSD
BR4_Tags | BPP103_VSDIntConfig_E | ROM Sprays Pump 103 | VSD Number of inverter modules incorrect | BPP103_VSDIntConfig_E | CAT_EVENT | WBWD-1750B012 | PRIV_ALARMACK | A_P1_SERV | VSD Number of inverter modules incorrect | BPP103_VSDIntConfig_E | C_EVENT | BPP103 | Class_Equipment | BR4_Cluster1 | BR4.UTILITIES.WATER.WBWD.BPP103_104.BPP103.VSD
BR4_Tags | BPP103_VSDINVDisabled_E | ROM Sprays Pump 103 | VSD Optional DC switch has opened | BPP103_VSDINVDisabled_E | CAT_EVENT | WBWD-1750B012 | PRIV_ALARMACK | A_P1_SERV | VSD Optional DC switch has opened | BPP103_VSDINVDisabled_E | C_EVENT | BPP103 | Class_Equipment | BR4_Cluster1 | BR4.UTILITIES.WATER.WBWD.BPP103_104.BPP103.VSD
BR4_Tags | BPP103_VSDInvOverTemp_E | ROM Sprays Pump 103 | VSD Converter module temp excessive | BPP103_VSDInvOverTemp_E | CAT_EVENT | WBWD-1750B012 | PRIV_ALARMACK | A_P1_SERV | VSD Converter module temp excessive | BPP103_VSDInvOverTemp_E | C_EVENT | BPP103 | Class_Equipment | BR4_Cluster1 | BR4.UTILITIES.WATER.WBWD.BPP103_104.BPP103.VSD
BR4_Tags | BPP103_VSDIOComm_E | ROM Sprays Pump 103 | VSD Communication error on control board | BPP103_VSDIOComm_E | CAT_EVENT | WBWD-1750B012 | PRIV_ALARMACK | A_P1_SERV | VSD Communication error on control board | BPP103_VSDIOComm_E | C_EVENT | BPP103 | Class_Equipment | BR4_Cluster1 | BR4.UTILITIES.WATER.WBWD.BPP103_104.BPP103.VSD
BR4_Tags | BPP103_VSDMotor1Temp_E | ROM Sprays Pump 103 | VSD Motor temp1 excess | BPP103_VSDMotor1Temp_E | CAT_EVENT | WBWD-1750B012 | PRIV_ALARMACK | A_P1_SERV | VSD Motor temp1 excess | BPP103_VSDMotor1Temp_E | C_EVENT | BPP103 | Class_Equipment | BR4_Cluster1 | BR4.UTILITIES.WATER.WBWD.BPP103_104.BPP103.VSD
BR4_Tags | BPP103_VSDMotor2Temp_E | ROM Sprays Pump 103 | VSD Motor temperature 2 excess | BPP103_VSDMotor2Temp_E | CAT_EVENT | WBWD-1750B012 | PRIV_ALARMACK | A_P1_SERV | VSD Motor temperature 2 excess | BPP103_VSDMotor2Temp_E | C_EVENT | BPP103 | Class_Equipment | BR4_Cluster1 | BR4.UTILITIES.WATER.WBWD.BPP103_104.BPP103.VSD
BR4_Tags | BPP103_VSDMotorPhase_E | ROM Sprays Pump 103 | VSD Motor phase lost | BPP103_VSDMotorPhase_E | CAT_EVENT | WBWD-1750B012 | PRIV_ALARMACK | A_P1_SERV | VSD Motor phase lost | BPP103_VSDMotorPhase_E | C_EVENT | BPP103 | Class_Equipment | BR4_Cluster1 | BR4.UTILITIES.WATER.WBWD.BPP103_104.BPP103.VSD
BR4_Tags | BPP103_VSDMotorStall_E | ROM Sprays Pump 103 | VSD Motor is operating in stall region | BPP103_VSDMotorStall_E | CAT_EVENT | WBWD-1750B012 | PRIV_ALARMACK | A_P1_SERV | VSD Motor is operating in stall region | BPP103_VSDMotorStall_E | C_EVENT | BPP103 | Class_Equipment | BR4_Cluster1 | BR4.UTILITIES.WATER.WBWD.BPP103_104.BPP103.VSD
BR4_Tags | BPP103_VSDMotorTemp_E | ROM Sprays Pump 103 | VSD Motor temperature high | BPP103_VSDMotorTemp_E | CAT_EVENT | WBWD-1750B012 | PRIV_ALARMACK | A_P1_SERV | VSD Motor temperature high | BPP103_VSDMotorTemp_E | C_EVENT | BPP103 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBWD.BPP103_104.BPP103.VSD
BR4_Tags | BPP103_VSDNoMotData_E | ROM Sprays Pump 103 | VSD Motor data is not given | BPP103_VSDNoMotData_E | CAT_EVENT | WBWD-1750B012 | PRIV_ALARMACK | A_P1_SERV | VSD Motor data is not given | BPP103_VSDNoMotData_E | C_EVENT | BPP103 | Class_Equipment | BR4_Cluster1 | BR4.UTILITIES.WATER.WBWD.BPP103_104.BPP103.VSD
BR4_Tags | BPP103_VSDOverCurrent_E | ROM Sprays Pump 103 | VSD Output current exceeds trip limit | BPP103_VSDOverCurrent_E | CAT_EVENT | WBWD-1750B012 | PRIV_ALARMACK | A_P1_SERV | VSD Output current exceeds trip limit | BPP103_VSDOverCurrent_E | C_EVENT | BPP103 | Class_Equipment | BR4_Cluster1 | BR4.UTILITIES.WATER.WBWD.BPP103_104.BPP103.VSD
BR4_Tags | BPP103_VSDOverfreq_E | ROM Sprays Pump 103 | VSD Motor turning faster allowed speed | BPP103_VSDOverfreq_E | CAT_EVENT | WBWD-1750B012 | PRIV_ALARMACK | A_P1_SERV | VSD Motor turning faster allowed speed | BPP103_VSDOverfreq_E | C_EVENT | BPP103 | Class_Equipment | BR4_Cluster1 | BR4.UTILITIES.WATER.WBWD.BPP103_104.BPP103.VSD
BR4_Tags | BPP103_VSDOverSWFreq_E | ROM Sprays Pump 103 | VSD Switching frequency is too high | BPP103_VSDOverSWFreq_E | CAT_EVENT | WBWD-1750B012 | PRIV_ALARMACK | A_P1_SERV | VSD Switching frequency is too high | BPP103_VSDOverSWFreq_E | C_EVENT | BPP103 | Class_Equipment | BR4_Cluster1 | BR4.UTILITIES.WATER.WBWD.BPP103_104.BPP103.VSD
BR4_Tags | BPP103_VSDPanelLoss_E | ROM Sprays Pump 103 | VSD Control panel has ceased comms | BPP103_VSDPanelLoss_E | CAT_EVENT | WBWD-1750B012 | PRIV_ALARMACK | A_P1_SERV | VSD Control panel has ceased comms | BPP103_VSDPanelLoss_E | C_EVENT | BPP103 | Class_Equipment | BR4_Cluster1 | BR4.UTILITIES.WATER.WBWD.BPP103_104.BPP103.VSD
BR4_Tags | BPP103_VSDPowerInvFail_E | ROM Sprays Pump 103 | VSD INT board fail in inverter unit | BPP103_VSDPowerInvFail_E | CAT_EVENT | WBWD-1750B012 | PRIV_ALARMACK | A_P1_SERV | VSD INT board fail in inverter unit | BPP103_VSDPowerInvFail_E | C_EVENT | BPP103 | Class_Equipment | BR4_Cluster1 | BR4.UTILITIES.WATER.WBWD.BPP103_104.BPP103.VSD
BR4_Tags | BPP103_VSDPPCCLink_E | ROM Sprays Pump 103 | VSD Fibre optic link to INT board fault | BPP103_VSDPPCCLink_E | CAT_EVENT | WBWD-1750B012 | PRIV_ALARMACK | A_P1_SERV | VSD Fibre optic link to INT board fault | BPP103_VSDPPCCLink_E | C_EVENT | BPP103 | Class_Equipment | BR4_Cluster1 | BR4.UTILITIES.WATER.WBWD.BPP103_104.BPP103.VSD
BR4_Tags | BPP103_VSDPPOverload_E | ROM Sprays Pump 103 | VSD Excess IGBT junction to case temp | BPP103_VSDPPOverload_E | CAT_EVENT | WBWD-1750B012 | PRIV_ALARMACK | A_P1_SERV | VSD Excess IGBT junction to case temp | BPP103_VSDPPOverload_E | C_EVENT | BPP103 | Class_Equipment | BR4_Cluster1 | BR4.UTILITIES.WATER.WBWD.BPP103_104.BPP103.VSD
BR4_Tags | BPP103_VSDRdy_A | ROM Sprays Pump 103 | VSD Not Ready Trip | BPP103_VSDRdy_A | CAT_P3 | WBWD-1750B012 | PRIV_ALARMACK | A_P1_SERV | VSD Not Ready Trip | BPP103_VSDRdy_A | C_LOPRI | BPP103 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBWD.BPP103_104.BPP103.VSD
BR4_Tags | BPP103_VSDRunDisabled_E | ROM Sprays Pump 103 | VSD No Run enable signal received | BPP103_VSDRunDisabled_E | CAT_EVENT | WBWD-1750B012 | PRIV_ALARMACK | A_P1_SERV | VSD No Run enable signal received | BPP103_VSDRunDisabled_E | C_EVENT | BPP103 | Class_Equipment | BR4_Cluster1 | BR4.UTILITIES.WATER.WBWD.BPP103_104.BPP103.VSD
BR4_Tags | BPP103_VSDShortCirc_E | ROM Sprays Pump 103 | VSD Shrt Cct in motor cables or motor | BPP103_VSDShortCirc_E | CAT_EVENT | WBWD-1750B012 | PRIV_ALARMACK | A_P1_SERV | VSD Shrt Cct in motor cables or motor | BPP103_VSDShortCirc_E | C_EVENT | BPP103 | Class_Equipment | BR4_Cluster1 | BR4.UTILITIES.WATER.WBWD.BPP103_104.BPP103.VSD
BR4_Tags | BPP103_VSDSupplyPhase_E | ROM Sprays Pump 103 | VSD Intermcircuit DC volts oscillating | BPP103_VSDSupplyPhase_E | CAT_EVENT | WBWD-1750B012 | PRIV_ALARMACK | A_P1_SERV | VSD Intermcircuit DC volts oscillating | BPP103_VSDSupplyPhase_E | C_EVENT | BPP103 | Class_Equipment | BR4_Cluster1 | BR4.UTILITIES.WATER.WBWD.BPP103_104.BPP103.VSD
BR4_Tags | BPP103_VSDSystemFault_E | ROM Sprays Pump 103 | VSD Active system fault word alarm | BPP103_VSDSystemFault_E | CAT_EVENT | WBWD-1750B012 | PRIV_ALARMACK | A_P1_SERV | VSD Active system fault word alarm | BPP103_VSDSystemFault_E | C_EVENT | BPP103 | Class_Equipment | BR4_Cluster1 | BR4.UTILITIES.WATER.WBWD.BPP103_104.BPP103.VSD
BR4_Tags | BPP103_VSDTempDif_E | ROM Sprays Pump 103 | VSD Excess temp diff in inverter modules | BPP103_VSDTempDif_E | CAT_EVENT | WBWD-1750B012 | PRIV_ALARMACK | A_P1_SERV | VSD Excess temp diff in inverter modules | BPP103_VSDTempDif_E | C_EVENT | BPP103 | Class_Equipment | BR4_Cluster1 | BR4.UTILITIES.WATER.WBWD.BPP103_104.BPP103.VSD
BR4_Tags | BPP103_VSDThermistor_E | ROM Sprays Pump 103 | VSD Thermal protect thermistor in excess | BPP103_VSDThermistor_E | CAT_EVENT | WBWD-1750B012 | PRIV_ALARMACK | A_P1_SERV | VSD Thermal protect thermistor in excess | BPP103_VSDThermistor_E | C_EVENT | BPP103 | Class_Equipment | BR4_Cluster1 | BR4.UTILITIES.WATER.WBWD.BPP103_104.BPP103.VSD
BR4_Tags | BPP103_VSDUnderload_E | ROM Sprays Pump 103 | VSD Motor load is too low due | BPP103_VSDUnderload_E | CAT_EVENT | WBWD-1750B012 | PRIV_ALARMACK | A_P1_SERV | VSD Motor load is too low due | BPP103_VSDUnderload_E | C_EVENT | BPP103 | Class_Equipment | BR4_Cluster1 | BR4.UTILITIES.WATER.WBWD.BPP103_104.BPP103.VSD
BR4_Tags | BPP103_VSDUserLCurve_E | ROM Sprays Pump 103 | VSD Integr current exceeded load curve | BPP103_VSDUserLCurve_E | CAT_EVENT | WBWD-1750B012 | PRIV_ALARMACK | A_P1_SERV | VSD Integr current exceeded load curve | BPP103_VSDUserLCurve_E | C_EVENT | BPP103 | Class_Equipment | BR4_Cluster1 | BR4.UTILITIES.WATER.WBWD.BPP103_104.BPP103.VSD
BR4_Tags | BPP103DCOK_A | ROM Sprays Pump 103 | 24VDC Power Supply Trip | BPP103DCOK_A | CAT_P3 | WBWD-1750B012 | PRIV_ALARMACK | A_P1_SERV | 24 VDC Supply OK | BPP103DCOK_A | C_LOPRI | BPP103 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBWD.BPP103_104.BPP103
BR4_Tags | BPP103FN01_Auto_A | ROM Sprays Pump Motor Fan | Not Group Started In Auto Trip | BPP103FN01_Auto_A | CAT_P3 | WBWD-1750B012 | PRIV_ALARMACK | A_P1_SERV | Fan Not Group Started In Auto | BPP103FN01_Auto_A | C_LOPRI | BPP103FN01 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBWD.BPP103_104.BPP103.FN01
BR4_Tags | BPP103FN01_MainCont_A | ROM Sprays Pump Motor Fan | Main Contactor Faulted Trip | BPP103FN01_MainCont_A | CAT_P3 | WBWD-1750B012 | PRIV_ALARMACK | A_P1_SERV | Main Contactor | BPP103FN01_MainCont_A | C_LOPRI | BPP103FN01 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBWD.BPP103_104.BPP103.FN01
BR4_Tags | BPP103FN01TOL01_A | ROM Sprays Pump Motor Fan | Thermal Overload Trip | BPP103FN01TOL01_A | CAT_P3 | WBWD-1750B012 | PRIV_ALARMACK | A_P1_SERV | Thermal Overload Trip | BPP103FN01TOL01_A | C_LOPRI | BPP103FN01 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBWD.BPP103_104.BPP103.FN01
BR4_Tags | BPP103FT01_Lo_A | ROM Sprays Pump Flow | Blocked/Nozzle Worn | BPP103FT01_Lo_A | CAT_P3 | WBWD-1750B012 | PRIV_ALARMACK | A_P1_SERV | Blocked/Nozzle Worn | BPP103FT01_Lo_A | C_LOPRI | BPP103FT01 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBWD.BPP103_104.BPP103FT01
BR4_Tags | BPP103FT01_LoLo_A | ROM Sprays Pump Flow | Flow Low Low Trip | BPP103FT01_LoLo_A | CAT_P3 | WBWD-1750B012 | PRIV_ALARMACK | A_P1_SERV | Flow Low Low | BPP103FT01_LoLo_A | C_LOPRI | BPP103FT01 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBWD.BPP103_104.BPP103FT01
BR4_Tags | BPP103FT01DCOK_A | ROM Sprays Pump Flow | 24VDC Power Supply Trip | BPP103FT01DCOK_A | CAT_P3 | WBWD-1750B012 | PRIV_ALARMACK | A_P1_SERV | 24VDC Supply OK | BPP103FT01DCOK_A | C_LOPRI | BPP103FT01 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBWD.BPP103_104.BPP103FT01
BR4_Tags | BPP103LOS01_A | ROM Sprays Pump 103 | Lock Off Stop Trip | BPP103LOS01_A | CAT_P1 | WBWD-1750B012 | PRIV_ALARMACK | A_P1_SERV | Lock Off Stop Trip | BPP103LOS01_A | C_LOPRI | BPP103 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBWD.BPP103_104.BPP103.LOS01
BR4_Tags | BPP103PT01_Hi_A | ROM Sprays Pump Pressure | Pressure High | BPP103PT01_Hi_A | CAT_P3 | WBWD-1750B012 | PRIV_ALARMACK | A_P1_SERV | Pressure High | BPP103PT01_Hi_A | C_LOPRI | BPP103PT01 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBWD.BPP103_104.BPP103PT01
BR4_Tags | BPP103PT01_HiHi_A | ROM Sprays Pump Pressure | Pressure High High Trip | BPP103PT01_HiHi_A | CAT_P3 | WBWD-1750B012 | PRIV_ALARMACK | A_P1_SERV | Pressure High High | BPP103PT01_HiHi_A | C_LOPRI | BPP103PT01 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBWD.BPP103_104.BPP103PT01
BR4_Tags | BPP103PT01_Lo_A | ROM Sprays Pump Pressure | Pressure Low Trip | BPP103PT01_Lo_A | CAT_P3 | WBWD-1750B012 | PRIV_ALARMACK | A_P1_SERV | Pressure Low | BPP103PT01_Lo_A | C_LOPRI | BPP103PT01 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBWD.BPP103_104.BPP103PT01
BR4_Tags | BPP103VS01DCOK_A | ROM Sprays Pump 103 | VSD 24VDC Power Supply Trip | BPP103VS01DCOK_A | CAT_P3 | WBWD-1750B012 | PRIV_ALARMACK | A_P1_SERV | VSD 24VDC Power Supply Trip | BPP103VS01DCOK_A | C_LOPRI | BPP103 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBWD.BPP103_104.BPP103
BR4_Tags | BPP103ZS01_LmtFlt_A | ROM Sprays Pump Prim Valve | Opened/Closed Limits Fault Trip | BPP103ZS01_LmtFlt_A | CAT_P3 | WBWD-1750B012 | PRIV_ALARMACK | A_P1_SERV | Limit Switch Fault | BPP103ZS01_LmtFlt_A | C_LOPRI | BPP103YV01 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBWD.BPP103_104.BPP103
BR4_Tags | BPP103ZS01A_A | ROM Sprays Pump Prim Valve | Failed to Open Trip | BPP103ZS01A_A | CAT_P3 | WBWD-1750B012 | PRIV_ALARMACK | A_P1_SERV | Failed to Open | BPP103ZS01A_A | C_LOPRI | BPP103YV01 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBWD.BPP103_104.BPP103
BR4_Tags | BPP103ZS01B_A | ROM Sprays Pump Prim Valve | Failed to Close Trip | BPP103ZS01B_A | CAT_P3 | WBWD-1750B012 | PRIV_ALARMACK | A_P1_SERV | Failed to Close | BPP103ZS01B_A | C_LOPRI | BPP103YV01 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBWD.BPP103_104.BPP103
BR4_Tags | BPP104_ACFlt_E | ROM Sprays Pump 104 | MNSiS AC Control voltage fault | BPP104_ACFlt_E | CAT_EVENT | WBWD-1750B012 | PRIV_ALARMACK | A_P1_SERV | MNSiS AC Control voltage fault | BPP104_ACFlt_E | C_EVENT | BPP104 | Class_Equipment | BR4_Cluster1 | BR4.UTILITIES.WATER.WBWD.BPP103_104.BPP104
BR4_Tags | BPP104_CARemote_E | ROM Sprays Pump 104 | MNSiS Control Access not in remote | BPP104_CARemote_E | CAT_EVENT | WBWD-1750B012 | PRIV_ALARMACK | A_P1_SERV | MNSiS Control Access not in remote | BPP104_CARemote_E | C_EVENT | BPP104 | Class_Equipment | BR4_Cluster1 | BR4.UTILITIES.WATER.WBWD.BPP103_104.BPP104
BR4_Tags | BPP104_DCOK_E | ROM Sprays Pump 104 | MNSiS DC Control voltage fault | BPP104_DCOK_E | CAT_EVENT | WBWD-1750B012 | PRIV_ALARMACK | A_P1_SERV | MNSiS DC Control voltage fault | BPP104_DCOK_E | C_EVENT | BPP104 | Class_Equipment | BR4_Cluster1 | BR4.UTILITIES.WATER.WBWD.BPP103_104.BPP104
BR4_Tags | BPP104_EStop_E | ROM Sprays Pump 104 | MNSiS Emergency stop active | BPP104_EStop_E | CAT_EVENT | WBWD-1750B012 | PRIV_ALARMACK | A_P1_SERV | MNSiS Emergency stop active | BPP104_EStop_E | C_EVENT | BPP104 | Class_Equipment | BR4_Cluster1 | BR4.UTILITIES.WATER.WBWD.BPP103_104.BPP104
BR4_Tags | BPP104_FailSafe_E | ROM Sprays Pump 104 | MNSiS MControl in fail safe mode | BPP104_FailSafe_E | CAT_EVENT | WBWD-1750B012 | PRIV_ALARMACK | A_P1_SERV | MNSiS MControl in fail safe mode | BPP104_FailSafe_E | C_EVENT | BPP104 | Class_Equipment | BR4_Cluster1 | BR4.UTILITIES.WATER.WBWD.BPP103_104.BPP104
BR4_Tags | BPP104_FwdCls_E | ROM Sprays Pump 104 | MNSiS Forward contractor failed to close | BPP104_FwdCls_E | CAT_EVENT | WBWD-1750B012 | PRIV_ALARMACK | A_P1_SERV | MNSiS Forward contractor failed to close | BPP104_FwdCls_E | C_EVENT | BPP104 | Class_Equipment | BR4_Cluster1 | BR4.UTILITIES.WATER.WBWD.BPP103_104.BPP104
BR4_Tags | BPP104_IRFHard_E | ROM Sprays Pump 104 | MNSiS Internal relay h/w fault trip | BPP104_IRFHard_E | CAT_EVENT | WBWD-1750B012 | PRIV_ALARMACK | A_P1_SERV | MNSiS Internal relay h/w fault trip | BPP104_IRFHard_E | C_EVENT | BPP104 | Class_Equipment | BR4_Cluster1 | BR4.UTILITIES.WATER.WBWD.BPP103_104.BPP104
BR4_Tags | BPP104_IRFSoft_E | ROM Sprays Pump 104 | MNSiS Internal relay s/w fault trip | BPP104_IRFSoft_E | CAT_EVENT | WBWD-1750B012 | PRIV_ALARMACK | A_P1_SERV | MNSiS Internal relay s/w fault trip | BPP104_IRFSoft_E | C_EVENT | BPP104 | Class_Equipment | BR4_Cluster1 | BR4.UTILITIES.WATER.WBWD.BPP103_104.BPP104
BR4_Tags | BPP104_IS01Opn_E | ROM Sprays Pump 104 | MNSiS MStart isolated | BPP104_IS01Opn_E | CAT_EVENT | WBWD-1750B012 | PRIV_ALARMACK | A_P1_SERV | MNSiS MStart isolated | BPP104_IS01Opn_E | C_EVENT | BPP104 | Class_Equipment | BR4_Cluster1 | BR4.UTILITIES.WATER.WBWD.BPP103_104.BPP104.IS01
BR4_Tags | BPP104_IS01Test_E | ROM Sprays Pump 104 | MNSiS Isolator in test position | BPP104_IS01Test_E | CAT_EVENT | WBWD-1750B012 | PRIV_ALARMACK | A_P1_SERV | MNSiS Isolator in test position | BPP104_IS01Test_E | C_EVENT | BPP104 | Class_Equipment | BR4_Cluster1 | BR4.UTILITIES.WATER.WBWD.BPP103_104.BPP104.IS01
BR4_Tags | BPP104_MContID_E | ROM Sprays Pump 104 | MNSiS Location supervision trip | BPP104_MContID_E | CAT_EVENT | WBWD-1750B012 | PRIV_ALARMACK | A_P1_SERV | MNSiS Location supervision trip | BPP104_MContID_E | C_EVENT | BPP104 | Class_Equipment | BR4_Cluster1 | BR4.UTILITIES.WATER.WBWD.BPP103_104.BPP104
BR4_Tags | BPP104_MContLife_E | ROM Sprays Pump 104 | MNSiS MControl life bit not healthy | BPP104_MContLife_E | CAT_EVENT | WBWD-1750B012 | PRIV_ALARMACK | A_P1_SERV | MNSiS MControl life bit not healthy | BPP104_MContLife_E | C_EVENT | BPP104 | Class_Equipment | BR4_Cluster1 | BR4.UTILITIES.WATER.WBWD.BPP103_104.BPP104
BR4_Tags | BPP104_MNSiSMainCont_A | ROM Sprays Pump 104 | MNSiS Main Contactor Faulted Trip | BPP104_MNSiSMainCont_A | CAT_P3 | WBWD-1750B012 | PRIV_ALARMACK | A_P1_SERV | MNSiS Main Contactor Faulted Trip | BPP104_MNSiSMainCont_A | C_LOPRI | BPP104 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBWD.BPP103_104.BPP104
BR4_Tags | BPP104_MNSiSOK_A | ROM Sprays Pump 104 | MCC Starter/Motor Electrical Fault Trip | BPP104_MNSiSOK_A | CAT_P2 | WBWD-1750B012 | PRIV_ALARMACK | A_P1_SERV | MCC Starter/Motor Electrical Fault Trip | BPP104_MNSiSOK_A | C_HIPRI | BPP104 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBWD.BPP103_104.BPP104
BR4_Tags | BPP104_MNSiSTrip_E | ROM Sprays Pump 104 | MNSiS General trip alarm | BPP104_MNSiSTrip_E | CAT_EVENT | WBWD-1750B012 | PRIV_ALARMACK | A_P1_SERV | MNSiS General trip alarm | BPP104_MNSiSTrip_E | C_EVENT | BPP104 | Class_Equipment | BR4_Cluster1 | BR4.UTILITIES.WATER.WBWD.BPP103_104.BPP104
BR4_Tags | BPP104_MNSiSWarning_E | ROM Sprays Pump 104 | MNSiS General warning alarm | BPP104_MNSiSWarning_E | CAT_EVENT | WBWD-1750B012 | PRIV_ALARMACK | A_P1_SERV | MNSiS General warning alarm | BPP104_MNSiSWarning_E | C_EVENT | BPP104 | Class_Equipment | BR4_Cluster1 | BR4.UTILITIES.WATER.WBWD.BPP103_104.BPP104
BR4_Tags | BPP104_MStartComms_E | ROM Sprays Pump 104 | MNSiS Power module comms error | BPP104_MStartComms_E | CAT_EVENT | WBWD-1750B012 | PRIV_ALARMACK | A_P1_SERV | MNSiS Power module comms error | BPP104_MStartComms_E | C_EVENT | BPP104 | Class_Equipment | BR4_Cluster1 | BR4.UTILITIES.WATER.WBWD.BPP103_104.BPP104
BR4_Tags | BPP104_MStartID_E | ROM Sprays Pump 104 | MNSiS Power module ID error | BPP104_MStartID_E | CAT_EVENT | WBWD-1750B012 | PRIV_ALARMACK | A_P1_SERV | MNSiS Power module ID error | BPP104_MStartID_E | C_EVENT | BPP104 | Class_Equipment | BR4_Cluster1 | BR4.UTILITIES.WATER.WBWD.BPP103_104.BPP104
BR4_Tags | BPP104_NoLoad_E | ROM Sprays Pump 104 | MNSiS No load trip level reached | BPP104_NoLoad_E | CAT_EVENT | WBWD-1750B012 | PRIV_ALARMACK | A_P1_SERV | MNSiS No load trip level reached | BPP104_NoLoad_E | C_EVENT | BPP104 | Class_Equipment | BR4_Cluster1 | BR4.UTILITIES.WATER.WBWD.BPP103_104.BPP104
BR4_Tags | BPP104_PTCFlt_E | ROM Sprays Pump 104 | MNSiS PTC trip | BPP104_PTCFlt_E | CAT_EVENT | WBWD-1750B012 | PRIV_ALARMACK | A_P1_SERV | MNSiS PTC trip | BPP104_PTCFlt_E | C_EVENT | BPP104 | Class_Equipment | BR4_Cluster1 | BR4.UTILITIES.WATER.WBWD.BPP103_104.BPP104
BR4_Tags | BPP104_RevCls_E | ROM Sprays Pump 104 | MNSiS Reverse contractor failed to close | BPP104_RevCls_E | CAT_EVENT | WBWD-1750B012 | PRIV_ALARMACK | A_P1_SERV | MNSiS Reverse contractor failed to close | BPP104_RevCls_E | C_EVENT | BPP104 | Class_Equipment | BR4_Cluster1 | BR4.UTILITIES.WATER.WBWD.BPP103_104.BPP104
BR4_Tags | BPP104_RunFlt1_E | ROM Sprays Pump 104 | MNSiS Motor still running fault | BPP104_RunFlt1_E | CAT_EVENT | WBWD-1750B012 | PRIV_ALARMACK | A_P1_SERV | MNSiS Motor still running fault | BPP104_RunFlt1_E | C_EVENT | BPP104 | Class_Equipment | BR4_Cluster1 | BR4.UTILITIES.WATER.WBWD.BPP103_104.BPP104
BR4_Tags | BPP104_RunFlt2_E | ROM Sprays Pump 104 | MNSiS Contactor welded | BPP104_RunFlt2_E | CAT_EVENT | WBWD-1750B012 | PRIV_ALARMACK | A_P1_SERV | MNSiS Contactor welded | BPP104_RunFlt2_E | C_EVENT | BPP104 | Class_Equipment | BR4_Cluster1 | BR4.UTILITIES.WATER.WBWD.BPP103_104.BPP104
BR4_Tags | BPP104_RunFlt3_E | ROM Sprays Pump 104 | MNSiS Motor not running fault | BPP104_RunFlt3_E | CAT_EVENT | WBWD-1750B012 | PRIV_ALARMACK | A_P1_SERV | MNSiS Motor not running fault | BPP104_RunFlt3_E | C_EVENT | BPP104 | Class_Equipment | BR4_Cluster1 | BR4.UTILITIES.WATER.WBWD.BPP103_104.BPP104
BR4_Tags | BPP104_Stall_E | ROM Sprays Pump 104 | MNSiS Motor stall trip level reached | BPP104_Stall_E | CAT_EVENT | WBWD-1750B012 | PRIV_ALARMACK | A_P1_SERV | MNSiS Motor stall trip level reached | BPP104_Stall_E | C_EVENT | BPP104 | Class_Equipment | BR4_Cluster1 | BR4.UTILITIES.WATER.WBWD.BPP103_104.BPP104
BR4_Tags | BPP104_SttLmt_E | ROM Sprays Pump 104 | MNSiS Starting limitation trip | BPP104_SttLmt_E | CAT_EVENT | WBWD-1750B012 | PRIV_ALARMACK | A_P1_SERV | MNSiS Starting limitation trip | BPP104_SttLmt_E | C_EVENT | BPP104 | Class_Equipment | BR4_Cluster1 | BR4.UTILITIES.WATER.WBWD.BPP103_104.BPP104
BR4_Tags | BPP104_TOL_E | ROM Sprays Pump 104 | MNSiS Thermal overload fault | BPP104_TOL_E | CAT_EVENT | WBWD-1750B012 | PRIV_ALARMACK | A_P1_SERV | MNSiS Thermal overload fault | BPP104_TOL_E | C_EVENT | BPP104 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBWD.BPP103_104.BPP104
BR4_Tags | BPP104_Underload_E | ROM Sprays Pump 104 | MNSiS Under load trip level reached | BPP104_Underload_E | CAT_EVENT | WBWD-1750B012 | PRIV_ALARMACK | A_P1_SERV | MNSiS Under load trip level reached | BPP104_Underload_E | C_EVENT | BPP104 | Class_Equipment | BR4_Cluster1 | BR4.UTILITIES.WATER.WBWD.BPP103_104.BPP104
BR4_Tags | BPP104_VSDACS800Temp_E | ROM Sprays Pump 104 | VSD Drive IGBT temperature is excessive | BPP104_VSDACS800Temp_E | CAT_EVENT | WBWD-1750B012 | PRIV_ALARMACK | A_P1_SERV | VSD Drive IGBT temperature is excessive | BPP104_VSDACS800Temp_E | C_EVENT | BPP104 | Class_Equipment | BR4_Cluster1 | BR4.UTILITIES.WATER.WBWD.BPP103_104.BPP104.VSD
BR4_Tags | BPP104_VSDAILow_E | ROM Sprays Pump 104 | VSD Analogue control signal below min | BPP104_VSDAILow_E | CAT_EVENT | WBWD-1750B012 | PRIV_ALARMACK | A_P1_SERV | VSD Analogue control signal below min | BPP104_VSDAILow_E | C_EVENT | BPP104 | Class_Equipment | BR4_Cluster1 | BR4.UTILITIES.WATER.WBWD.BPP103_104.BPP104.VSD
BR4_Tags | BPP104_VSDBCOverheat_E | ROM Sprays Pump 104 | VSD Brake chopper overload | BPP104_VSDBCOverheat_E | CAT_EVENT | WBWD-1750B012 | PRIV_ALARMACK | A_P1_SERV | VSD Brake chopper overload | BPP104_VSDBCOverheat_E | C_EVENT | BPP104 | Class_Equipment | BR4_Cluster1 | BR4.UTILITIES.WATER.WBWD.BPP103_104.BPP104.VSD
BR4_Tags | BPP104_VSDBCShortCircuit_E | ROM Sprays Pump 104 | VSD SC in brake chopper IGBTs | BPP104_VSDBCShortCircuit_E | CAT_EVENT | WBWD-1750B012 | PRIV_ALARMACK | A_P1_SERV | VSD SC in brake chopper IGBTs | BPP104_VSDBCShortCircuit_E | C_EVENT | BPP104 | Class_Equipment | BR4_Cluster1 | BR4.UTILITIES.WATER.WBWD.BPP103_104.BPP104.VSD
BR4_Tags | BPP104_VSDBrakeAckn_E | ROM Sprays Pump 104 | VSD Brake ack signal incorrect | BPP104_VSDBrakeAckn_E | CAT_EVENT | WBWD-1750B012 | PRIV_ALARMACK | A_P1_SERV | VSD Brake ack signal incorrect | BPP104_VSDBrakeAckn_E | C_EVENT | BPP104 | Class_Equipment | BR4_Cluster1 | BR4.UTILITIES.WATER.WBWD.BPP103_104.BPP104.VSD
BR4_Tags | BPP104_VSDBRBroken_E | ROM Sprays Pump 104 | VSD Brake resistor disconnected or high | BPP104_VSDBRBroken_E | CAT_EVENT | WBWD-1750B012 | PRIV_ALARMACK | A_P1_SERV | VSD Brake resistor disconnected or high | BPP104_VSDBRBroken_E | C_EVENT | BPP104 | Class_Equipment | BR4_Cluster1 | BR4.UTILITIES.WATER.WBWD.BPP103_104.BPP104.VSD
BR4_Tags | BPP104_VSDBROverheat_E | ROM Sprays Pump 104 | VSD Brake resistor overload | BPP104_VSDBROverheat_E | CAT_EVENT | WBWD-1750B012 | PRIV_ALARMACK | A_P1_SERV | VSD Brake resistor overload | BPP104_VSDBROverheat_E | C_EVENT | BPP104 | Class_Equipment | BR4_Cluster1 | BR4.UTILITIES.WATER.WBWD.BPP103_104.BPP104.VSD
BR4_Tags | BPP104_VSDBRWiring_E | ROM Sprays Pump 104 | VSD Wrong connection of brake resistor | BPP104_VSDBRWiring_E | CAT_EVENT | WBWD-1750B012 | PRIV_ALARMACK | A_P1_SERV | VSD Wrong connection of brake resistor | BPP104_VSDBRWiring_E | C_EVENT | BPP104 | Class_Equipment | BR4_Cluster1 | BR4.UTILITIES.WATER.WBWD.BPP103_104.BPP104.VSD
BR4_Tags | BPP104_VSDChokeOtemp_E | ROM Sprays Pump 104 | VSD Excess temp ofDrive output filter | BPP104_VSDChokeOtemp_E | CAT_EVENT | WBWD-1750B012 | PRIV_ALARMACK | A_P1_SERV | VSD Excess temp ofDrive output filter | BPP104_VSDChokeOtemp_E | C_EVENT | BPP104 | Class_Equipment | BR4_Cluster1 | BR4.UTILITIES.WATER.WBWD.BPP103_104.BPP104.VSD
BR4_Tags | BPP104_VSDCommModule_E | ROM Sprays Pump 104 | VSD Comms fault btwnDrive and master | BPP104_VSDCommModule_E | CAT_EVENT | WBWD-1750B012 | PRIV_ALARMACK | A_P1_SERV | VSD Comms fault btwnDrive and master | BPP104_VSDCommModule_E | C_EVENT | BPP104 | Class_Equipment | BR4_Cluster1 | BR4.UTILITIES.WATER.WBWD.BPP103_104.BPP104.VSD
BR4_Tags | BPP104_VSDCommsOK_A | ROM Sprays Pump 104 | VSD Communications Faulted Trip | BPP104_VSDCommsOK_A | CAT_P3 | WBWD-1750B012 | PRIV_ALARMACK | A_P1_SERV | VSD Communications Faulted Trip | BPP104_VSDCommsOK_A | C_LOPRI | BPP104 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBWD.BPP103_104.BPP104.VSD
BR4_Tags | BPP104_VSDCtrlBTemp_E | ROM Sprays Pump 104 | VSD Control board temp is above 88 degC | BPP104_VSDCtrlBTemp_E | CAT_EVENT | WBWD-1750B012 | PRIV_ALARMACK | A_P1_SERV | VSD Control board temp is above 88 degC | BPP104_VSDCtrlBTemp_E | C_EVENT | BPP104 | Class_Equipment | BR4_Cluster1 | BR4.UTILITIES.WATER.WBWD.BPP103_104.BPP104.VSD
BR4_Tags | BPP104_VSDDCOvervolt_E | ROM Sprays Pump 104 | VSD Excess interm circuit DC voltage | BPP104_VSDDCOvervolt_E | CAT_EVENT | WBWD-1750B012 | PRIV_ALARMACK | A_P1_SERV | VSD Excess interm circuit DC voltage | BPP104_VSDDCOvervolt_E | C_EVENT | BPP104 | Class_Equipment | BR4_Cluster1 | BR4.UTILITIES.WATER.WBWD.BPP103_104.BPP104.VSD
BR4_Tags | BPP104_VSDDCUndervolt_E | ROM Sprays Pump 104 | VSD Interm circuit DC volts insufficient | BPP104_VSDDCUndervolt_E | CAT_EVENT | WBWD-1750B012 | PRIV_ALARMACK | A_P1_SERV | VSD Interm circuit DC volts insufficient | BPP104_VSDDCUndervolt_E | C_EVENT | BPP104 | Class_Equipment | BR4_Cluster1 | BR4.UTILITIES.WATER.WBWD.BPP103_104.BPP104.VSD
BR4_Tags | BPP104_VSDEarthFault_E | ROM Sprays Pump 104 | VSD Drive has detected an earth fault | BPP104_VSDEarthFault_E | CAT_EVENT | WBWD-1750B012 | PRIV_ALARMACK | A_P1_SERV | VSD Drive has detected an earth fault | BPP104_VSDEarthFault_E | C_EVENT | BPP104 | Class_Equipment | BR4_Cluster1 | BR4.UTILITIES.WATER.WBWD.BPP103_104.BPP104.VSD
BR4_Tags | BPP104_VSDEncoderErr_E | ROM Sprays Pump 104 | VSD Pulse encoder communication fault | BPP104_VSDEncoderErr_E | CAT_EVENT | WBWD-1750B012 | PRIV_ALARMACK | A_P1_SERV | VSD Pulse encoder communication fault | BPP104_VSDEncoderErr_E | C_EVENT | BPP104 | Class_Equipment | BR4_Cluster1 | BR4.UTILITIES.WATER.WBWD.BPP103_104.BPP104.VSD
BR4_Tags | BPP104_VSDExternalFault_E | ROM Sprays Pump 104 | VSD Fault in external device | BPP104_VSDExternalFault_E | CAT_EVENT | WBWD-1750B012 | PRIV_ALARMACK | A_P1_SERV | VSD Fault in external device | BPP104_VSDExternalFault_E | C_EVENT | BPP104 | Class_Equipment | BR4_Cluster1 | BR4.UTILITIES.WATER.WBWD.BPP103_104.BPP104.VSD
BR4_Tags | BPP104_VSDFlt_A | ROM Sprays Pump 104 | VSD Fault Trip | BPP104_VSDFlt_A | CAT_P2 | WBWD-1750B012 | PRIV_ALARMACK | A_P1_SERV | VSD Fault Trip | BPP104_VSDFlt_A | C_HIPRI | BPP104 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBWD.BPP103_104.BPP104.VSD
BR4_Tags | BPP104_VSDInChokeTemp_E | ROM Sprays Pump 104 | VSD Excess input choke temp | BPP104_VSDInChokeTemp_E | CAT_EVENT | WBWD-1750B012 | PRIV_ALARMACK | A_P1_SERV | VSD Excess input choke temp | BPP104_VSDInChokeTemp_E | C_EVENT | BPP104 | Class_Equipment | BR4_Cluster1 | BR4.UTILITIES.WATER.WBWD.BPP103_104.BPP104.VSD
BR4_Tags | BPP104_VSDIntConfig_E | ROM Sprays Pump 104 | VSD Number of inverter modules incorrect | BPP104_VSDIntConfig_E | CAT_EVENT | WBWD-1750B012 | PRIV_ALARMACK | A_P1_SERV | VSD Number of inverter modules incorrect | BPP104_VSDIntConfig_E | C_EVENT | BPP104 | Class_Equipment | BR4_Cluster1 | BR4.UTILITIES.WATER.WBWD.BPP103_104.BPP104.VSD
BR4_Tags | BPP104_VSDINVDisabled_E | ROM Sprays Pump 104 | VSD Optional DC switch has opened | BPP104_VSDINVDisabled_E | CAT_EVENT | WBWD-1750B012 | PRIV_ALARMACK | A_P1_SERV | VSD Optional DC switch has opened | BPP104_VSDINVDisabled_E | C_EVENT | BPP104 | Class_Equipment | BR4_Cluster1 | BR4.UTILITIES.WATER.WBWD.BPP103_104.BPP104.VSD
BR4_Tags | BPP104_VSDInvOverTemp_E | ROM Sprays Pump 104 | VSD Converter module temp excessive | BPP104_VSDInvOverTemp_E | CAT_EVENT | WBWD-1750B012 | PRIV_ALARMACK | A_P1_SERV | VSD Converter module temp excessive | BPP104_VSDInvOverTemp_E | C_EVENT | BPP104 | Class_Equipment | BR4_Cluster1 | BR4.UTILITIES.WATER.WBWD.BPP103_104.BPP104.VSD
BR4_Tags | BPP104_VSDIOComm_E | ROM Sprays Pump 104 | VSD Communication error on control board | BPP104_VSDIOComm_E | CAT_EVENT | WBWD-1750B012 | PRIV_ALARMACK | A_P1_SERV | VSD Communication error on control board | BPP104_VSDIOComm_E | C_EVENT | BPP104 | Class_Equipment | BR4_Cluster1 | BR4.UTILITIES.WATER.WBWD.BPP103_104.BPP104.VSD
BR4_Tags | BPP104_VSDMotor1Temp_E | ROM Sprays Pump 104 | VSD Motor temp1 excess | BPP104_VSDMotor1Temp_E | CAT_EVENT | WBWD-1750B012 | PRIV_ALARMACK | A_P1_SERV | VSD Motor temp1 excess | BPP104_VSDMotor1Temp_E | C_EVENT | BPP104 | Class_Equipment | BR4_Cluster1 | BR4.UTILITIES.WATER.WBWD.BPP103_104.BPP104.VSD
BR4_Tags | BPP104_VSDMotor2Temp_E | ROM Sprays Pump 104 | VSD Motor temperature 2 excess | BPP104_VSDMotor2Temp_E | CAT_EVENT | WBWD-1750B012 | PRIV_ALARMACK | A_P1_SERV | VSD Motor temperature 2 excess | BPP104_VSDMotor2Temp_E | C_EVENT | BPP104 | Class_Equipment | BR4_Cluster1 | BR4.UTILITIES.WATER.WBWD.BPP103_104.BPP104.VSD
BR4_Tags | BPP104_VSDMotorPhase_E | ROM Sprays Pump 104 | VSD Motor phase lost | BPP104_VSDMotorPhase_E | CAT_EVENT | WBWD-1750B012 | PRIV_ALARMACK | A_P1_SERV | VSD Motor phase lost | BPP104_VSDMotorPhase_E | C_EVENT | BPP104 | Class_Equipment | BR4_Cluster1 | BR4.UTILITIES.WATER.WBWD.BPP103_104.BPP104.VSD
BR4_Tags | BPP104_VSDMotorStall_E | ROM Sprays Pump 104 | VSD Motor is operating in stall region | BPP104_VSDMotorStall_E | CAT_EVENT | WBWD-1750B012 | PRIV_ALARMACK | A_P1_SERV | VSD Motor is operating in stall region | BPP104_VSDMotorStall_E | C_EVENT | BPP104 | Class_Equipment | BR4_Cluster1 | BR4.UTILITIES.WATER.WBWD.BPP103_104.BPP104.VSD
BR4_Tags | BPP104_VSDMotorTemp_E | ROM Sprays Pump 104 | VSD Motor temperature high | BPP104_VSDMotorTemp_E | CAT_EVENT | WBWD-1750B012 | PRIV_ALARMACK | A_P1_SERV | VSD Motor temperature high | BPP104_VSDMotorTemp_E | C_EVENT | BPP104 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBWD.BPP103_104.BPP104.VSD
BR4_Tags | BPP104_VSDNoMotData_E | ROM Sprays Pump 104 | VSD Motor data is not given | BPP104_VSDNoMotData_E | CAT_EVENT | WBWD-1750B012 | PRIV_ALARMACK | A_P1_SERV | VSD Motor data is not given | BPP104_VSDNoMotData_E | C_EVENT | BPP104 | Class_Equipment | BR4_Cluster1 | BR4.UTILITIES.WATER.WBWD.BPP103_104.BPP104.VSD
BR4_Tags | BPP104_VSDOverCurrent_E | ROM Sprays Pump 104 | VSD Output current exceeds trip limit | BPP104_VSDOverCurrent_E | CAT_EVENT | WBWD-1750B012 | PRIV_ALARMACK | A_P1_SERV | VSD Output current exceeds trip limit | BPP104_VSDOverCurrent_E | C_EVENT | BPP104 | Class_Equipment | BR4_Cluster1 | BR4.UTILITIES.WATER.WBWD.BPP103_104.BPP104.VSD
BR4_Tags | BPP104_VSDOverfreq_E | ROM Sprays Pump 104 | VSD Motor turning faster allowed speed | BPP104_VSDOverfreq_E | CAT_EVENT | WBWD-1750B012 | PRIV_ALARMACK | A_P1_SERV | VSD Motor turning faster allowed speed | BPP104_VSDOverfreq_E | C_EVENT | BPP104 | Class_Equipment | BR4_Cluster1 | BR4.UTILITIES.WATER.WBWD.BPP103_104.BPP104.VSD
BR4_Tags | BPP104_VSDOverSWFreq_E | ROM Sprays Pump 104 | VSD Switching frequency is too high | BPP104_VSDOverSWFreq_E | CAT_EVENT | WBWD-1750B012 | PRIV_ALARMACK | A_P1_SERV | VSD Switching frequency is too high | BPP104_VSDOverSWFreq_E | C_EVENT | BPP104 | Class_Equipment | BR4_Cluster1 | BR4.UTILITIES.WATER.WBWD.BPP103_104.BPP104.VSD
BR4_Tags | BPP104_VSDPanelLoss_E | ROM Sprays Pump 104 | VSD Control panel has ceased comms | BPP104_VSDPanelLoss_E | CAT_EVENT | WBWD-1750B012 | PRIV_ALARMACK | A_P1_SERV | VSD Control panel has ceased comms | BPP104_VSDPanelLoss_E | C_EVENT | BPP104 | Class_Equipment | BR4_Cluster1 | BR4.UTILITIES.WATER.WBWD.BPP103_104.BPP104.VSD
BR4_Tags | BPP104_VSDPowerInvFail_E | ROM Sprays Pump 104 | VSD INT board fail in inverter unit | BPP104_VSDPowerInvFail_E | CAT_EVENT | WBWD-1750B012 | PRIV_ALARMACK | A_P1_SERV | VSD INT board fail in inverter unit | BPP104_VSDPowerInvFail_E | C_EVENT | BPP104 | Class_Equipment | BR4_Cluster1 | BR4.UTILITIES.WATER.WBWD.BPP103_104.BPP104.VSD
BR4_Tags | BPP104_VSDPPCCLink_E | ROM Sprays Pump 104 | VSD Fibre optic link to INT board fault | BPP104_VSDPPCCLink_E | CAT_EVENT | WBWD-1750B012 | PRIV_ALARMACK | A_P1_SERV | VSD Fibre optic link to INT board fault | BPP104_VSDPPCCLink_E | C_EVENT | BPP104 | Class_Equipment | BR4_Cluster1 | BR4.UTILITIES.WATER.WBWD.BPP103_104.BPP104.VSD
BR4_Tags | BPP104_VSDPPOverload_E | ROM Sprays Pump 104 | VSD Excess IGBT junction to case temp | BPP104_VSDPPOverload_E | CAT_EVENT | WBWD-1750B012 | PRIV_ALARMACK | A_P1_SERV | VSD Excess IGBT junction to case temp | BPP104_VSDPPOverload_E | C_EVENT | BPP104 | Class_Equipment | BR4_Cluster1 | BR4.UTILITIES.WATER.WBWD.BPP103_104.BPP104.VSD
BR4_Tags | BPP104_VSDRdy_A | ROM Sprays Pump 104 | VSD Not Ready Trip | BPP104_VSDRdy_A | CAT_P3 | WBWD-1750B012 | PRIV_ALARMACK | A_P1_SERV | VSD Not Ready Trip | BPP104_VSDRdy_A | C_LOPRI | BPP104 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBWD.BPP103_104.BPP104.VSD
BR4_Tags | BPP104_VSDRunDisabled_E | ROM Sprays Pump 104 | VSD No Run enable signal received | BPP104_VSDRunDisabled_E | CAT_EVENT | WBWD-1750B012 | PRIV_ALARMACK | A_P1_SERV | VSD No Run enable signal received | BPP104_VSDRunDisabled_E | C_EVENT | BPP104 | Class_Equipment | BR4_Cluster1 | BR4.UTILITIES.WATER.WBWD.BPP103_104.BPP104.VSD
BR4_Tags | BPP104_VSDShortCirc_E | ROM Sprays Pump 104 | VSD Shrt Cct in motor cables or motor | BPP104_VSDShortCirc_E | CAT_EVENT | WBWD-1750B012 | PRIV_ALARMACK | A_P1_SERV | VSD Shrt Cct in motor cables or motor | BPP104_VSDShortCirc_E | C_EVENT | BPP104 | Class_Equipment | BR4_Cluster1 | BR4.UTILITIES.WATER.WBWD.BPP103_104.BPP104.VSD
BR4_Tags | BPP104_VSDSupplyPhase_E | ROM Sprays Pump 104 | VSD Intermcircuit DC volts oscillating | BPP104_VSDSupplyPhase_E | CAT_EVENT | WBWD-1750B012 | PRIV_ALARMACK | A_P1_SERV | VSD Intermcircuit DC volts oscillating | BPP104_VSDSupplyPhase_E | C_EVENT | BPP104 | Class_Equipment | BR4_Cluster1 | BR4.UTILITIES.WATER.WBWD.BPP103_104.BPP104.VSD
BR4_Tags | BPP104_VSDSystemFault_E | ROM Sprays Pump 104 | VSD Active system fault word alarm | BPP104_VSDSystemFault_E | CAT_EVENT | WBWD-1750B012 | PRIV_ALARMACK | A_P1_SERV | VSD Active system fault word alarm | BPP104_VSDSystemFault_E | C_EVENT | BPP104 | Class_Equipment | BR4_Cluster1 | BR4.UTILITIES.WATER.WBWD.BPP103_104.BPP104.VSD
BR4_Tags | BPP104_VSDTempDif_E | ROM Sprays Pump 104 | VSD Excess temp diff in inverter modules | BPP104_VSDTempDif_E | CAT_EVENT | WBWD-1750B012 | PRIV_ALARMACK | A_P1_SERV | VSD Excess temp diff in inverter modules | BPP104_VSDTempDif_E | C_EVENT | BPP104 | Class_Equipment | BR4_Cluster1 | BR4.UTILITIES.WATER.WBWD.BPP103_104.BPP104.VSD
BR4_Tags | BPP104_VSDThermistor_E | ROM Sprays Pump 104 | VSD Thermal protect thermistor in excess | BPP104_VSDThermistor_E | CAT_EVENT | WBWD-1750B012 | PRIV_ALARMACK | A_P1_SERV | VSD Thermal protect thermistor in excess | BPP104_VSDThermistor_E | C_EVENT | BPP104 | Class_Equipment | BR4_Cluster1 | BR4.UTILITIES.WATER.WBWD.BPP103_104.BPP104.VSD
BR4_Tags | BPP104_VSDUnderload_E | ROM Sprays Pump 104 | VSD Motor load is too low due | BPP104_VSDUnderload_E | CAT_EVENT | WBWD-1750B012 | PRIV_ALARMACK | A_P1_SERV | VSD Motor load is too low due | BPP104_VSDUnderload_E | C_EVENT | BPP104 | Class_Equipment | BR4_Cluster1 | BR4.UTILITIES.WATER.WBWD.BPP103_104.BPP104.VSD
BR4_Tags | BPP104_VSDUserLCurve_E | ROM Sprays Pump 104 | VSD Integr current exceeded load curve | BPP104_VSDUserLCurve_E | CAT_EVENT | WBWD-1750B012 | PRIV_ALARMACK | A_P1_SERV | VSD Integr current exceeded load curve | BPP104_VSDUserLCurve_E | C_EVENT | BPP104 | Class_Equipment | BR4_Cluster1 | BR4.UTILITIES.WATER.WBWD.BPP103_104.BPP104.VSD
BR4_Tags | BPP104DCOK_A | ROM Sprays Pump 104 | 24VDC Power Supply Trip | BPP104DCOK_A | CAT_P3 | WBWD-1750B012 | PRIV_ALARMACK | A_P1_SERV | 24 VDC Supply OK | BPP104DCOK_A | C_LOPRI | BPP104 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBWD.BPP103_104.BPP104
BR4_Tags | BPP104FN01_Auto_A | ROM Sprays Pump Motor Fan | Not Group Started In Auto Trip | BPP104FN01_Auto_A | CAT_P3 | WBWD-1750B012 | PRIV_ALARMACK | A_P1_SERV | Fan Not Group Started In Auto | BPP104FN01_Auto_A | C_LOPRI | BPP104FN01 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBWD.BPP103_104.BPP104.FN01
BR4_Tags | BPP104FN01_MainCont_A | ROM Sprays Pump Motor Fan | Main Contactor Faulted Trip | BPP104FN01_MainCont_A | CAT_P3 | WBWD-1750B012 | PRIV_ALARMACK | A_P1_SERV | Main Contactor | BPP104FN01_MainCont_A | C_LOPRI | BPP104FN01 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBWD.BPP103_104.BPP104.FN01
BR4_Tags | BPP104FN01TOL01_A | ROM Sprays Pump Motor Fan | Thermal Overload Trip | BPP104FN01TOL01_A | CAT_P3 | WBWD-1750B012 | PRIV_ALARMACK | A_P1_SERV | Thermal Overload Trip | BPP104FN01TOL01_A | C_LOPRI | BPP104FN01 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBWD.BPP103_104.BPP104.FN01
BR4_Tags | BPP104LOS01_A | ROM Sprays Pump 104 | Lock Off Stop Trip | BPP104LOS01_A | CAT_P1 | WBWD-1750B012 | PRIV_ALARMACK | A_P1_SERV | Lock Off Stop Trip | BPP104LOS01_A | C_LOPRI | BPP104 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBWD.BPP103_104.BPP104.LOS01
BR4_Tags | BPP104VS01DCOK_A | ROM Sprays Pump 104 | VSD 24VDC Power Supply Trip | BPP104VS01DCOK_A | CAT_P3 | WBWD-1750B012 | PRIV_ALARMACK | A_P1_SERV | VSD 24VDC Power Supply Trip | BPP104VS01DCOK_A | C_LOPRI | BPP104 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBWD.BPP103_104.BPP104
BR4_Tags | BPP501_ACFlt_E | Process Water Pump 501 | MNSiS AC Control voltage fault | BPP501_ACFlt_E | CAT_EVENT | WBWD-1750B012 | PRIV_ALARMACK | A_P1_SERV | MNSiS AC Control voltage fault | BPP501_ACFlt_E | C_EVENT | BPP501 | Class_Equipment | BR4_Cluster1 | BR4.UTILITIES.WATER.WBWD.BPP501_502.BPP501
BR4_Tags | BPP501_CARemote_E | Process Water Pump 501 | MNSiS Control Access not in remote | BPP501_CARemote_E | CAT_EVENT | WBWD-1750B012 | PRIV_ALARMACK | A_P1_SERV | MNSiS Control Access not in remote | BPP501_CARemote_E | C_EVENT | BPP501 | Class_Equipment | BR4_Cluster1 | BR4.UTILITIES.WATER.WBWD.BPP501_502.BPP501
BR4_Tags | BPP501_DCOK_E | Process Water Pump 501 | MNSiS DC Control voltage fault | BPP501_DCOK_E | CAT_EVENT | WBWD-1750B012 | PRIV_ALARMACK | A_P1_SERV | MNSiS DC Control voltage fault | BPP501_DCOK_E | C_EVENT | BPP501 | Class_Equipment | BR4_Cluster1 | BR4.UTILITIES.WATER.WBWD.BPP501_502.BPP501
BR4_Tags | BPP501_EStop_E | Process Water Pump 501 | MNSiS Emergency stop active | BPP501_EStop_E | CAT_EVENT | WBWD-1750B012 | PRIV_ALARMACK | A_P1_SERV | MNSiS Emergency stop active | BPP501_EStop_E | C_EVENT | BPP501 | Class_Equipment | BR4_Cluster1 | BR4.UTILITIES.WATER.WBWD.BPP501_502.BPP501
BR4_Tags | BPP501_FailSafe_E | Process Water Pump 501 | MNSiS MControl in fail safe mode | BPP501_FailSafe_E | CAT_EVENT | WBWD-1750B012 | PRIV_ALARMACK | A_P1_SERV | MNSiS MControl in fail safe mode | BPP501_FailSafe_E | C_EVENT | BPP501 | Class_Equipment | BR4_Cluster1 | BR4.UTILITIES.WATER.WBWD.BPP501_502.BPP501
BR4_Tags | BPP501_FwdCls_E | Process Water Pump 501 | MNSiS Forward contractor failed to close | BPP501_FwdCls_E | CAT_EVENT | WBWD-1750B012 | PRIV_ALARMACK | A_P1_SERV | MNSiS Forward contractor failed to close | BPP501_FwdCls_E | C_EVENT | BPP501 | Class_Equipment | BR4_Cluster1 | BR4.UTILITIES.WATER.WBWD.BPP501_502.BPP501
BR4_Tags | BPP501_IRFHard_E | Process Water Pump 501 | MNSiS Internal relay h/w fault trip | BPP501_IRFHard_E | CAT_EVENT | WBWD-1750B012 | PRIV_ALARMACK | A_P1_SERV | MNSiS Internal relay h/w fault trip | BPP501_IRFHard_E | C_EVENT | BPP501 | Class_Equipment | BR4_Cluster1 | BR4.UTILITIES.WATER.WBWD.BPP501_502.BPP501
BR4_Tags | BPP501_IRFSoft_E | Process Water Pump 501 | MNSiS Internal relay s/w fault trip | BPP501_IRFSoft_E | CAT_EVENT | WBWD-1750B012 | PRIV_ALARMACK | A_P1_SERV | MNSiS Internal relay s/w fault trip | BPP501_IRFSoft_E | C_EVENT | BPP501 | Class_Equipment | BR4_Cluster1 | BR4.UTILITIES.WATER.WBWD.BPP501_502.BPP501
BR4_Tags | BPP501_IS01Opn_E | Process Water Pump 501 | MNSiS MStart isolated | BPP501_IS01Opn_E | CAT_EVENT | WBWD-1750B012 | PRIV_ALARMACK | A_P1_SERV | MNSiS MStart isolated | BPP501_IS01Opn_E | C_EVENT | BPP501 | Class_Equipment | BR4_Cluster1 | BR4.UTILITIES.WATER.WBWD.BPP501_502.BPP501.IS01
BR4_Tags | BPP501_IS01Test_E | Process Water Pump 501 | MNSiS Isolator in test position | BPP501_IS01Test_E | CAT_EVENT | WBWD-1750B012 | PRIV_ALARMACK | A_P1_SERV | MNSiS Isolator in test position | BPP501_IS01Test_E | C_EVENT | BPP501 | Class_Equipment | BR4_Cluster1 | BR4.UTILITIES.WATER.WBWD.BPP501_502.BPP501.IS01
BR4_Tags | BPP501_MContID_E | Process Water Pump 501 | MNSiS Location supervision trip | BPP501_MContID_E | CAT_EVENT | WBWD-1750B012 | PRIV_ALARMACK | A_P1_SERV | MNSiS Location supervision trip | BPP501_MContID_E | C_EVENT | BPP501 | Class_Equipment | BR4_Cluster1 | BR4.UTILITIES.WATER.WBWD.BPP501_502.BPP501
BR4_Tags | BPP501_MContLife_E | Process Water Pump 501 | MNSiS MControl life bit not healthy | BPP501_MContLife_E | CAT_EVENT | WBWD-1750B012 | PRIV_ALARMACK | A_P1_SERV | MNSiS MControl life bit not healthy | BPP501_MContLife_E | C_EVENT | BPP501 | Class_Equipment | BR4_Cluster1 | BR4.UTILITIES.WATER.WBWD.BPP501_502.BPP501
BR4_Tags | BPP501_MNSiSMainCont_A | Process Water Pump 501 | MNSiS Main Contactor Faulted Trip | BPP501_MNSiSMainCont_A | CAT_P3 | WBWD-1750B012 | PRIV_ALARMACK | A_P1_SERV | MNSiS Main Contactor Faulted Trip | BPP501_MNSiSMainCont_A | C_LOPRI | BPP501 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBWD.BPP501_502.BPP501
BR4_Tags | BPP501_MNSiSOK_A | Process Water Pump 501 | MCC Starter/Motor Electrical Fault Trip | BPP501_MNSiSOK_A | CAT_P2 | WBWD-1750B012 | PRIV_ALARMACK | A_P1_SERV | MCC Starter/Motor Electrical Fault Trip | BPP501_MNSiSOK_A | C_HIPRI | BPP501 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBWD.BPP501_502.BPP501
BR4_Tags | BPP501_MNSiSTrip_E | Process Water Pump 501 | MNSiS General trip alarm | BPP501_MNSiSTrip_E | CAT_EVENT | WBWD-1750B012 | PRIV_ALARMACK | A_P1_SERV | MNSiS General trip alarm | BPP501_MNSiSTrip_E | C_EVENT | BPP501 | Class_Equipment | BR4_Cluster1 | BR4.UTILITIES.WATER.WBWD.BPP501_502.BPP501
BR4_Tags | BPP501_MNSiSWarning_E | Process Water Pump 501 | MNSiS General warning alarm | BPP501_MNSiSWarning_E | CAT_EVENT | WBWD-1750B012 | PRIV_ALARMACK | A_P1_SERV | MNSiS General warning alarm | BPP501_MNSiSWarning_E | C_EVENT | BPP501 | Class_Equipment | BR4_Cluster1 | BR4.UTILITIES.WATER.WBWD.BPP501_502.BPP501
BR4_Tags | BPP501_MStartComms_E | Process Water Pump 501 | MNSiS Power module comms error | BPP501_MStartComms_E | CAT_EVENT | WBWD-1750B012 | PRIV_ALARMACK | A_P1_SERV | MNSiS Power module comms error | BPP501_MStartComms_E | C_EVENT | BPP501 | Class_Equipment | BR4_Cluster1 | BR4.UTILITIES.WATER.WBWD.BPP501_502.BPP501
BR4_Tags | BPP501_MStartID_E | Process Water Pump 501 | MNSiS Power module ID error | BPP501_MStartID_E | CAT_EVENT | WBWD-1750B012 | PRIV_ALARMACK | A_P1_SERV | MNSiS Power module ID error | BPP501_MStartID_E | C_EVENT | BPP501 | Class_Equipment | BR4_Cluster1 | BR4.UTILITIES.WATER.WBWD.BPP501_502.BPP501
BR4_Tags | BPP501_NoLoad_E | Process Water Pump 501 | MNSiS No load trip level reached | BPP501_NoLoad_E | CAT_EVENT | WBWD-1750B012 | PRIV_ALARMACK | A_P1_SERV | MNSiS No load trip level reached | BPP501_NoLoad_E | C_EVENT | BPP501 | Class_Equipment | BR4_Cluster1 | BR4.UTILITIES.WATER.WBWD.BPP501_502.BPP501
BR4_Tags | BPP501_PrmStg1_A | Proc Wtr Pump Priming Seq | Required Drives and Valves Not Healthy Trip | BPP501_PrmStg1_A | CAT_P3 | WBWD-1750B012 | PRIV_ALARMACK | A_P1_SERV | Required Drives and Valves Not Healthy | BPP501_PrmStg1_A | C_LOPRI | BPP501YV01 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBWD.BPP501_502.BPP501
BR4_Tags | BPP501_PrmStg2_A | Proc Wtr Pump Priming Seq | Required Drives and Valves Faulted Trip | BPP501_PrmStg2_A | CAT_P3 | WBWD-1750B012 | PRIV_ALARMACK | A_P1_SERV | Required Drives and Valves Fault | BPP501_PrmStg2_A | C_LOPRI | BPP501YV01 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBWD.BPP501_502.BPP501
BR4_Tags | BPP501_PrmStg3_A | Proc Wtr Pump Priming Seq | Stage 3 Start Pressure Low Trip | BPP501_PrmStg3_A | CAT_P3 | WBWD-1750B012 | PRIV_ALARMACK | A_P1_SERV | Min Pressure for Pump Start Not Reached | BPP501_PrmStg3_A | C_LOPRI | BPP501YV01 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBWD.BPP501_502.BPP501
BR4_Tags | BPP501_PrmStg4_A | Proc Wtr Pump Priming Seq | Stage 4 Operating Pressure Low Trip | BPP501_PrmStg4_A | CAT_P3 | WBWD-1750B012 | PRIV_ALARMACK | A_P1_SERV | Operating Press Not Reached Priming Failed | BPP501_PrmStg4_A | C_LOPRI | BPP501YV01 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBWD.BPP501_502.BPP501
BR4_Tags | BPP501_PrmStg6_A | Proc Wtr Pump Priming Seq | Stage 6 Operating Pressure Low Trip | BPP501_PrmStg6_A | CAT_P3 | WBWD-1750B012 | PRIV_ALARMACK | A_P1_SERV | Operating Press Not Reached Priming Failed | BPP501_PrmStg6_A | C_LOPRI | BPP501YV01 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBWD.BPP501_502.BPP501
BR4_Tags | BPP501_PTCFlt_E | Process Water Pump 501 | MNSiS PTC trip | BPP501_PTCFlt_E | CAT_EVENT | WBWD-1750B012 | PRIV_ALARMACK | A_P1_SERV | MNSiS PTC trip | BPP501_PTCFlt_E | C_EVENT | BPP501 | Class_Equipment | BR4_Cluster1 | BR4.UTILITIES.WATER.WBWD.BPP501_502.BPP501
BR4_Tags | BPP501_RevCls_E | Process Water Pump 501 | MNSiS Reverse contractor failed to close | BPP501_RevCls_E | CAT_EVENT | WBWD-1750B012 | PRIV_ALARMACK | A_P1_SERV | MNSiS Reverse contractor failed to close | BPP501_RevCls_E | C_EVENT | BPP501 | Class_Equipment | BR4_Cluster1 | BR4.UTILITIES.WATER.WBWD.BPP501_502.BPP501
BR4_Tags | BPP501_RunFlt1_E | Process Water Pump 501 | MNSiS Motor still running fault | BPP501_RunFlt1_E | CAT_EVENT | WBWD-1750B012 | PRIV_ALARMACK | A_P1_SERV | MNSiS Motor still running fault | BPP501_RunFlt1_E | C_EVENT | BPP501 | Class_Equipment | BR4_Cluster1 | BR4.UTILITIES.WATER.WBWD.BPP501_502.BPP501
BR4_Tags | BPP501_RunFlt2_E | Process Water Pump 501 | MNSiS Contactor welded | BPP501_RunFlt2_E | CAT_EVENT | WBWD-1750B012 | PRIV_ALARMACK | A_P1_SERV | MNSiS Contactor welded | BPP501_RunFlt2_E | C_EVENT | BPP501 | Class_Equipment | BR4_Cluster1 | BR4.UTILITIES.WATER.WBWD.BPP501_502.BPP501
BR4_Tags | BPP501_RunFlt3_E | Process Water Pump 501 | MNSiS Motor not running fault | BPP501_RunFlt3_E | CAT_EVENT | WBWD-1750B012 | PRIV_ALARMACK | A_P1_SERV | MNSiS Motor not running fault | BPP501_RunFlt3_E | C_EVENT | BPP501 | Class_Equipment | BR4_Cluster1 | BR4.UTILITIES.WATER.WBWD.BPP501_502.BPP501
BR4_Tags | BPP501_Stall_E | Process Water Pump 501 | MNSiS Motor stall trip level reached | BPP501_Stall_E | CAT_EVENT | WBWD-1750B012 | PRIV_ALARMACK | A_P1_SERV | MNSiS Motor stall trip level reached | BPP501_Stall_E | C_EVENT | BPP501 | Class_Equipment | BR4_Cluster1 | BR4.UTILITIES.WATER.WBWD.BPP501_502.BPP501
BR4_Tags | BPP501_SttLmt_E | Process Water Pump 501 | MNSiS Starting limitation trip | BPP501_SttLmt_E | CAT_EVENT | WBWD-1750B012 | PRIV_ALARMACK | A_P1_SERV | MNSiS Starting limitation trip | BPP501_SttLmt_E | C_EVENT | BPP501 | Class_Equipment | BR4_Cluster1 | BR4.UTILITIES.WATER.WBWD.BPP501_502.BPP501
BR4_Tags | BPP501_TOL_E | Process Water Pump 501 | MNSiS Thermal overload fault | BPP501_TOL_E | CAT_EVENT | WBWD-1750B012 | PRIV_ALARMACK | A_P1_SERV | MNSiS Thermal overload fault | BPP501_TOL_E | C_EVENT | BPP501 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBWD.BPP501_502.BPP501
BR4_Tags | BPP501_Underload_E | Process Water Pump 501 | MNSiS Under load trip level reached | BPP501_Underload_E | CAT_EVENT | WBWD-1750B012 | PRIV_ALARMACK | A_P1_SERV | MNSiS Under load trip level reached | BPP501_Underload_E | C_EVENT | BPP501 | Class_Equipment | BR4_Cluster1 | BR4.UTILITIES.WATER.WBWD.BPP501_502.BPP501
BR4_Tags | BPP501DCOK_A | Process Water Pump 501 | 24VDC Power Supply Trip | BPP501DCOK_A | CAT_P3 | WBWD-1750B012 | PRIV_ALARMACK | A_P1_SERV | 24 VDC Supply OK | BPP501DCOK_A | C_LOPRI | BPP501 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBWD.BPP501_502.BPP501
BR4_Tags | BPP501FT01_LoLo_A | Process Water Pump 501 | Flow Low Low Trip | BPP501FT01_LoLo_A | CAT_P3 | WBWD-1750B012 | PRIV_ALARMACK | A_P1_SERV | Flow Low Low | BPP501FT01_LoLo_A | C_LOPRI | BPP501FT01 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBWD.BPP501_502.BPP501FT01
BR4_Tags | BPP501FT01DCOK_A | Process Water Pump 501 | 24VDC Power Supply Trip | BPP501FT01DCOK_A | CAT_P3 | WBWD-1750B012 | PRIV_ALARMACK | A_P1_SERV | 24 VDC Supply OK | BPP501FT01DCOK_A | C_LOPRI | BPP501FT01 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBWD.BPP501_502.BPP501FT01
BR4_Tags | BPP501LOS01_A | Process Water Pump 501 | Lock Off Stop Trip | BPP501LOS01_A | CAT_P1 | WBWD-1750B012 | PRIV_ALARMACK | A_P1_SERV | Lock Off Stop Trip | BPP501LOS01_A | C_LOPRI | BPP501 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBWD.BPP501_502.BPP501.LOS01
BR4_Tags | BPP501PT01_HiHi_A | Process Water Pump 501 | Pressure High High Trip | BPP501PT01_HiHi_A | CAT_P3 | WBWD-1750B012 | PRIV_ALARMACK | A_P1_SERV | Pressure Hi Hi | BPP501PT01_HiHi_A | C_LOPRI | BPP501PT01 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBWD.BPP501_502.BPP501PT01
BR4_Tags | BPP501PT01_LoLo_A | Process Water Pump 501 | Pressure Low Low Alarm | BPP501PT01_LoLo_A | CAT_P3 | WBWD-1750B012 | PRIV_ALARMACK | A_P1_SERV | Pressure Low Low Alarm | BPP501PT01_LoLo_A | C_LOPRI | BPP501PT01 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBWD.BPP501_502.BPP501PT01
BR4_Tags | BPP501ZS01_LmtFlt_A | Proc Wtr Pump Priming Valve | Opened/Closed Limits Fault Trip | BPP501ZS01_LmtFlt_A | CAT_P3 | WBWD-1750B012 | PRIV_ALARMACK | A_P1_SERV | Limit Switch Fault | BPP501ZS01_LmtFlt_A | C_LOPRI | BPP501YV01 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBWD.BPP501_502.BPP501
BR4_Tags | BPP501ZS01A_A | Proc Wtr Pump Priming Valve | Failed to Open Trip | BPP501ZS01A_A | CAT_P3 | WBWD-1750B012 | PRIV_ALARMACK | A_P1_SERV | Failed to Open | BPP501ZS01A_A | C_LOPRI | BPP501YV01 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBWD.BPP501_502.BPP501
BR4_Tags | BPP501ZS01B_A | Proc Wtr Pump Priming Valve | Failed to Close Trip | BPP501ZS01B_A | CAT_P3 | WBWD-1750B012 | PRIV_ALARMACK | A_P1_SERV | Failed to Close | BPP501ZS01B_A | C_LOPRI | BPP501YV01 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBWD.BPP501_502.BPP501
BR4_Tags | BPP501ZS02_LmtFlt_A | Proc Wtr Pump Recirc Valve | Opened/Closed Limits Fault Trip | BPP501ZS02_LmtFlt_A | CAT_P3 | WBWD-1750B012 | PRIV_ALARMACK | A_P1_SERV | Limit Switch Fault | BPP501ZS02_LmtFlt_A | C_LOPRI | BPP501FV01 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBWD.BPP501_502.BPP501
BR4_Tags | BPP501ZS02A_A | Proc Wtr Pump Recirc Valve | Failed to Open Trip | BPP501ZS02A_A | CAT_P3 | WBWD-1750B012 | PRIV_ALARMACK | A_P1_SERV | Failed to Open | BPP501ZS02A_A | C_LOPRI | BPP501FV01 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBWD.BPP501_502.BPP501
BR4_Tags | BPP501ZS02B_A | Proc Wtr Pump Recirc Valve | Failed to Close Trip | BPP501ZS02B_A | CAT_P3 | WBWD-1750B012 | PRIV_ALARMACK | A_P1_SERV | Failed to Close | BPP501ZS02B_A | C_LOPRI | BPP501FV01 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBWD.BPP501_502.BPP501
BR4_Tags | BPP502_ACFlt_E | Process Water Pump 502 | MNSiS AC Control voltage fault | BPP502_ACFlt_E | CAT_EVENT | WBWD-1750B012 | PRIV_ALARMACK | A_P1_SERV | MNSiS AC Control voltage fault | BPP502_ACFlt_E | C_EVENT | BPP502 | Class_Equipment | BR4_Cluster1 | BR4.UTILITIES.WATER.WBWD.BPP501_502.BPP502
BR4_Tags | BPP502_CARemote_E | Process Water Pump 502 | MNSiS Control Access not in remote | BPP502_CARemote_E | CAT_EVENT | WBWD-1750B012 | PRIV_ALARMACK | A_P1_SERV | MNSiS Control Access not in remote | BPP502_CARemote_E | C_EVENT | BPP502 | Class_Equipment | BR4_Cluster1 | BR4.UTILITIES.WATER.WBWD.BPP501_502.BPP502
BR4_Tags | BPP502_DCOK_E | Process Water Pump 502 | MNSiS DC Control voltage fault | BPP502_DCOK_E | CAT_EVENT | WBWD-1750B012 | PRIV_ALARMACK | A_P1_SERV | MNSiS DC Control voltage fault | BPP502_DCOK_E | C_EVENT | BPP502 | Class_Equipment | BR4_Cluster1 | BR4.UTILITIES.WATER.WBWD.BPP501_502.BPP502
BR4_Tags | BPP502_EStop_E | Process Water Pump 502 | MNSiS Emergency stop active | BPP502_EStop_E | CAT_EVENT | WBWD-1750B012 | PRIV_ALARMACK | A_P1_SERV | MNSiS Emergency stop active | BPP502_EStop_E | C_EVENT | BPP502 | Class_Equipment | BR4_Cluster1 | BR4.UTILITIES.WATER.WBWD.BPP501_502.BPP502
BR4_Tags | BPP502_FailSafe_E | Process Water Pump 502 | MNSiS MControl in fail safe mode | BPP502_FailSafe_E | CAT_EVENT | WBWD-1750B012 | PRIV_ALARMACK | A_P1_SERV | MNSiS MControl in fail safe mode | BPP502_FailSafe_E | C_EVENT | BPP502 | Class_Equipment | BR4_Cluster1 | BR4.UTILITIES.WATER.WBWD.BPP501_502.BPP502
BR4_Tags | BPP502_FwdCls_E | Process Water Pump 502 | MNSiS Forward contractor failed to close | BPP502_FwdCls_E | CAT_EVENT | WBWD-1750B012 | PRIV_ALARMACK | A_P1_SERV | MNSiS Forward contractor failed to close | BPP502_FwdCls_E | C_EVENT | BPP502 | Class_Equipment | BR4_Cluster1 | BR4.UTILITIES.WATER.WBWD.BPP501_502.BPP502
BR4_Tags | BPP502_IRFHard_E | Process Water Pump 502 | MNSiS Internal relay h/w fault trip | BPP502_IRFHard_E | CAT_EVENT | WBWD-1750B012 | PRIV_ALARMACK | A_P1_SERV | MNSiS Internal relay h/w fault trip | BPP502_IRFHard_E | C_EVENT | BPP502 | Class_Equipment | BR4_Cluster1 | BR4.UTILITIES.WATER.WBWD.BPP501_502.BPP502
BR4_Tags | BPP502_IRFSoft_E | Process Water Pump 502 | MNSiS Internal relay s/w fault trip | BPP502_IRFSoft_E | CAT_EVENT | WBWD-1750B012 | PRIV_ALARMACK | A_P1_SERV | MNSiS Internal relay s/w fault trip | BPP502_IRFSoft_E | C_EVENT | BPP502 | Class_Equipment | BR4_Cluster1 | BR4.UTILITIES.WATER.WBWD.BPP501_502.BPP502
BR4_Tags | BPP502_IS01Opn_E | Process Water Pump 502 | MNSiS MStart isolated | BPP502_IS01Opn_E | CAT_EVENT | WBWD-1750B012 | PRIV_ALARMACK | A_P1_SERV | MNSiS MStart isolated | BPP502_IS01Opn_E | C_EVENT | BPP502 | Class_Equipment | BR4_Cluster1 | BR4.UTILITIES.WATER.WBWD.BPP501_502.BPP502.IS01
BR4_Tags | BPP502_IS01Test_E | Process Water Pump 502 | MNSiS Isolator in test position | BPP502_IS01Test_E | CAT_EVENT | WBWD-1750B012 | PRIV_ALARMACK | A_P1_SERV | MNSiS Isolator in test position | BPP502_IS01Test_E | C_EVENT | BPP502 | Class_Equipment | BR4_Cluster1 | BR4.UTILITIES.WATER.WBWD.BPP501_502.BPP502.IS01
BR4_Tags | BPP502_MContID_E | Process Water Pump 502 | MNSiS Location supervision trip | BPP502_MContID_E | CAT_EVENT | WBWD-1750B012 | PRIV_ALARMACK | A_P1_SERV | MNSiS Location supervision trip | BPP502_MContID_E | C_EVENT | BPP502 | Class_Equipment | BR4_Cluster1 | BR4.UTILITIES.WATER.WBWD.BPP501_502.BPP502
BR4_Tags | BPP502_MContLife_E | Process Water Pump 502 | MNSiS MControl life bit not healthy | BPP502_MContLife_E | CAT_EVENT | WBWD-1750B012 | PRIV_ALARMACK | A_P1_SERV | MNSiS MControl life bit not healthy | BPP502_MContLife_E | C_EVENT | BPP502 | Class_Equipment | BR4_Cluster1 | BR4.UTILITIES.WATER.WBWD.BPP501_502.BPP502
BR4_Tags | BPP502_MNSiSMainCont_A | Process Water Pump 502 | MNSiS Main Contactor Faulted Trip | BPP502_MNSiSMainCont_A | CAT_P3 | WBWD-1750B012 | PRIV_ALARMACK | A_P1_SERV | MNSiS Main Contactor Faulted Trip | BPP502_MNSiSMainCont_A | C_LOPRI | BPP502 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBWD.BPP501_502.BPP502
BR4_Tags | BPP502_MNSiSOK_A | Process Water Pump 502 | MCC Starter/Motor Electrical Fault Trip | BPP502_MNSiSOK_A | CAT_P2 | WBWD-1750B012 | PRIV_ALARMACK | A_P1_SERV | MCC Starter/Motor Electrical Fault Trip | BPP502_MNSiSOK_A | C_HIPRI | BPP502 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBWD.BPP501_502.BPP502
BR4_Tags | BPP502_MNSiSTrip_E | Process Water Pump 502 | MNSiS General trip alarm | BPP502_MNSiSTrip_E | CAT_EVENT | WBWD-1750B012 | PRIV_ALARMACK | A_P1_SERV | MNSiS General trip alarm | BPP502_MNSiSTrip_E | C_EVENT | BPP502 | Class_Equipment | BR4_Cluster1 | BR4.UTILITIES.WATER.WBWD.BPP501_502.BPP502
BR4_Tags | BPP502_MNSiSWarning_E | Process Water Pump 502 | MNSiS General warning alarm | BPP502_MNSiSWarning_E | CAT_EVENT | WBWD-1750B012 | PRIV_ALARMACK | A_P1_SERV | MNSiS General warning alarm | BPP502_MNSiSWarning_E | C_EVENT | BPP502 | Class_Equipment | BR4_Cluster1 | BR4.UTILITIES.WATER.WBWD.BPP501_502.BPP502
BR4_Tags | BPP502_MStartComms_E | Process Water Pump 502 | MNSiS Power module comms error | BPP502_MStartComms_E | CAT_EVENT | WBWD-1750B012 | PRIV_ALARMACK | A_P1_SERV | MNSiS Power module comms error | BPP502_MStartComms_E | C_EVENT | BPP502 | Class_Equipment | BR4_Cluster1 | BR4.UTILITIES.WATER.WBWD.BPP501_502.BPP502
BR4_Tags | BPP502_MStartID_E | Process Water Pump 502 | MNSiS Power module ID error | BPP502_MStartID_E | CAT_EVENT | WBWD-1750B012 | PRIV_ALARMACK | A_P1_SERV | MNSiS Power module ID error | BPP502_MStartID_E | C_EVENT | BPP502 | Class_Equipment | BR4_Cluster1 | BR4.UTILITIES.WATER.WBWD.BPP501_502.BPP502
BR4_Tags | BPP502_NoLoad_E | Process Water Pump 502 | MNSiS No load trip level reached | BPP502_NoLoad_E | CAT_EVENT | WBWD-1750B012 | PRIV_ALARMACK | A_P1_SERV | MNSiS No load trip level reached | BPP502_NoLoad_E | C_EVENT | BPP502 | Class_Equipment | BR4_Cluster1 | BR4.UTILITIES.WATER.WBWD.BPP501_502.BPP502
BR4_Tags | BPP502_PTCFlt_E | Process Water Pump 502 | MNSiS PTC trip | BPP502_PTCFlt_E | CAT_EVENT | WBWD-1750B012 | PRIV_ALARMACK | A_P1_SERV | MNSiS PTC trip | BPP502_PTCFlt_E | C_EVENT | BPP502 | Class_Equipment | BR4_Cluster1 | BR4.UTILITIES.WATER.WBWD.BPP501_502.BPP502
BR4_Tags | BPP502_RevCls_E | Process Water Pump 502 | MNSiS Reverse contractor failed to close | BPP502_RevCls_E | CAT_EVENT | WBWD-1750B012 | PRIV_ALARMACK | A_P1_SERV | MNSiS Reverse contractor failed to close | BPP502_RevCls_E | C_EVENT | BPP502 | Class_Equipment | BR4_Cluster1 | BR4.UTILITIES.WATER.WBWD.BPP501_502.BPP502
BR4_Tags | BPP502_RunFlt1_E | Process Water Pump 502 | MNSiS Motor still running fault | BPP502_RunFlt1_E | CAT_EVENT | WBWD-1750B012 | PRIV_ALARMACK | A_P1_SERV | MNSiS Motor still running fault | BPP502_RunFlt1_E | C_EVENT | BPP502 | Class_Equipment | BR4_Cluster1 | BR4.UTILITIES.WATER.WBWD.BPP501_502.BPP502
BR4_Tags | BPP502_RunFlt2_E | Process Water Pump 502 | MNSiS Contactor welded | BPP502_RunFlt2_E | CAT_EVENT | WBWD-1750B012 | PRIV_ALARMACK | A_P1_SERV | MNSiS Contactor welded | BPP502_RunFlt2_E | C_EVENT | BPP502 | Class_Equipment | BR4_Cluster1 | BR4.UTILITIES.WATER.WBWD.BPP501_502.BPP502
BR4_Tags | BPP502_RunFlt3_E | Process Water Pump 502 | MNSiS Motor not running fault | BPP502_RunFlt3_E | CAT_EVENT | WBWD-1750B012 | PRIV_ALARMACK | A_P1_SERV | MNSiS Motor not running fault | BPP502_RunFlt3_E | C_EVENT | BPP502 | Class_Equipment | BR4_Cluster1 | BR4.UTILITIES.WATER.WBWD.BPP501_502.BPP502
BR4_Tags | BPP502_Stall_E | Process Water Pump 502 | MNSiS Motor stall trip level reached | BPP502_Stall_E | CAT_EVENT | WBWD-1750B012 | PRIV_ALARMACK | A_P1_SERV | MNSiS Motor stall trip level reached | BPP502_Stall_E | C_EVENT | BPP502 | Class_Equipment | BR4_Cluster1 | BR4.UTILITIES.WATER.WBWD.BPP501_502.BPP502
BR4_Tags | BPP502_SttLmt_E | Process Water Pump 502 | MNSiS Starting limitation trip | BPP502_SttLmt_E | CAT_EVENT | WBWD-1750B012 | PRIV_ALARMACK | A_P1_SERV | MNSiS Starting limitation trip | BPP502_SttLmt_E | C_EVENT | BPP502 | Class_Equipment | BR4_Cluster1 | BR4.UTILITIES.WATER.WBWD.BPP501_502.BPP502
BR4_Tags | BPP502_TOL_E | Process Water Pump 502 | MNSiS Thermal overload fault | BPP502_TOL_E | CAT_EVENT | WBWD-1750B012 | PRIV_ALARMACK | A_P1_SERV | MNSiS Thermal overload fault | BPP502_TOL_E | C_EVENT | BPP502 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBWD.BPP501_502.BPP502
BR4_Tags | BPP502_Underload_E | Process Water Pump 502 | MNSiS Under load trip level reached | BPP502_Underload_E | CAT_EVENT | WBWD-1750B012 | PRIV_ALARMACK | A_P1_SERV | MNSiS Under load trip level reached | BPP502_Underload_E | C_EVENT | BPP502 | Class_Equipment | BR4_Cluster1 | BR4.UTILITIES.WATER.WBWD.BPP501_502.BPP502
BR4_Tags | BPP502DCOK_A | Process Water Pump 502 | 24VDC Power Supply Trip | BPP502DCOK_A | CAT_P3 | WBWD-1750B012 | PRIV_ALARMACK | A_P1_SERV | 24 VDC Supply OK | BPP502DCOK_A | C_LOPRI | BPP502 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBWD.BPP501_502.BPP502
BR4_Tags | BPP502LOS01_A | Process Water Pump 502 | Lock Off Stop Trip | BPP502LOS01_A | CAT_P1 | WBWD-1750B012 | PRIV_ALARMACK | A_P1_SERV | Lock Off Stop Trip | BPP502LOS01_A | C_LOPRI | BPP502 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBWD.BPP501_502.BPP502.LOS01
BR4_Tags | BPP703DCOK_A | West Bore Transfer Pump 703 | 24VDC Power Supply Trip | BPP703DCOK_A | CAT_P3 | WBBWD-1750B004 | PRIV_ALARMACK | A_P1_SERV | Loss of 24 V DC supply | BPP703DCOK_A | C_LOPRI | BPP703 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.BPP703_706.BPP703
BR4_Tags | BPP703FQ02_100Percent_A | West Borefield Creek Discharge | Exceeded 100% of Annual Limit | BPP703FQ02_100Percent_A | CAT_P1 | WBBWD-Discharge | PRIV_ALARMACK | A_P1_SERV | BPP703FQ02_100Percent_A | BPP703FQ02_100Percent_A | C_CRITPRI | BPP703 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.BPP703_706.BPP703
BR4_Tags | BPP703FQ02_95Percent_A | West Borefield Creek Discharge | Exceeded 95% of Annual Limit | BPP703FQ02_95Percent_A | CAT_P2 | WBBWD-Discharge | PRIV_ALARMACK | A_P1_SERV | BPP703FQ02_95Percent_A | BPP703FQ02_95Percent_A | C_HIPRI | BPP703 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.BPP703_706.BPP703
BR4_Tags | BPP703FQ02_TotVolDay_EXC_A | West Borefield Creek Discharge | Exceeded Daily Discharge Limit | BPP703FQ02_TotVolDay_EXC_A | CAT_P2 | WBBWD-Discharge | PRIV_ALARMACK | A_P1_SERV | BPP703FQ02_TotVolDay_EXC_A | BPP703FQ02_TotVolDay_EXC_A | C_HIPRI | BPP703 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.BPP703_706.BPP703
BR4_Tags | BPP703FQ02_TotVolFNight_EXC_A | West Borefield Creek Discharge | Exceeded Fortnighly Discharge Limit | BPP703FQ02_TotVolFNight_EXC_A | CAT_P2 | WBBWD-Discharge | PRIV_ALARMACK | A_P1_SERV | BPP703FQ02_TotVolMnth_EXC_A | BPP703FQ02_TotVolFNight_EXC_A | C_HIPRI | BPP703 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.BPP703_706.BPP703
BR4_Tags | BPP703FQ02_TotVolMnth_EXC_A | West Borefield Creek Discharge | Exceeded Monthly Discharge Limit | BPP703FQ02_TotVolMnth_EXC_A | CAT_P2 | WBBWD-Discharge | PRIV_ALARMACK | A_P1_SERV | BPP703FQ02_TotVolMnth_EXC_A | BPP703FQ02_TotVolMnth_EXC_A | C_HIPRI | BPP703 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.BPP703_706.BPP703
BR4_Tags | BPP703FT01_ChOK_A | West Bore Transfer Pumps PLC | Rack 0 Slot 8 Channel 0 Fault | BPP703FT01_ChOK_A | CAT_P3 | BPL752 | PRIV_ALARMACK | A_P1_SERV | Rack 0 Slot 8 Channel 0 Fault | BPP703FT01_ChOK_A | C_LOPRI | BPL752 | Class_Equipment | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.BPP703_706.BPP703FT01
BR4_Tags | BPP703FT01_LoLo_A | West Bore Transfer Pumps | Flow Low Low Trip | BPP703FT01_LoLo_A | CAT_P3 | WBBWD-1750B004 | PRIV_ALARMACK | A_P1_SERV | Flow Low Low | BPP703FT01_LoLo_A | C_LOPRI | BPP703FT01 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.BPP703_706.BPP703FT01
BR4_Tags | BPP703FT01_ROVF_E | West Bore Transfer Pumps PLC | Rack 0 Slot 6 Channel 0 Overflow Error | BPP703FT01_ROVF_E | CAT_P4 | BPL752 | PRIV_ALARMACK | A_P1_SERV | Rack 0 Slot 6 Channel 0 Overflow | BPP703FT01_ROVF_E | C_EVENT | BPL752 | Class_Equipment | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.BPP703_706.BPP703FT01
BR4_Tags | BPP703FT01_RUNF_E | West Bore Transfer Pumps PLC | Rack 0 Slot 6 Channel 0 Underflow Error | BPP703FT01_RUNF_E | CAT_P4 | BPL752 | PRIV_ALARMACK | A_P1_SERV | Rack 0 Slot 6 Channel 0 Underflow | BPP703FT01_RUNF_E | C_EVENT | BPL752 | Class_Equipment | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.BPP703_706.BPP703FT01
BR4_Tags | BPP703FT02_H_A | West Borefield Creek Discharge | High Flow | BPP703FT02_H_A | CAT_P2 | WBBWD-Discharge | PRIV_ALARMACK | A_P1_SERV | BPP703FT02_H_A | BPP703FT02_H_A | C_HIPRI | BPP703 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.BPP703_706.BPP703FT02
BR4_Tags | BPP703FT02_HH_A | West Borefield Creek Discharge | High High Flow | BPP703FT02_HH_A | CAT_P2 | WBBWD-Discharge | PRIV_ALARMACK | A_P1_SERV | BPP703FT02_HH_A | BPP703FT02_HH_A | C_HIPRI | BPP703 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.BPP703_706.BPP703FT02
BR4_Tags | BPP703LOS01_A | West Bore Transfer Pump 703 | Lock Off Stop Trip | BPP703LOS01_A | CAT_P1 | WBBWD-1750B004 | PRIV_ALARMACK | A_P1_SERV | Lock Off Stop Trip | BPP703LOS01_A | C_LOPRI | BPP703 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.BPP703_706.BPP703.LOS01
BR4_Tags | BPP703MC01_A | West Bore Transfer Pump 703 | Main Contactor Faulted Trip | BPP703MC01_A | CAT_P3 | WBBWD-1750B004 | PRIV_ALARMACK | A_P1_SERV | Main Contactor Failure | BPP703MC01_A | C_LOPRI | BPP703 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.BPP703_706.BPP703.MC01
BR4_Tags | BPP703PT01_ChOK_A | West Bore Transfer Pumps PLC | Rack 0 Slot 8 Channel 2 Fault | BPP703PT01_ChOK_A | CAT_P3 | BPL752 | PRIV_ALARMACK | A_P1_SERV | Rack 0 Slot 8 Channel 2 Fault | BPP703PT01_ChOK_A | C_LOPRI | BPL752 | Class_Equipment | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.BPP703_706.BPP703PT01
BR4_Tags | BPP703PT01_HiHi_A | West Bore Transfer Pumps | Pressure High High Trip | BPP703PT01_HiHi_A | CAT_P3 | WBBWD-1750B004 | PRIV_ALARMACK | A_P1_SERV | Pressure High High | BPP703PT01_HiHi_A | C_LOPRI | BPP703PT01 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.BPP703_706.BPP703PT01
BR4_Tags | BPP703PT01_LoLo_A | West Bore Transfer Pumps | Pressure Low Low Trip | BPP703PT01_LoLo_A | CAT_P3 | WBBWD-1750B004 | PRIV_ALARMACK | A_P1_SERV | Pressure Low Low | BPP703PT01_LoLo_A | C_LOPRI | BPP703PT01 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.BPP703_706.BPP703PT01
BR4_Tags | BPP703PT01_ROVF_E | West Bore Transfer Pumps PLC | Rack 0 Slot 6 Channel 2 Overflow Error | BPP703PT01_ROVF_E | CAT_P4 | BPL752 | PRIV_ALARMACK | A_P1_SERV | Rack 0 Slot 6 Channel 2 Overflow | BPP703PT01_ROVF_E | C_EVENT | BPL752 | Class_Equipment | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.BPP703_706.BPP703PT01
BR4_Tags | BPP703PT01_RUNF_E | West Bore Transfer Pumps PLC | Rack 0 Slot 6 Channel 2 Underflow Error | BPP703PT01_RUNF_E | CAT_P4 | BPL752 | PRIV_ALARMACK | A_P1_SERV | Rack 0 Slot 6 Channel 2 Underflow | BPP703PT01_RUNF_E | C_EVENT | BPL752 | Class_Equipment | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.BPP703_706.BPP703PT01
BR4_Tags | BPP703PT03_HiHi_A | West Borefield Transfer | Pressure Transmitter Hi Hi Alarm | BPP703PT03_HiHi_A | CAT_P3 | WBBWD-1750B004 | PRIV_ALARMACK | A_P1_SERV | Pressure Transmitter Hi Hi Alarm | BPP703PT03_HiHi_A | C_LOPRI | BPP703PT03 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.BPP703_706.BPP703PT03
BR4_Tags | BPP703SS01_A | West Bore Transfer Pump 703 | Soft Starter Faulted Trip | BPP703SS01_A | CAT_P3 | WBBWD-1750B004 | PRIV_ALARMACK | A_P1_SERV | Soft Starter Tripped | BPP703SS01_A | C_LOPRI | BPP703 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.BPP703_706.BPP703
BR4_Tags | BPP704DCOK_A | West Bore Transfer Pump 704 | 24VDC Power Supply Trip | BPP704DCOK_A | CAT_P3 | WBBWD-1750B004 | PRIV_ALARMACK | A_P1_SERV | Loss of 24 V DC supply | BPP704DCOK_A | C_LOPRI | BPP704 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.BPP703_706.BPP704
BR4_Tags | BPP704LOS01_A | West Bore Transfer Pump 704 | Lock Off Stop Trip | BPP704LOS01_A | CAT_P1 | WBBWD-1750B004 | PRIV_ALARMACK | A_P1_SERV | Lock Off Stop Trip | BPP704LOS01_A | C_LOPRI | BPP704 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.BPP703_706.BPP704.LOS01
BR4_Tags | BPP704MC01_A | West Bore Transfer Pump 704 | Main Contactor Faulted Trip | BPP704MC01_A | CAT_P3 | WBBWD-1750B004 | PRIV_ALARMACK | A_P1_SERV | Main Contactor Failure | BPP704MC01_A | C_LOPRI | BPP704 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.BPP703_706.BPP704.MC01
BR4_Tags | BPP704SS01_A | West Bore Transfer Pump 704 | Soft Starter Faulted Trip | BPP704SS01_A | CAT_P3 | WBBWD-1750B004 | PRIV_ALARMACK | A_P1_SERV | Soft Starter Tripped | BPP704SS01_A | C_LOPRI | BPP704 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.BPP703_706.BPP704
BR4_Tags | BPP705DCOK_A | West Bore Transfer Pump 705 | 24VDC Power Supply Trip | BPP705DCOK_A | CAT_P3 | WBBWD-1750B004 | PRIV_ALARMACK | A_P1_SERV | Loss of 24 V DC supply | BPP705DCOK_A | C_LOPRI | BPP705 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.BPP703_706.BPP705
BR4_Tags | BPP705LOS01_A | West Bore Transfer Pump 705 | Lock Off Stop Trip | BPP705LOS01_A | CAT_P1 | WBBWD-1750B004 | PRIV_ALARMACK | A_P1_SERV | Lock Off Stop Trip | BPP705LOS01_A | C_LOPRI | BPP705 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.BPP703_706.BPP705.LOS01
BR4_Tags | BPP705MC01_A | West Bore Transfer Pump 705 | Main Contactor Faulted Trip | BPP705MC01_A | CAT_P3 | WBBWD-1750B004 | PRIV_ALARMACK | A_P1_SERV | Main Contactor Failure | BPP705MC01_A | C_LOPRI | BPP705 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.BPP703_706.BPP705.MC01
BR4_Tags | BPP705SS01_A | West Bore Transfer Pump 705 | Soft Starter Faulted Trip | BPP705SS01_A | CAT_P3 | WBBWD-1750B004 | PRIV_ALARMACK | A_P1_SERV | Soft Starter Tripped | BPP705SS01_A | C_LOPRI | BPP705 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.BPP703_706.BPP705
BR4_Tags | BPP706DCOK_A | West Bore Transfer Pump 706 | 24VDC Power Supply Trip | BPP706DCOK_A | CAT_P3 | WBBWD-1750B004 | PRIV_ALARMACK | A_P1_SERV | Loss of 24 V DC supply | BPP706DCOK_A | C_LOPRI | BPP706 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.BPP703_706.BPP706
BR4_Tags | BPP706LOS01_A | West Bore Transfer Pump 706 | Lock Off Stop Trip | BPP706LOS01_A | CAT_P1 | WBBWD-1750B004 | PRIV_ALARMACK | A_P1_SERV | Lock Off Stop Trip | BPP706LOS01_A | C_LOPRI | BPP706 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.BPP703_706.BPP706.LOS01
BR4_Tags | BPP706MC01_A | West Bore Transfer Pump 706 | Main Contactor Faulted Trip | BPP706MC01_A | CAT_P3 | WBBWD-1750B004 | PRIV_ALARMACK | A_P1_SERV | Main Contactor Failure | BPP706MC01_A | C_LOPRI | BPP706 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.BPP703_706.BPP706.MC01
BR4_Tags | BPP706SS01_A | West Bore Transfer Pump 706 | Soft Starter Faulted Trip | BPP706SS01_A | CAT_P3 | WBBWD-1750B004 | PRIV_ALARMACK | A_P1_SERV | Soft Starter Tripped | BPP706SS01_A | C_LOPRI | BPP706 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.BPP703_706.BPP706
BR4_Tags | BPP70X_ExcssveFlow_A | West Bore Transfer Pumps | Excessive Flow Trip | BPP70X_ExcssveFlow_A | CAT_P3 | WBBWD-1750B004 | PRIV_ALARMACK | A_P1_SERV | Excessive Flow | BPP70X_ExcssveFlow_A | C_LOPRI | BPP703FT01 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.BPP703_706
BR4_Tags | BPP70X_ExcssveRecirc_A | West Borefield Transfer | Excessive Recirculation Flow | BPP70X_ExcssveRecirc_A | CAT_P3 | WBBWD-1750B004 | PRIV_ALARMACK | A_P1_SERV | Excessive Recirculation Flow | BPP70X_ExcssveRecirc_A | C_LOPRI | BPP703FT01 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.BPP703_706
BR4_Tags | BPP823PWRFAIL_A | Cent Fac Electric Fire Pump | Phase Failure | BPP823PWRFAIL_A | CAT_P1 | WBWD-1750B011 | PRIV_ALARMACK | A_P1_SERV | Phase Failure | BPP823PWRFAIL_A | C_CRITPRI | BPP823 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.CFPFW.BPP823_824.BPP823
BR4_Tags | BPP823RNNG_A | Cent Fac Electric Fire Pump | Running | BPP823RNNG_A | CAT_P1 | WBWD-1750B011 | PRIV_ALARMACK | A_P1_SERV | Running | BPP823RNNG_A | C_CRITPRI | BPP823 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.CFPFW.BPP823_824.BPP823
BR4_Tags | BPP824DCOK_A | Cent Fac Diesel Fire Pump | 24VDC Power Supply Fault | BPP824DCOK_A | CAT_P1 | WBWD-1750B011 | PRIV_ALARMACK | A_P1_SERV | 24 VDC Supply OK | BPP824DCOK_A | C_CRITPRI | BPP824 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.CFPFW.BPP823_824.BPP824
BR4_Tags | BPP824FAILSTT_A | Cent Fac Diesel Fire Pump | Failed to Start | BPP824FAILSTT_A | CAT_P1 | WBWD-1750B011 | PRIV_ALARMACK | A_P1_SERV | Failed to Start | BPP824FAILSTT_A | C_CRITPRI | BPP824 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.CFPFW.BPP823_824.BPP824
BR4_Tags | BPP824FLT_A | Cent Fac Diesel Fire Pump | Faulted | BPP824FLT_A | CAT_P1 | WBWD-1750B011 | PRIV_ALARMACK | A_P1_SERV | Faulted | BPP824FLT_A | C_CRITPRI | BPP824 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.CFPFW.BPP823_824.BPP824
BR4_Tags | BPP824ISLTD_A | Cent Fac Diesel Fire Pump | Isolated | BPP824ISLTD_A | CAT_P1 | WBWD-1750B011 | PRIV_ALARMACK | A_P1_SERV | Isolated | BPP824ISLTD_A | C_CRITPRI | BPP824 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.CFPFW.BPP823_824.BPP824
BR4_Tags | BPP824PWRFAIL_A | Cent Fac Diesel Fire Pump | Low Fuel/Low DC Volts | BPP824PWRFAIL_A | CAT_P1 | WBWD-1750B011 | PRIV_ALARMACK | A_P1_SERV | Low Fuel/Low DC Volts | BPP824PWRFAIL_A | C_CRITPRI | BPP824 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.CFPFW.BPP823_824.BPP824
BR4_Tags | BPP824RNNG_A | Cent Fac Diesel Fire Pump | Pump Running | BPP824RNNG_A | CAT_P1 | WBWD-1750B011 | PRIV_ALARMACK | A_P1_SERV | Running | BPP824RNNG_A | C_CRITPRI | BPP824 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.CFPFW.BPP823_824.BPP824
BR4_Tags | BPP825_ACFlt_E | HV Wash Pump | MNSiS AC Control voltage fault | BPP825_ACFlt_E | CAT_EVENT | WBWD-1750B012 | PRIV_ALARMACK | A_P1_SERV | MNSiS AC Control voltage fault | BPP825_ACFlt_E | C_EVENT | BPP825 | Class_Equipment | BR4_Cluster1 | BR4.UTILITIES.WATER.WBWD.BPP825
BR4_Tags | BPP825_CARemote_E | HV Wash Pump | MNSiS Control Access not in remote | BPP825_CARemote_E | CAT_EVENT | WBWD-1750B012 | PRIV_ALARMACK | A_P1_SERV | MNSiS Control Access not in remote | BPP825_CARemote_E | C_EVENT | BPP825 | Class_Equipment | BR4_Cluster1 | BR4.UTILITIES.WATER.WBWD.BPP825
BR4_Tags | BPP825_DCOK_E | HV Wash Pump | MNSiS DC Control voltage fault | BPP825_DCOK_E | CAT_EVENT | WBWD-1750B012 | PRIV_ALARMACK | A_P1_SERV | MNSiS DC Control voltage fault | BPP825_DCOK_E | C_EVENT | BPP825 | Class_Equipment | BR4_Cluster1 | BR4.UTILITIES.WATER.WBWD.BPP825
BR4_Tags | BPP825_EStop_E | HV Wash Pump | MNSiS Emergency stop active | BPP825_EStop_E | CAT_EVENT | WBWD-1750B012 | PRIV_ALARMACK | A_P1_SERV | MNSiS Emergency stop active | BPP825_EStop_E | C_EVENT | BPP825 | Class_Equipment | BR4_Cluster1 | BR4.UTILITIES.WATER.WBWD.BPP825
BR4_Tags | BPP825_FailSafe_E | HV Wash Pump | MNSiS MControl in fail safe mode | BPP825_FailSafe_E | CAT_EVENT | WBWD-1750B012 | PRIV_ALARMACK | A_P1_SERV | MNSiS MControl in fail safe mode | BPP825_FailSafe_E | C_EVENT | BPP825 | Class_Equipment | BR4_Cluster1 | BR4.UTILITIES.WATER.WBWD.BPP825
BR4_Tags | BPP825_FwdCls_E | HV Wash Pump | MNSiS Forward contractor failed to close | BPP825_FwdCls_E | CAT_EVENT | WBWD-1750B012 | PRIV_ALARMACK | A_P1_SERV | MNSiS Forward contractor failed to close | BPP825_FwdCls_E | C_EVENT | BPP825 | Class_Equipment | BR4_Cluster1 | BR4.UTILITIES.WATER.WBWD.BPP825
BR4_Tags | BPP825_IRFHard_E | HV Wash Pump | MNSiS Internal relay h/w fault trip | BPP825_IRFHard_E | CAT_EVENT | WBWD-1750B012 | PRIV_ALARMACK | A_P1_SERV | MNSiS Internal relay h/w fault trip | BPP825_IRFHard_E | C_EVENT | BPP825 | Class_Equipment | BR4_Cluster1 | BR4.UTILITIES.WATER.WBWD.BPP825
BR4_Tags | BPP825_IRFSoft_E | HV Wash Pump | MNSiS Internal relay s/w fault trip | BPP825_IRFSoft_E | CAT_EVENT | WBWD-1750B012 | PRIV_ALARMACK | A_P1_SERV | MNSiS Internal relay s/w fault trip | BPP825_IRFSoft_E | C_EVENT | BPP825 | Class_Equipment | BR4_Cluster1 | BR4.UTILITIES.WATER.WBWD.BPP825
BR4_Tags | BPP825_IS01Opn_E | HV Wash Pump | MNSiS MStart isolated | BPP825_IS01Opn_E | CAT_EVENT | WBWD-1750B012 | PRIV_ALARMACK | A_P1_SERV | MNSiS MStart isolated | BPP825_IS01Opn_E | C_EVENT | BPP825 | Class_Equipment | BR4_Cluster1 | BR4.UTILITIES.WATER.WBWD.BPP825.IS01
BR4_Tags | BPP825_IS01Test_E | HV Wash Pump | MNSiS Isolator in test position | BPP825_IS01Test_E | CAT_EVENT | WBWD-1750B012 | PRIV_ALARMACK | A_P1_SERV | MNSiS Isolator in test position | BPP825_IS01Test_E | C_EVENT | BPP825 | Class_Equipment | BR4_Cluster1 | BR4.UTILITIES.WATER.WBWD.BPP825.IS01
BR4_Tags | BPP825_MContID_E | HV Wash Pump | MNSiS Location supervision trip | BPP825_MContID_E | CAT_EVENT | WBWD-1750B012 | PRIV_ALARMACK | A_P1_SERV | MNSiS Location supervision trip | BPP825_MContID_E | C_EVENT | BPP825 | Class_Equipment | BR4_Cluster1 | BR4.UTILITIES.WATER.WBWD.BPP825
BR4_Tags | BPP825_MContLife_E | HV Wash Pump | MNSiS MControl life bit not healthy | BPP825_MContLife_E | CAT_EVENT | WBWD-1750B012 | PRIV_ALARMACK | A_P1_SERV | MNSiS MControl life bit not healthy | BPP825_MContLife_E | C_EVENT | BPP825 | Class_Equipment | BR4_Cluster1 | BR4.UTILITIES.WATER.WBWD.BPP825
BR4_Tags | BPP825_MNSiSMainCont_A | HV Wash Pump | MNSiS Main Contactor Faulted Trip | BPP825_MNSiSMainCont_A | CAT_P3 | WBWD-1750B012 | PRIV_ALARMACK | A_P1_SERV | MNSiS Main Contactor Faulted Trip | BPP825_MNSiSMainCont_A | C_LOPRI | BPP825 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBWD.BPP825
BR4_Tags | BPP825_MNSiSOK_A | HV Wash Pump | MCC Starter/Motor Electrical Fault Trip | BPP825_MNSiSOK_A | CAT_P2 | WBWD-1750B012 | PRIV_ALARMACK | A_P1_SERV | MCC Starter/Motor Electrical Fault Trip | BPP825_MNSiSOK_A | C_HIPRI | BPP825 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBWD.BPP825
BR4_Tags | BPP825_MNSiSTrip_E | HV Wash Pump | MNSiS General trip alarm | BPP825_MNSiSTrip_E | CAT_EVENT | WBWD-1750B012 | PRIV_ALARMACK | A_P1_SERV | MNSiS General trip alarm | BPP825_MNSiSTrip_E | C_EVENT | BPP825 | Class_Equipment | BR4_Cluster1 | BR4.UTILITIES.WATER.WBWD.BPP825
BR4_Tags | BPP825_MNSiSWarning_E | HV Wash Pump | MNSiS General warning alarm | BPP825_MNSiSWarning_E | CAT_EVENT | WBWD-1750B012 | PRIV_ALARMACK | A_P1_SERV | MNSiS General warning alarm | BPP825_MNSiSWarning_E | C_EVENT | BPP825 | Class_Equipment | BR4_Cluster1 | BR4.UTILITIES.WATER.WBWD.BPP825
BR4_Tags | BPP825_MStartComms_E | HV Wash Pump | MNSiS Power module comms error | BPP825_MStartComms_E | CAT_EVENT | WBWD-1750B012 | PRIV_ALARMACK | A_P1_SERV | MNSiS Power module comms error | BPP825_MStartComms_E | C_EVENT | BPP825 | Class_Equipment | BR4_Cluster1 | BR4.UTILITIES.WATER.WBWD.BPP825
BR4_Tags | BPP825_MStartID_E | HV Wash Pump | MNSiS Power module ID error | BPP825_MStartID_E | CAT_EVENT | WBWD-1750B012 | PRIV_ALARMACK | A_P1_SERV | MNSiS Power module ID error | BPP825_MStartID_E | C_EVENT | BPP825 | Class_Equipment | BR4_Cluster1 | BR4.UTILITIES.WATER.WBWD.BPP825
BR4_Tags | BPP825_NoLoad_E | HV Wash Pump | MNSiS No load trip level reached | BPP825_NoLoad_E | CAT_EVENT | WBWD-1750B012 | PRIV_ALARMACK | A_P1_SERV | MNSiS No load trip level reached | BPP825_NoLoad_E | C_EVENT | BPP825 | Class_Equipment | BR4_Cluster1 | BR4.UTILITIES.WATER.WBWD.BPP825
BR4_Tags | BPP825_PrmStg1_A | HV Wash Pump Priming Seq | Required Drives and Valves Not Healthy Trip | BPP825_PrmStg1_A | CAT_P3 | WBWD-1750B012 | PRIV_ALARMACK | A_P1_SERV | Required Drives and Valves Not Healthy | BPP825_PrmStg1_A | C_LOPRI | BPP825YV01 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBWD.BPP825
BR4_Tags | BPP825_PrmStg2_A | HV Wash Pump Priming Seq | Required Drives and Valves Faulted Trip | BPP825_PrmStg2_A | CAT_P3 | WBWD-1750B012 | PRIV_ALARMACK | A_P1_SERV | Required Drives and Valves Fault | BPP825_PrmStg2_A | C_LOPRI | BPP825YV01 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBWD.BPP825
BR4_Tags | BPP825_PrmStg3_A | HV Wash Pump Priming Seq | Stage 3 Start Pressure Low Trip | BPP825_PrmStg3_A | CAT_P3 | WBWD-1750B012 | PRIV_ALARMACK | A_P1_SERV | Min Pressure for Pump Start Not Reached | BPP825_PrmStg3_A | C_LOPRI | BPP825YV01 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBWD.BPP825
BR4_Tags | BPP825_PrmStg4_A | HV Wash Pump Priming Seq | Stage 4 Operating Pressure Low Trip | BPP825_PrmStg4_A | CAT_P3 | WBWD-1750B012 | PRIV_ALARMACK | A_P1_SERV | Operating Press Not Reached Priming Failed | BPP825_PrmStg4_A | C_LOPRI | BPP825YV01 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBWD.BPP825
BR4_Tags | BPP825_PrmStg6_A | HV Wash Pump Priming Seq | Stage 6 Operating Pressure Low Trip | BPP825_PrmStg6_A | CAT_P3 | WBWD-1750B012 | PRIV_ALARMACK | A_P1_SERV | Operating Press Not Reached Priming Failed | BPP825_PrmStg6_A | C_LOPRI | BPP825YV01 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBWD.BPP825
BR4_Tags | BPP825_PTCFlt_E | HV Wash Pump | MNSiS PTC trip | BPP825_PTCFlt_E | CAT_EVENT | WBWD-1750B012 | PRIV_ALARMACK | A_P1_SERV | MNSiS PTC trip | BPP825_PTCFlt_E | C_EVENT | BPP825 | Class_Equipment | BR4_Cluster1 | BR4.UTILITIES.WATER.WBWD.BPP825
BR4_Tags | BPP825_RevCls_E | HV Wash Pump | MNSiS Reverse contractor failed to close | BPP825_RevCls_E | CAT_EVENT | WBWD-1750B012 | PRIV_ALARMACK | A_P1_SERV | MNSiS Reverse contractor failed to close | BPP825_RevCls_E | C_EVENT | BPP825 | Class_Equipment | BR4_Cluster1 | BR4.UTILITIES.WATER.WBWD.BPP825
BR4_Tags | BPP825_RunFlt1_E | HV Wash Pump | MNSiS Motor still running fault | BPP825_RunFlt1_E | CAT_EVENT | WBWD-1750B012 | PRIV_ALARMACK | A_P1_SERV | MNSiS Motor still running fault | BPP825_RunFlt1_E | C_EVENT | BPP825 | Class_Equipment | BR4_Cluster1 | BR4.UTILITIES.WATER.WBWD.BPP825
BR4_Tags | BPP825_RunFlt2_E | HV Wash Pump | MNSiS Contactor welded | BPP825_RunFlt2_E | CAT_EVENT | WBWD-1750B012 | PRIV_ALARMACK | A_P1_SERV | MNSiS Contactor welded | BPP825_RunFlt2_E | C_EVENT | BPP825 | Class_Equipment | BR4_Cluster1 | BR4.UTILITIES.WATER.WBWD.BPP825
BR4_Tags | BPP825_RunFlt3_E | HV Wash Pump | MNSiS Motor not running fault | BPP825_RunFlt3_E | CAT_EVENT | WBWD-1750B012 | PRIV_ALARMACK | A_P1_SERV | MNSiS Motor not running fault | BPP825_RunFlt3_E | C_EVENT | BPP825 | Class_Equipment | BR4_Cluster1 | BR4.UTILITIES.WATER.WBWD.BPP825
BR4_Tags | BPP825_Stall_E | HV Wash Pump | MNSiS Motor stall trip level reached | BPP825_Stall_E | CAT_EVENT | WBWD-1750B012 | PRIV_ALARMACK | A_P1_SERV | MNSiS Motor stall trip level reached | BPP825_Stall_E | C_EVENT | BPP825 | Class_Equipment | BR4_Cluster1 | BR4.UTILITIES.WATER.WBWD.BPP825
BR4_Tags | BPP825_SttLmt_E | HV Wash Pump | MNSiS Starting limitation trip | BPP825_SttLmt_E | CAT_EVENT | WBWD-1750B012 | PRIV_ALARMACK | A_P1_SERV | MNSiS Starting limitation trip | BPP825_SttLmt_E | C_EVENT | BPP825 | Class_Equipment | BR4_Cluster1 | BR4.UTILITIES.WATER.WBWD.BPP825
BR4_Tags | BPP825_TOL_E | HV Wash Pump | MNSiS Thermal overload fault | BPP825_TOL_E | CAT_EVENT | WBWD-1750B012 | PRIV_ALARMACK | A_P1_SERV | MNSiS Thermal overload fault | BPP825_TOL_E | C_EVENT | BPP825 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBWD.BPP825
BR4_Tags | BPP825_Underload_E | HV Wash Pump | MNSiS Under load trip level reached | BPP825_Underload_E | CAT_EVENT | WBWD-1750B012 | PRIV_ALARMACK | A_P1_SERV | MNSiS Under load trip level reached | BPP825_Underload_E | C_EVENT | BPP825 | Class_Equipment | BR4_Cluster1 | BR4.UTILITIES.WATER.WBWD.BPP825
BR4_Tags | BPP825FT01_Hi_A | HV Wash Pump Flow | Excessive Flow Trip | BPP825FT01_Hi_A | CAT_P3 | WBWD-1750B012 | PRIV_ALARMACK | A_P1_SERV | Excessive Flow | BPP825FT01_Hi_A | C_LOPRI | BPP825FT01 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBWD.BPP825.FT01
BR4_Tags | BPP825FT01_LoLo_A | HV Wash Pump Flow | Flow Low Low Trip | BPP825FT01_LoLo_A | CAT_P3 | WBWD-1750B012 | PRIV_ALARMACK | A_P1_SERV | Flow Low Low | BPP825FT01_LoLo_A | C_LOPRI | BPP825FT01 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBWD.BPP825.FT01
BR4_Tags | BPP825LOS01_A | HV Wash Pump | Lock Off Stop Trip | BPP825LOS01_A | CAT_P1 | WBWD-1750B012 | PRIV_ALARMACK | A_P1_SERV | Lock Off Stop Trip | BPP825LOS01_A | C_LOPRI | BPP825 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBWD.BPP825.LOS01
BR4_Tags | BPP825ZS01_LmtFlt_A | HV Wash Pump Priming Valve | Opened/Closed Limits Fault Trip | BPP825ZS01_LmtFlt_A | CAT_P3 | WBWD-1750B012 | PRIV_ALARMACK | A_P1_SERV | Limit Switch Fault | BPP825ZS01_LmtFlt_A | C_LOPRI | BPP825YV01 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBWD.BPP825
BR4_Tags | BPP825ZS01A_A | HV Wash Pump Priming Valve | Failed to Open Trip | BPP825ZS01A_A | CAT_P3 | WBWD-1750B012 | PRIV_ALARMACK | A_P1_SERV | Failed to Open | BPP825ZS01A_A | C_LOPRI | BPP825YV01 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBWD.BPP825
BR4_Tags | BPP825ZS01B_A | HV Wash Pump Priming Valve | Failed to Close Trip | BPP825ZS01B_A | CAT_P3 | WBWD-1750B012 | PRIV_ALARMACK | A_P1_SERV | Failed to Close | BPP825ZS01B_A | C_LOPRI | BPP825YV01 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBWD.BPP825
BR4_Tags | BSR1760AC01FLT_A | Proc Wtr Swtchrm Air Cond 1 | Air Conditioner 1 Fault | BSR1760AC01FLT_A | CAT_P3 | SWRBSR1760 | PRIV_ALARMACK | A_CM_POWER | Air Conditioner 1 Fault | BSR1760AC01FLT_A | C_LOPRI | BSR1760AC01 | Class_Process | BR4_Cluster1 | BR4.SRV.PWR.BSR1760.AC01
BR4_Tags | BSR1760AC01HT01_A | Proc Wtr Swtchrm Air Cond 1 | Temperature High | BSR1760AC01HT01_A | CAT_P3 | SWRBSR1760 | PRIV_ALARMACK | A_CM_POWER | Air Conditioner 1 High Temp | BSR1760AC01HT01_A | C_LOPRI | BSR1760AC01 | Class_Process | BR4_Cluster1 | BR4.SRV.PWR.BSR1760.AC01
BR4_Tags | BSR1760AC02FLT_A | Proc Wtr Swtchrm Air Cond 2 | Air Conditioner 2 Fault | BSR1760AC02FLT_A | CAT_P3 | SWRBSR1760 | PRIV_ALARMACK | A_CM_POWER | Air Conditioner 2 Fault | BSR1760AC02FLT_A | C_LOPRI | BSR1760AC02 | Class_Process | BR4_Cluster1 | BR4.SRV.PWR.BSR1760.AC02
BR4_Tags | BSR1760AC02HT01_A | Proc Wtr Swtchrm Air Cond 2 | Temperature High | BSR1760AC02HT01_A | CAT_P3 | SWRBSR1760 | PRIV_ALARMACK | A_CM_POWER | Air Conditioner 2 High Temp | BSR1760AC02HT01_A | C_LOPRI | BSR1760AC02 | Class_Process | BR4_Cluster1 | BR4.SRV.PWR.BSR1760.AC02
BR4_Tags | BSR1760DCOK_A | Proc Wtr Switchroom 1760 | 24VDC Power Supply Trip | BSR1760DCOK_A | CAT_P3 | SWRBSR1760 | PRIV_ALARMACK | A_CM_POWER | 24VDC Supply OK | BSR1760DCOK_A | C_LOPRI | BSR1760 | Class_Process | BR4_Cluster1 | BR4.SRV.PWR.BSR1760
BR4_Tags | BSR1760TE01_Hi_A | Proc Wtr Switchroom 1760 | Temperature High | BSR1760TE01_Hi_A | CAT_P2 | SWRBSR1760 | PRIV_ALARMACK | A_CM_POWER | Temperature High | BSR1760TE01_Hi_A | C_HIPRI | BSR1760 | Class_Process | BR4_Cluster1 | BR4.SRV.PWR.BSR1760.TE01
BR4_Tags | BTF1760TS01_A | Proc Wtr Swtchrm Transformer | Oil Temperature >105 Degrees Celsius | BTF1760TS01_A | CAT_P1 | POWERDIST1 | PRIV_ALARMACK | A_CM_POWER | Oil Temperature >105 Degrees Celsius | BTF1760TS01_A | C_CRITPRI | BTF1760 | Class_Equipment | BR4_Cluster1 | BR4.SRV.PWR.BSR1760.BTF1760
BR4_Tags | BTK702_AvgFlwDiff_A | West Bore Transfer Tank 702 | Cannot Meet User Demand Alarm | BTK702_AvgFlwDiff_A | CAT_P2 | WBBWD-1750B004 | PRIV_ALARMACK | A_P1_SERV | Cannot Meet User Demand Alarm | BTK702_AvgFlwDiff_A | C_HIPRI | BTK702 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.BTK702
BR4_Tags | BTK702_BlwAddPmpPt_A | West Bore Transfer Tank 702 | Level Low and Next Bore Not Starting | BTK702_BlwAddPmpPt_A | CAT_P3 | WBBWD-1750B004 | PRIV_ALARMACK | A_P1_SERV | Level Low and Next Bore Not Starting | BTK702_BlwAddPmpPt_A | C_LOPRI | BTK702 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.BTK702
BR4_Tags | BTK702DCOK_A | West Bore Transfer Tank 702 | 24VDC Power Supply Trip | BTK702DCOK_A | CAT_P3 | WBBWD-1750B004 | PRIV_ALARMACK | A_P1_SERV | Loss of 24 V DC supply | BTK702DCOK_A | C_LOPRI | BTK702 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.BTK702
BR4_Tags | BTK702LS01_A | West Bore Transfer Tank 702 | Level Low Low Trip | BTK702LS01_A | CAT_P3 | WBBWD-1750B004 | PRIV_ALARMACK | A_P1_SERV | Level Low Low Trip | BTK702LS01_A | C_LOPRI | BTK702 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.BTK702
BR4_Tags | BTK702LS02_A | West Bore Transfer Tank 702 | Level High High | BTK702LS02_A | CAT_P3 | WBBWD-1750B004 | PRIV_ALARMACK | A_P1_SERV | Level High High | BTK702LS02_A | C_LOPRI | BTK702 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.BTK702
BR4_Tags | BTK702LSX_A | West Bore Transfer Tank 702 | Level Switch Fault Trip | BTK702LSX_A | CAT_P3 | WBBWD-1750B004 | PRIV_ALARMACK | A_P1_SERV | Level Switch Fault | BTK702LSX_A | C_LOPRI | BTK702 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.BTK702
BR4_Tags | BTK702LT01_ChOK_A | West Bore Transfer Pumps PLC | Rack 0 Slot 8 Channel 1 Fault | BTK702LT01_ChOK_A | CAT_P3 | BPL752 | PRIV_ALARMACK | A_P1_SERV | Rack 0 Slot 8 Channel 1 Fault | BTK702LT01_ChOK_A | C_LOPRI | BPL752 | Class_Equipment | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.BTK702.LT01
BR4_Tags | BTK702LT01_LoLo_A | West Bore Transfer Tank 702 | Level Low Low | BTK702LT01_LoLo_A | CAT_P3 | WBBWD-1750B004 | PRIV_ALARMACK | A_P1_SERV | Level Low Low | BTK702LT01_LoLo_A | C_LOPRI | BTK702 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.BTK702.LT01
BR4_Tags | BTK702LT01_ROVF_E | West Bore Transfer Pumps PLC | Rack 0 Slot 6 Channel 1 Overflow Error | BTK702LT01_ROVF_E | CAT_P4 | BPL752 | PRIV_ALARMACK | A_P1_SERV | Rack 0 Slot 6 Channel 1 Overflow | BTK702LT01_ROVF_E | C_EVENT | BPL752 | Class_Equipment | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.BTK702.LT01
BR4_Tags | BTK702LT01_RUNF_E | West Bore Transfer Pumps PLC | Rack 0 Slot 6 Channel 1 Underflow Error | BTK702LT01_RUNF_E | CAT_P4 | BPL752 | PRIV_ALARMACK | A_P1_SERV | Rack 0 Slot 6 Channel 1 Underflow | BTK702LT01_RUNF_E | C_EVENT | BPL752 | Class_Equipment | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.BTK702.LT01
BR4_Tags | BTK801ALS01_A | Cent Fac Fire Water Tank A | Level Low Low | BTK801ALS01_A | CAT_P2 | WBWD-1750B011 | PRIV_ALARMACK | A_P1_SERV | Level Low Low | BTK801ALS01_A | C_HIPRI | BTK801A | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.CFPFW.BTK801A
BR4_Tags | BTK801ALS02_A | Cent Fac Fire Water Tank A | Not at Full Capacity | BTK801ALS02_A | CAT_P3 | WBWD-1750B011 | PRIV_ALARMACK | A_P1_SERV | Level High High | BTK801ALS02_A | C_LOPRI | BTK801A | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.CFPFW.BTK801A
BR4_Tags | BTK801ALT01_Lo_A | Cent Fac Fire Water Tank A | Level Low | BTK801ALT01_Lo_A | CAT_P2 | WBWD-1750B011 | PRIV_ALARMACK | A_P1_SERV | Level Low | BTK801ALT01_Lo_A | C_HIPRI | BTK801A | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.CFPFW.BTK801A.LT01
BR4_Tags | BTK801BLS01_A | Cent Fac Fire Water Tank B | Level Low Low | BTK801BLS01_A | CAT_P2 | WBWD-1750B011 | PRIV_ALARMACK | A_P1_SERV | Level Low Low Trip | BTK801BLS01_A | C_HIPRI | BTK801B | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.CFPFW.BTK801B
BR4_Tags | BTK801BLS02_A | Cent Fac Fire Water Tank B | Not at Full Capacity | BTK801BLS02_A | CAT_P3 | WBWD-1750B011 | PRIV_ALARMACK | A_P1_SERV | Level High High | BTK801BLS02_A | C_LOPRI | BTK801B | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.CFPFW.BTK801B
BR4_Tags | BTK801BLT01_Lo_A | Cent Fac Fire Water Tank B | Level Low | BTK801BLT01_Lo_A | CAT_P2 | WBWD-1750B011 | PRIV_ALARMACK | A_P1_SERV | Level Low | BTK801BLT01_Lo_A | C_HIPRI | BTK801B | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.CFPFW.BTK801B.LT01
BR4_Tags | BTK801DCOK_A | Cent Fac Fire Water Tank A | 24VDC Power Supply Trip | BTK801DCOK_A | CAT_P3 | WBWD-1750B011 | PRIV_ALARMACK | A_P1_SERV | 24VDC Supply OK | BTK801DCOK_A | C_LOPRI | BTK801A | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.CFPFW.BTK801A
BR4_Tags | BTY702DCOK_A | Proc Wtr Turkeys Nest | 24VDC Power Supply Trip | BTY702DCOK_A | CAT_P3 | WBWD-1750B012 | PRIV_ALARMACK | A_P1_SERV | 24VDC Supply OK | BTY702DCOK_A | C_LOPRI | BTY702 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBWD.BTY702
BR4_Tags | BTY702LS01_A | Proc Wtr Turkeys Nest | Level Switch Low Low Trip | BTY702LS01_A | CAT_P3 | WBWD-1750B012 | PRIV_ALARMACK | A_P1_SERV | Level Switch Low Low Trip | BTY702LS01_A | C_LOPRI | BTY702 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBWD.BTY702
BR4_Tags | BTY702LS02_A | Proc Wtr Turkeys Nest | Level Switch High High Trip | BTY702LS02_A | CAT_P3 | WBWD-1750B012 | PRIV_ALARMACK | A_P1_SERV | Level Switch High High | BTY702LS02_A | C_LOPRI | BTY702 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBWD.BTY702
BR4_Tags | BTY702LSX_A | Proc Wtr Turkeys Nest | Level Switch Fault Trip | BTY702LSX_A | CAT_P3 | WBWD-1750B012 | PRIV_ALARMACK | A_P1_SERV | Level Switch Fault | BTY702LSX_A | C_LOPRI | BTY702 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBWD.BTY702
BR4_Tags | BTY702LT01_HiHi_A | Proc Wtr Turkeys Nest | Level High High Trip | BTY702LT01_HiHi_A | CAT_P3 | WBWD-1750B012 | PRIV_ALARMACK | A_P1_SERV | Level High High | BTY702LT01_HiHi_A | C_LOPRI | BTY702 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBWD.BTY702.LT01
BR4_Tags | BTY702LT01_LoLo_A | Proc Wtr Turkeys Nest | Level Low Low | BTY702LT01_LoLo_A | CAT_P3 | WBWD-1750B012 | PRIV_ALARMACK | A_P1_SERV | Level Low Low | BTY702LT01_LoLo_A | C_LOPRI | BTY702 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBWD.BTY702.LT01
BR4_Tags | BTY702ZS01_LmtFlt_A | Proc Wtr Turkeys Inlet Valve | Opened/Closed Limits Fault Trip | BTY702ZS01_LmtFlt_A | CAT_P3 | WBWD-1750B012 | PRIV_ALARMACK | A_P1_SERV | Shut-Off Valve Limits Fault | BTY702ZS01_LmtFlt_A | C_LOPRI | BTY702LV01 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBWD.BTY702.LV01
BR4_Tags | BTY702ZS01A_A | Proc Wtr Turkeys Inlet Valve | Failed to Open Trip | BTY702ZS01A_A | CAT_P3 | WBWD-1750B012 | PRIV_ALARMACK | A_P1_SERV | Failed to Open Trip | BTY702ZS01A_A | C_LOPRI | BTY702LV01 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBWD.BTY702.LV01
BR4_Tags | BTY702ZS01B_A | Proc Wtr Turkeys Inlet Valve | Failed to Close Trip | BTY702ZS01B_A | CAT_P3 | WBWD-1750B012 | PRIV_ALARMACK | A_P1_SERV | Failed to Close Trip | BTY702ZS01B_A | C_LOPRI | BTY702LV01 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBWD.BTY702.LV01
BR4_Tags | BWA701PS_A | East Bore Water Accum | Pressure Switch Fault Trip | BWA701PS_A | CAT_P3 | EBBWD-1750B001 | PRIV_ALARMACK | A_P1_SERV | Pressure Switch Fault Alarm | BWA701PS_A | C_LOPRI | BWA701 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.EBBWD.BWA701
BR4_Tags | BWA701PSL_A | East Bore Water Accum | Pressure Low | BWA701PSL_A | CAT_P3 | EBBWD-1750B001 | PRIV_ALARMACK | A_P1_SERV | Pressure Low | BWA701PSL_A | C_LOPRI | BWA701 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.EBBWD.BWA701
BR4_Tags | BWA803_LmtFlt_A | HV Wash Pump Accumulator | Pressure Switch Fault Trip | BWA803_LmtFlt_A | CAT_P3 | WBWD-1750B012 | PRIV_ALARMACK | A_P1_SERV | Pressure Switch Fault | BWA803_LmtFlt_A | C_LOPRI | BWA803 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBWD.BWA803
BR4_Tags | BWA803DCOK_A | HV Wash Pump | 24VDC Power Supply Trip | BWA803DCOK_A | CAT_P3 | WBWD-1750B012 | PRIV_ALARMACK | A_P1_SERV | 24 VDC Supply OK | BWA803DCOK_A | C_LOPRI | BPP825 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBWD.BWA803
BR4_Tags | DWB10PT01_Hi_A | East Dewatering Bore 10 | Upstream Pressure Hi | DWB10PT01_Hi_A | CAT_P3 | EBBWD-1750B001 | PRIV_ALARMACK | A_P1_SERV | Upstream Pressure Hi | DWB10PT01_Hi_A | C_LOPRI | DWB10 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.EBBWD.DWB10.PT01
BR4_Tags | DWB10PT01_HiHi_A | East Dewatering Bore 10 | Upstream Pressure HiHi | DWB10PT01_HiHi_A | CAT_P3 | EBBWD-1750B001 | PRIV_ALARMACK | A_P1_SERV | Upstream Pressure HiHi | DWB10PT01_HiHi_A | C_LOPRI | DWB10 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.EBBWD.DWB10.PT01
BR4_Tags | DWB10PT02_Hi_A | East Dewatering Bore 10 | Downstream Pressure Hi | DWB10PT02_Hi_A | CAT_P3 | EBBWD-1750B001 | PRIV_ALARMACK | A_P1_SERV | Downstream Pressure Hi | DWB10PT02_Hi_A | C_LOPRI | DWB10 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.EBBWD.DWB10.PT02
BR4_Tags | DWB10PT02_HiHi_A | East Dewatering Bore 10 | Downstream Pressure HiHi | DWB10PT02_HiHi_A | CAT_P3 | EBBWD-1750B001 | PRIV_ALARMACK | A_P1_SERV | Downstream Pressure HiHi | DWB10PT02_HiHi_A | C_LOPRI | DWB10 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.EBBWD.DWB10.PT02
BR4_Tags | DWB10_NotRnng_A | East Dewatering Bore 10 | Pump Not Running - Genset Shutdown | DWB10_NotRnng_A | CAT_P3 | EBBWD-1750B001 | PRIV_ALARMACK | A_P1_SERV | Pump Not Running - Genset Shutdown | DWB10_NotRnng_A | C_LOPRI | DWB10 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.EBBWD.DWB10
BR4_Tags | DWB10_Stt_A | East Dewatering Bore 10 | Too Many Starts Trip | DWB10_Stt_A | CAT_P3 | EBBWD-1750B001 | PRIV_ALARMACK | A_P1_SERV | Too Many Starts | DWB10_Stt_A | C_LOPRI | DWB10 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.EBBWD.DWB10
BR4_Tags | DWB10DCOK_A | East Dewatering Bore 10 | 24VDC Power Supply Trip | DWB10DCOK_A | CAT_P3 | EBBWD-1750B001 | PRIV_ALARMACK | A_P1_SERV | Loss Of 24 VDC Supply | DWB10DCOK_A | C_LOPRI | DWB10 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.EBBWD.DWB10
BR4_Tags | DWB10FT01_Lo_A | East Dewatering Bore 10 | Flow Low Trip | DWB10FT01_Lo_A | CAT_P3 | EBBWD-1750B001 | PRIV_ALARMACK | A_P1_SERV | Flow Low | DWB10FT01_Lo_A | C_LOPRI | DWB10 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.EBBWD.DWB10.FT01
BR4_Tags | DWB10LOS01_A | East Dewatering Bore 10 | Lock Off Stop Trip | DWB10LOS01_A | CAT_P1 | EBBWD-1750B001 | PRIV_ALARMACK | A_P1_SERV | Lock Off Stop Trip | DWB10LOS01_A | C_LOPRI | DWB10 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.EBBWD.DWB10.LOS01
BR4_Tags | DWB10LSL_A | East Dewatering Bore 10 | Level Low Trip | DWB10LSL_A | CAT_P3 | EBBWD-1750B001 | PRIV_ALARMACK | A_P1_SERV | Level Low | DWB10LSL_A | C_LOPRI | DWB10 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.EBBWD.DWB10
BR4_Tags | DWB10MC01_A | East Dewatering Bore 10 | Main Contactor Faulted Trip | DWB10MC01_A | CAT_P3 | EBBWD-1750B001 | PRIV_ALARMACK | A_P1_SERV | Main Contactor Fault | DWB10MC01_A | C_LOPRI | DWB10 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.EBBWD.DWB10.MC01
BR4_Tags | DWB10SS01_A | East Dewatering Bore 10 | Soft Starter Faulted Trip | DWB10SS01_A | CAT_P3 | EBBWD-1750B001 | PRIV_ALARMACK | A_P1_SERV | Soft Starter Fault | DWB10SS01_A | C_LOPRI | DWB10 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.EBBWD.DWB10
BR4_Tags | TKN01PLCM01OK_A | Proc Wtr Switchroom 1760 | Serial Device Server Fail | TKN01PLCM01OK_A | CAT_P3 | BPL760 | PRIV_ALARMACK | A_P1_SERV | Serial Device Server Fail | TKN01PLCM01OK_A | C_LOPRI | BPL760 | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL760
BR4_Tags | WSPB2_Stt_A | Bore | Too Many Starts Trip | WSPB2_Stt_A | CAT_P3 | WBBWD-1750B004 | PRIV_ALARMACK | A_P1_SERV | Too Many Starts Alarm | WSPB2_Stt_A | C_LOPRI | WSPB2 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.WSPB2
BR4_Tags | WSPB2_DCOK01_A | Bore | 24VDC Power Supply Trip | WSPB2_DCOK01_A | CAT_P3 | WBBWD-1750B004 | PRIV_ALARMACK | A_P1_SERV | 24VDC Power Supply Trip | WSPB2_DCOK01_A | C_LOPRI | WSPB2 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.WSPB2
BR4_Tags | WSPB2_FT01_Lo_A | Bore | Flow Low Trip | WSPB2_FT01_Lo_A | CAT_P3 | WBBWD-1750B004 | PRIV_ALARMACK | A_P1_SERV | Flow Low Trip | WSPB2_FT01_Lo_A | C_LOPRI | WSPB2 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.WSPB2
BR4_Tags | WSPB2_LOS01_A | Bore | Lock Off Stop Trip | WSPB2_LOS01_A | CAT_P1 | WBBWD-1750B004 | PRIV_ALARMACK | A_P1_SERV | Lock Off Stop Trip | WSPB2_LOS01_A | C_LOPRI | WSPB2 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.WSPB2
BR4_Tags | WSPB2_LSL_A | Bore | Level Low Trip | WSPB2_LSL_A | CAT_P3 | WBBWD-1750B004 | PRIV_ALARMACK | A_P1_SERV | Level Low Trip | WSPB2_LSL_A | C_LOPRI | WSPB2 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.WSPB2
BR4_Tags | WSPB2_MC01_A | Bore | Main Contactor Faulted Trip | WSPB2_MC01_A | CAT_P3 | WBBWD-1750B004 | PRIV_ALARMACK | A_P1_SERV | Main Contactor Faulted Trip | WSPB2_MC01_A | C_LOPRI | WSPB2 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.WSPB2
BR4_Tags | WSPB2_SS01_A | Bore | Soft Starter Faulted Trip | WSPB2_SS01_A | CAT_P3 | WBBWD-1750B004 | PRIV_ALARMACK | A_P1_SERV | Soft Starter Faulted Trip | WSPB2_SS01_A | C_LOPRI | WSPB2 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.WSPB2
BR4_Tags | B308S_Commn_E | Bore | Common Warning Alarm | B308S_Commn_E | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B308S_Commn_E | C_LOPRI | B308S | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B308S
BR4_Tags | B308S_CommnSd_A | Bore | Common Shutdown Alarm | B308S_CommnSd_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B308S_CommnSd_A | C_LOPRI | B308S | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B308S
BR4_Tags | B308S_CommsFlt_A | Bore | Comms Fail | B308S_CommsFlt_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B308S_CommsFlt_A | C_LOPRI | B308S | Class_Equipment | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B308S
BR4_Tags | B308S_CurrUnbal_A | Bore | Phase Current Imbalance | B308S_CurrUnbal_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B308S_CurrUnbal_A | C_LOPRI | B308S | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B308S
BR4_Tags | B308S_EARTH_A | Bore | Earth Leakage Shutdown | B308S_EARTH_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B308S_EARTH_A | C_LOPRI | B308S | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B308S
BR4_Tags | B308S_ECR_A | Bore | Earth Continuity Shutdown | B308S_ECR_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B308S_ECR_A | C_LOPRI | B308S | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B308S
BR4_Tags | B308S_ECR_Overide_A | Bore | ECR Bypass On | B308S_ECR_Overide_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B308S_ECR_Overide_A | C_LOPRI | B308S | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B308S
BR4_Tags | B308S_ECU_A | Bore | ECU Shutdown Fault | B308S_ECU_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B308S_ECU_A | C_LOPRI | B308S | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B308S
BR4_Tags | B308S_ECUWarning_E | Bore | ECU Warning Fault | B308S_ECUWarning_E | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B308S_ECUWarning_E | C_LOPRI | B308S | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B308S
BR4_Tags | B308S_FT01_Lo_A | Bore | Flow Low Warning | B308S_FT01_Lo_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B308S_FT01_Lo_A | C_LOPRI | B308S | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B308S.FT01
BR4_Tags | B308S_FT01_LoLo_A | Bore | Flow Low Low Shutdown | B308S_FT01_LoLo_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B308S_FT01_LoLo_A | C_LOPRI | B308S | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B308S.FT01
BR4_Tags | B308S_LOS_A | Bore | Emergency Stop Shutdown | B308S_LOS_A | CAT_P1 |  | PRIV_ALARMACK | A_P1_SERV |  | B308S_LOS_A | C_LOPRI | B308S | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B308S
BR4_Tags | B308S_LT01_Lo_A | Bore | Low Bore Level Warning | B308S_LT01_Lo_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B308S_LT01_Lo_A | C_LOPRI | B308S | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B308S.LT01
BR4_Tags | B308S_LT01_LoLo_A | Bore | Low Bore Level Shutdown | B308S_LT01_LoLo_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B308S_LT01_LoLo_A | C_LOPRI | B308S | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B308S.LT01
BR4_Tags | B308S_LT02_Lo_A | Bore | Low Fuel Warning | B308S_LT02_Lo_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B308S_LT02_Lo_A | C_LOPRI | B308S | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B308S.LT02
BR4_Tags | B308S_LT02_LoLo_A | Bore | Low Fuel Shutdown | B308S_LT02_LoLo_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B308S_LT02_LoLo_A | C_LOPRI | B308S | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B308S.LT02
BR4_Tags | B308S_MCB_A | Bore | Main Breaker Tripped | B308S_MCB_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B308S_MCB_A | C_LOPRI | B308S | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B308S.MCB
BR4_Tags | B308S_OverCurr_A | Bore | Over Current Shutdown | B308S_OverCurr_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B308S_OverCurr_A | C_LOPRI | B308S | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B308S
BR4_Tags | B308S_OverVolt_A | Bore | Over Voltage Shutdown | B308S_OverVolt_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B308S_OverVolt_A | C_LOPRI | B308S | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B308S
BR4_Tags | B308S_PT01_Hi_A | Bore | High Upstream Pressure Warning | B308S_PT01_Hi_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B308S_PT01_Hi_A | C_LOPRI | B308S | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B308S.PT01
BR4_Tags | B308S_PT01_HiHi_A | Bore | High Upstream Pressure Shutdown | B308S_PT01_HiHi_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B308S_PT01_HiHi_A | C_LOPRI | B308S | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B308S.PT01
BR4_Tags | B308S_PT02_Hi_A | Bore | High Downstream Pressure Warning | B308S_PT02_Hi_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B308S_PT02_Hi_A | C_LOPRI | B308S | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B308S.PT02
BR4_Tags | B308S_PT02_HiHi_A | Bore | High Downstream Pressure Shutdown | B308S_PT02_HiHi_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B308S_PT02_HiHi_A | C_LOPRI | B308S | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B308S.PT02
BR4_Tags | B308S_RnngFail_A | Bore | Failed while Running | B308S_RnngFail_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B308S_RnngFail_A | C_LOPRI | B308S | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B308S
BR4_Tags | B308S_StpFail_A | Bore | Failed to Stop | B308S_StpFail_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B308S_StpFail_A | C_LOPRI | B308S | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B308S
BR4_Tags | B308S_Stt_A | Bore | Excessive Starts | B308S_Stt_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B308S_Stt_A | C_LOPRI | B308S | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B308S
BR4_Tags | B308S_SttFail_A | Bore | Failed to Start | B308S_SttFail_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B308S_SttFail_A | C_LOPRI | B308S | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B308S
BR4_Tags | B308S_TOL01_A | Bore | Thermal Overload Shutdown | B308S_TOL01_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B308S_TOL01_A | C_LOPRI | B308S | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B308S
BR4_Tags | B308S_TT01_Hi_A | Bore | High Pump Temp Warning | B308S_TT01_Hi_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B308S_TT01_Hi_A | C_LOPRI | B308S | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B308S.TT01
BR4_Tags | B308S_TT01_HiHi_A | Bore | High Pump Temp Shutdown | B308S_TT01_HiHi_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV |  | B308S_TT01_HiHi_A | C_LOPRI | B308S | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.B308S.TT01
BR4_Tags | WSPB7_FT01_LoLo_A | Bore | Flow Lo Lo Alarm | WSPB7_FT01_LoLo_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV | Flow Lo Lo Alarm | WSPB7_FT01_LoLo_A | C_LOPRI | WSPB7 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.WSPB7.FT01
BR4_Tags | WSPB7_HMI01RTUFlt_A | Bore | Local HMI01 Serial Comms Fault (Warning) | WSPB7_HMI01RTUFlt_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV | Local HMI01 Serial Comms Fault (Warning) | WSPB7_HMI01RTUFlt_A | C_LOPRI | WSPB7 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.WSPB7
BR4_Tags | WSPB7_LOS01_A | Bore | Remote Lock Off Stop Trip | WSPB7_LOS01_A | CAT_P1 |  | PRIV_ALARMACK | A_P1_SERV | Remote Lock Off Stop Trip | WSPB7_LOS01_A | C_LOPRI | WSPB7 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.WSPB7
BR4_Tags | WSPB7_LT01_LoLo_A | Bore | Bore Level Lo Lo Alarm | WSPB7_LT01_LoLo_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV | Bore Level Lo Lo Alarm | WSPB7_LT01_LoLo_A | C_LOPRI | WSPB7 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.WSPB7.LT01
BR4_Tags | WSPB7_MC01_A | Bore | Main Contactor Alarm | WSPB7_MC01_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV | Main Contactor Alarm | WSPB7_MC01_A | C_LOPRI | WSPB7 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.WSPB7.MC01
BR4_Tags | WSPB7_PT01_HiHi_A | Bore | Upstream Pressure Hi Hi Fault | WSPB7_PT01_HiHi_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV | Upstream Pressure Hi Hi Fault | WSPB7_PT01_HiHi_A | C_LOPRI | WSPB7 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.WSPB7.PT01
BR4_Tags | WSPB7_PT02_HiHi_A | Bore | Downstream Pressure Hi Hi Fault | WSPB7_PT02_HiHi_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV | Downstream Pressure Hi Hi Fault | WSPB7_PT02_HiHi_A | C_LOPRI | WSPB7 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.WSPB7.PT02
BR4_Tags | WSPB7_SD01Flt_A | Bore | Surge Diverter Faulted Alarm | WSPB7_SD01Flt_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV | Surge Diverter Faulted Alarm | WSPB7_SD01Flt_A | C_LOPRI | WSPB7 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.WSPB7
BR4_Tags | WSPB7_Stt_A | Bore | Too Many Starts Alarm | WSPB7_Stt_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV | Too Many Starts Alarm | WSPB7_Stt_A | C_LOPRI | WSPB7 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.WSPB7
BR4_Tags | WSPB7_SttFail_A | Bore | VSD Failed to Start | WSPB7_SttFail_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV | VSD Failed to Start | WSPB7_SttFail_A | C_LOPRI | WSPB7 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.WSPB7.VSD
BR4_Tags | WSPB7_TOL01_A | Bore | Motor Overload (from VSD) | WSPB7_TOL01_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV | Motor Overload (from VSD) | WSPB7_TOL01_A | C_LOPRI | WSPB7 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.WSPB7.VSD
BR4_Tags | WSPB7_TT01_Hi_A | Bore | Temperature Hi Warning Alarm | WSPB7_TT01_Hi_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV | Temperature Hi Warning Alarm | WSPB7_TT01_Hi_A | C_LOPRI | WSPB7 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.WSPB7.TT01
BR4_Tags | WSPB7_TT01_HiHi_A | Bore | Motor Temperature Hi Hi | WSPB7_TT01_HiHi_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV | Motor Temperature Hi Hi | WSPB7_TT01_HiHi_A | C_LOPRI | WSPB7 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.WSPB7.TT01
BR4_Tags | WSPB7_VSDCommsFlt_A | Bore | VSD Comms Fault (Warning) | WSPB7_VSDCommsFlt_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV | VSD Comms Fault (Warning) | WSPB7_VSDCommsFlt_A | C_LOPRI | WSPB7 | Class_Equipment | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.WSPB7.VSD
BR4_Tags | WSPB7_VSDFlt_A | Bore | VSD Fault Alarm | WSPB7_VSDFlt_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV | VSD Fault Alarm | WSPB7_VSDFlt_A | C_LOPRI | WSPB7 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.WSPB7.VSD
BR4_Tags | WSPB7_VSD01PR01_A | Bore | Hard Wired Interlocks Protection Relay Fault | WSPB7_VSD01PR01_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV | Hard Wired Interlocks Protection Relay Fault | WSPB7_VSD01PR01_A | C_LOPRI | WSPB7 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.WSPB7.VSD
BR4_Tags | WSPB7_PT01_LoLo_A | Bore | Upstream Pressure Lo Lo Fault | WSPB7_PT01_LoLo_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV | Upstream Pressure Lo Lo Fault | WSPB7_PT01_LoLo_A | C_LOPRI | WSPB7 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.WSPB7.PT01
BR4_Tags | WSPB7_PT02_LoLo_A | Bore | Downstreamstream Pressure Lo Lo Fault | WSPB7_PT02_LoLo_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV | Downstreamstream Pressure Lo Lo Fault | WSPB7_PT02_LoLo_A | C_LOPRI | WSPB7 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.WSPB7.PT02
BR4_Tags | WSPB7_R0S2OK_A | Bore | Rack 0 Slot 2 Module Fault | WSPB7_R0S2OK_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV | Rack 0 Slot 2 Module Fault | WSPB7_R0S2OK_A | C_LOPRI | WSPB7 | Class_Equipment | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.WSPB7
BR4_Tags | WSPB7_R0S3OK_A | Bore | Rack 0 Slot 3 Module Fault | WSPB7_R0S3OK_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV | Rack 0 Slot 3 Module Fault | WSPB7_R0S3OK_A | C_LOPRI | WSPB7 | Class_Equipment | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.WSPB7
BR4_Tags | WSPB7_R0S4OK_A | Bore | Rack 0 Slot 4 Module Fault | WSPB7_R0S4OK_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV | Rack 0 Slot 4 Module Fault | WSPB7_R0S4OK_A | C_LOPRI | WSPB7 | Class_Equipment | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.WSPB7
BR4_Tags | WSPB7_R0S5OK_A | Bore | Rack 0 Slot 5 Module Fault | WSPB7_R0S5OK_A | CAT_P3 |  | PRIV_ALARMACK | A_P1_SERV | Rack 0 Slot 5 Module Fault | WSPB7_R0S5OK_A | C_LOPRI | WSPB7 | Class_Equipment | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.WSPB7
BR4_Tags | BP1590_LOS_A | Bore | Drive LOS Alarm | BP1590_LOS_A | CAT_P1 | EBBWD-1750B001 | PRIV_ALARMACK | A_P1_SERV | BP1590_LOS_A | BP1590_LOS_A | C_LOPRI | BP1590 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.EBBWD.BP1590
BR4_Tags | BP1590_ECR_FLT_A | Bore | ECR Fault | BP1590_ECR_FLT_A | CAT_P3 | EBBWD-1750B001 | PRIV_ALARMACK | A_P1_SERV | BP1590_ECR_FLT_A | BP1590_ECR_FLT_A | C_LOPRI | BP1590 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.EBBWD.BP1590
BR4_Tags | BP1590_ELR_FLT_A | Bore | ELR Fault | BP1590_ELR_FLT_A | CAT_P3 | EBBWD-1750B001 | PRIV_ALARMACK | A_P1_SERV | BP1590_ELR_FLT_A | BP1590_ELR_FLT_A | C_LOPRI | BP1590 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.EBBWD.BP1590
BR4_Tags | BP1590_CB_A | Bore | CB Trip | BP1590_CB_A | CAT_P3 | EBBWD-1750B001 | PRIV_ALARMACK | A_P1_SERV | BP1590_CB_A | BP1590_CB_A | C_LOPRI | BP1590 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.EBBWD.BP1590
BR4_Tags | BP1590_ECUShutDown_A | Bore | ECU Trip | BP1590_ECUShutDown_A | CAT_P3 | EBBWD-1750B001 | PRIV_ALARMACK | A_P1_SERV | BP1590_ECUShutDown_A | BP1590_ECUShutDown_A | C_LOPRI | BP1590 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.EBBWD.BP1590
BR4_Tags | BP1590_PT02_HIHI_A | Bore | Downstream Pressure HiHi | BP1590_PT02_HIHI_A | CAT_P3 | EBBWD-1750B001 | PRIV_ALARMACK | A_P1_SERV | BP1590_PT02_HIHI_A | BP1590_PT02_HIHI_A | C_LOPRI | BP1590 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.EBBWD.BP1590.PT02
BR4_Tags | BP1590_FT01_LOLO_A | Bore | Discharge Flow LoLo | BP1590_FT01_LOLO_A | CAT_P3 | EBBWD-1750B001 | PRIV_ALARMACK | A_P1_SERV | BP1590_FT01_LOLO_A | BP1590_FT01_LOLO_A | C_LOPRI | BP1590 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.EBBWD.BP1590.FT01
BR4_Tags | BP1590_LT03_LOLO_A | Bore | External Fuel Tank LoLo | BP1590_LT03_LOLO_A | CAT_P3 | EBBWD-1750B001 | PRIV_ALARMACK | A_P1_SERV | BP1590_LT03_LOLO_A | BP1590_LT03_LOLO_A | C_LOPRI | BP1590 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.EBBWD.BP1590.LT03
BR4_Tags | BP1590_PT01_HIHI_A | Bore | Upstream Pressure HiHI | BP1590_PT01_HIHI_A | CAT_P3 | EBBWD-1750B001 | PRIV_ALARMACK | A_P1_SERV | BP1590_PT01_HIHI_A | BP1590_PT01_HIHI_A | C_LOPRI | BP1590 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.EBBWD.BP1590.PT01
BR4_Tags | BP1590_LT01_LOLO_A | Bore | Bore Level LoLo | BP1590_LT01_LOLO_A | CAT_P3 | EBBWD-1750B001 | PRIV_ALARMACK | A_P1_SERV | BP1590_LT01_LOLO_A | BP1590_LT01_LOLO_A | C_LOPRI | BP1590 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.EBBWD.BP1590.LT01
BR4_Tags | BP1590_RmtFailWhileRng_A | Bore | Failed While Running | BP1590_RmtFailWhileRng_A | CAT_P3 | EBBWD-1750B001 | PRIV_ALARMACK | A_P1_SERV | BP1590_RmtFailWhileRng_A | BP1590_RmtFailWhileRng_A | C_LOPRI | BP1590 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.EBBWD.BP1590
BR4_Tags | BP1590_StartFail_A | Bore | Failed to Start | BP1590_StartFail_A | CAT_P3 | EBBWD-1750B001 | PRIV_ALARMACK | A_P1_SERV | BP1590_StartFail_A | BP1590_StartFail_A | C_LOPRI | BP1590 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.EBBWD.BP1590
BR4_Tags | BP1590_StopFail_A | Bore | Failed to Stop | BP1590_StopFail_A | CAT_P3 | EBBWD-1750B001 | PRIV_ALARMACK | A_P1_SERV | BP1590_StopFail_A | BP1590_StopFail_A | C_LOPRI | BP1590 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.EBBWD.BP1590
BR4_Tags | BP1590_OverCurr_A | Bore | Overload | BP1590_OverCurr_A | CAT_P3 | EBBWD-1750B001 | PRIV_ALARMACK | A_P1_SERV | BP1590_OverCurr_A | BP1590_OverCurr_A | C_LOPRI | BP1590 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.EBBWD.BP1590
BR4_Tags | BP1590_ShortCurr_A | Bore | Over Current Short | BP1590_ShortCurr_A | CAT_P3 | EBBWD-1750B001 | PRIV_ALARMACK | A_P1_SERV | BP1590_ShortCurr_A | BP1590_ShortCurr_A | C_LOPRI | BP1590 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.EBBWD.BP1590
BR4_Tags | BP1590_CommnSd_A | Bore | Common Shutdown | BP1590_CommnSd_A | CAT_P3 | EBBWD-1750B001 | PRIV_ALARMACK | A_P1_SERV | BP1590_CommnSd_A | BP1590_CommnSd_A | C_LOPRI | BP1590 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.EBBWD.BP1590
BR4_Tags | BP1590_GenVoltLimit_A | Bore | Gen Voltage Limit | BP1590_GenVoltLimit_A | CAT_P3 | EBBWD-1750B001 | PRIV_ALARMACK | A_P1_SERV | BP1590_GenVoltLimit_A | BP1590_GenVoltLimit_A | C_LOPRI | BP1590 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.EBBWD.BP1590
BR4_Tags | BP1590_GenCurrUnbal_A | Bore | Current Unbalance | BP1590_GenCurrUnbal_A | CAT_P3 | EBBWD-1750B001 | PRIV_ALARMACK | A_P1_SERV | BP1590_GenCurrUnbal_A | BP1590_GenCurrUnbal_A | C_LOPRI | BP1590 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.EBBWD.BP1590
BR4_Tags | BP1590_LT02_LOLO_A | Bore | Internal Fuel Tank LoLo | BP1590_LT02_LOLO_A | CAT_P3 | EBBWD-1750B001 | PRIV_ALARMACK | A_P1_SERV | BP1590_LT02_LOLO_A | BP1590_LT02_LOLO_A | C_LOPRI | BP1590 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.EBBWD.BP1590.LT02
BR4_Tags | BP1590_ISOL_DOOR_A | Bore | Isolator Door Open | BP1590_ISOL_DOOR_A | CAT_P3 | EBBWD-1750B001 | PRIV_ALARMACK | A_P1_SERV | BP1590_ISOL_DOOR_A | BP1590_ISOL_DOOR_A | C_LOPRI | BP1590 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.EBBWD.BP1590
BR4_Tags | BP1590_NoFuelTkSel_A | Bore | No Fuel Tank Selected | BP1590_NoFuelTkSel_A | CAT_P3 | EBBWD-1750B001 | PRIV_ALARMACK | A_P1_SERV | BP1590_NoFuelTkSel_A | BP1590_NoFuelTkSel_A | C_LOPRI | BP1590 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.EBBWD.BP1590
BR4_Tags | BP1590_TT04_A | Bore | Intake Temperature Fault | BP1590_TT04_A | CAT_P3 | EBBWD-1750B001 | PRIV_ALARMACK | A_P1_SERV | BP1590_TT04_A | BP1590_TT04_A | C_LOPRI | BP1590 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.EBBWD.BP1590.TT04
BR4_Tags | BP1590_TT03_A | Bore | Coolant Temp Fault(ECU) | BP1590_TT03_A | CAT_P3 | EBBWD-1750B001 | PRIV_ALARMACK | A_P1_SERV | BP1590_TT03_A | BP1590_TT03_A | C_LOPRI | BP1590 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.EBBWD.BP1590.TT03
BR4_Tags | BP1590_PT04_A | Bore | Oil Pressure Fault | BP1590_PT04_A | CAT_P3 | EBBWD-1750B001 | PRIV_ALARMACK | A_P1_SERV | BP1590_PT04_A | BP1590_PT04_A | C_LOPRI | BP1590 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.EBBWD.BP1590.PT04
BR4_Tags | BP1590_TT01_HIHI_A | Bore | Motor Temp HiHi | BP1590_TT01_HIHI_A | CAT_P3 | EBBWD-1750B001 | PRIV_ALARMACK | A_P1_SERV | BP1590_TT01_HIHI_A | BP1590_TT01_HIHI_A | C_LOPRI | BP1590 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.EBBWD.BP1590.TT01
BR4_Tags | BP1590_PT03_HIHI_A | Bore | Boost Pressure HiHi | BP1590_PT03_HIHI_A | CAT_P3 | EBBWD-1750B001 | PRIV_ALARMACK | A_P1_SERV | BP1590_PT03_HIHI_A | BP1590_PT03_HIHI_A | C_LOPRI | BP1590 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.EBBWD.BP1590.PT03
BR4_Tags | BP1590_Stt_A | Bore | Too Many Starts | BP1590_Stt_A | CAT_P3 | EBBWD-1750B001 | PRIV_ALARMACK | A_P1_SERV | BP1590_Stt_A | BP1590_Stt_A | C_LOPRI | BP1590 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.EBBWD.BP1590
BR4_Tags | BP1590_TT03_HIHI_A | Bore | Coolant Temp HiHi | BP1590_TT03_HIHI_A | CAT_P3 | EBBWD-1750B001 | PRIV_ALARMACK | A_P1_SERV | BP1590_TT03_HIHI_A | BP1590_TT03_HIHI_A | C_LOPRI | BP1590 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.EBBWD.BP1590.TT03
BR4_Tags | BP1590_Commn_A | Bore | Common Alarm | BP1590_Commn_A | CAT_P3 | EBBWD-1750B001 | PRIV_ALARMACK | A_P1_SERV | BP1590_Commn_A | BP1590_Commn_A | C_LOPRI | BP1590 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.EBBWD.BP1590
BR4_Tags | BP1590_ECR_Overide_A | Bore | ECR Override is on | BP1590_ECR_Overide_A | CAT_P3 | EBBWD-1750B001 | PRIV_ALARMACK | A_P1_SERV | BP1590_ECR_Overide_A | BP1590_ECR_Overide_A | C_LOPRI | BP1590 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.EBBWD.BP1590
BR4_Tags | BP1590_LT01_Lo_A | Bore | Bore Level Lo Warn | BP1590_LT01_Lo_A | CAT_P3 | EBBWD-1750B001 | PRIV_ALARMACK | A_P1_SERV | BP1590_LT01_Lo_A | BP1590_LT01_Lo_A | C_LOPRI | BP1590 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.EBBWD.BP1590.LT01
BR4_Tags | BP1590_TT01_Hi_A | Bore | Motor Temp Hi Warn | BP1590_TT01_Hi_A | CAT_P3 | EBBWD-1750B001 | PRIV_ALARMACK | A_P1_SERV | BP1590_TT01_Hi_A | BP1590_TT01_Hi_A | C_LOPRI | BP1590 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.EBBWD.BP1590.TT01
BR4_Tags | BP1590_PT01_Hi_A | Bore | Upstream Pressure Hi Warn | BP1590_PT01_Hi_A | CAT_P3 | EBBWD-1750B001 | PRIV_ALARMACK | A_P1_SERV | BP1590_PT01_Hi_A | BP1590_PT01_Hi_A | C_LOPRI | BP1590 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.EBBWD.BP1590.PT01
BR4_Tags | BP1590_FT01_Lo_A | Bore | Discharge Flow Low Warn | BP1590_FT01_Lo_A | CAT_P3 | EBBWD-1750B001 | PRIV_ALARMACK | A_P1_SERV | BP1590_FT01_Lo_A | BP1590_FT01_Lo_A | C_LOPRI | BP1590 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.EBBWD.BP1590.FT01
BR4_Tags | BP1590_PT02_Hi_A | Bore | Downstream Pressure Hi Warn | BP1590_PT02_Hi_A | CAT_P3 | EBBWD-1750B001 | PRIV_ALARMACK | A_P1_SERV | BP1590_PT02_Hi_A | BP1590_PT02_Hi_A | C_LOPRI | BP1590 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.EBBWD.BP1590.PT02
BR4_Tags | BP1590_LT02_Lo_A | Bore | Internal Fuel Tank Lo Warn | BP1590_LT02_Lo_A | CAT_P3 | EBBWD-1750B001 | PRIV_ALARMACK | A_P1_SERV | BP1590_LT02_Lo_A | BP1590_LT02_Lo_A | C_LOPRI | BP1590 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.EBBWD.BP1590.LT02
BR4_Tags | BP1590_LT03_Lo_A | Bore | External Fuel Tank Lo Warn | BP1590_LT03_Lo_A | CAT_P3 | EBBWD-1750B001 | PRIV_ALARMACK | A_P1_SERV | BP1590_LT03_Lo_A | BP1590_LT03_Lo_A | C_LOPRI | BP1590 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.EBBWD.BP1590.LT03
BR4_Tags | BP1590_PT03_HI_A | Bore | Boost Pressure Hi Warn | BP1590_PT03_HI_A | CAT_P3 | EBBWD-1750B001 | PRIV_ALARMACK | A_P1_SERV | BP1590_PT03_HI_A | BP1590_PT03_HI_A | C_LOPRI | BP1590 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.EBBWD.BP1590.PT03
BR4_Tags | BP1590_PT04Wrn_A | Bore | Oil Pressure Warn | BP1590_PT04Wrn_A | CAT_P3 | EBBWD-1750B001 | PRIV_ALARMACK | A_P1_SERV | BP1590_PT04Wrn_A | BP1590_PT04Wrn_A | C_LOPRI | BP1590 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.EBBWD.BP1590.PT04
BR4_Tags | BP1590_TT03_HI_A | Bore | Coolant Temp Hi Warning | BP1590_TT03_HI_A | CAT_P3 | EBBWD-1750B001 | PRIV_ALARMACK | A_P1_SERV | BP1590_TT03_HI_A | BP1590_TT03_HI_A | C_LOPRI | BP1590 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.EBBWD.BP1590.TT03
BR4_Tags | BP1590_TT04Wrn_A | Bore | Intake Temp Warn | BP1590_TT04Wrn_A | CAT_P3 | EBBWD-1750B001 | PRIV_ALARMACK | A_P1_SERV | BP1590_TT04Wrn_A | BP1590_TT04Wrn_A | C_LOPRI | BP1590 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.EBBWD.BP1590.TT04
BR4_Tags | BP1590_TT03Wrn_A | Bore | Coolant Temp Warn(ECU) | BP1590_TT03Wrn_A | CAT_P3 | EBBWD-1750B001 | PRIV_ALARMACK | A_P1_SERV | BP1590_TT03Wrn_A | BP1590_TT03Wrn_A | C_LOPRI | BP1590 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.EBBWD.BP1590.TT03
BR4_Tags | BP1591_LOS_A | Bore | Drive LOS Alarm | BP1591_LOS_A | CAT_P1 | EBBWD-1750B001 | PRIV_ALARMACK | A_P1_SERV | BP1591_LOS_A | BP1591_LOS_A | C_LOPRI | BP1591 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.EBBWD.BP1591
BR4_Tags | BP1591_ECR_FLT_A | Bore | ECR Fault | BP1591_ECR_FLT_A | CAT_P3 | EBBWD-1750B001 | PRIV_ALARMACK | A_P1_SERV | BP1591_ECR_FLT_A | BP1591_ECR_FLT_A | C_LOPRI | BP1591 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.EBBWD.BP1591
BR4_Tags | BP1591_ELR_FLT_A | Bore | ELR Fault | BP1591_ELR_FLT_A | CAT_P3 | EBBWD-1750B001 | PRIV_ALARMACK | A_P1_SERV | BP1591_ELR_FLT_A | BP1591_ELR_FLT_A | C_LOPRI | BP1591 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.EBBWD.BP1591
BR4_Tags | BP1591_CB_A | Bore | CB Trip | BP1591_CB_A | CAT_P3 | EBBWD-1750B001 | PRIV_ALARMACK | A_P1_SERV | BP1591_CB_A | BP1591_CB_A | C_LOPRI | BP1591 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.EBBWD.BP1591
BR4_Tags | BP1591_ECUShutDown_A | Bore | ECU Trip | BP1591_ECUShutDown_A | CAT_P3 | EBBWD-1750B001 | PRIV_ALARMACK | A_P1_SERV | BP1591_ECUShutDown_A | BP1591_ECUShutDown_A | C_LOPRI | BP1591 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.EBBWD.BP1591
BR4_Tags | BP1591_PT02_HIHI_A | Bore | Downstream Pressure HiHi | BP1591_PT02_HIHI_A | CAT_P3 | EBBWD-1750B001 | PRIV_ALARMACK | A_P1_SERV | BP1591_PT02_HIHI_A | BP1591_PT02_HIHI_A | C_LOPRI | BP1591 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.EBBWD.BP1591.PT02
BR4_Tags | BP1591_FT01_LOLO_A | Bore | Discharge Flow LoLo | BP1591_FT01_LOLO_A | CAT_P3 | EBBWD-1750B001 | PRIV_ALARMACK | A_P1_SERV | BP1591_FT01_LOLO_A | BP1591_FT01_LOLO_A | C_LOPRI | BP1591 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.EBBWD.BP1591.FT01
BR4_Tags | BP1591_LT03_LOLO_A | Bore | External Fuel Tank LoLo | BP1591_LT03_LOLO_A | CAT_P3 | EBBWD-1750B001 | PRIV_ALARMACK | A_P1_SERV | BP1591_LT03_LOLO_A | BP1591_LT03_LOLO_A | C_LOPRI | BP1591 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.EBBWD.BP1591.LT03
BR4_Tags | BP1591_PT01_HIHI_A | Bore | Upstream Pressure HiHI | BP1591_PT01_HIHI_A | CAT_P3 | EBBWD-1750B001 | PRIV_ALARMACK | A_P1_SERV | BP1591_PT01_HIHI_A | BP1591_PT01_HIHI_A | C_LOPRI | BP1591 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.EBBWD.BP1591.PT01
BR4_Tags | BP1591_LT01_LOLO_A | Bore | Bore Level LoLo | BP1591_LT01_LOLO_A | CAT_P3 | EBBWD-1750B001 | PRIV_ALARMACK | A_P1_SERV | BP1591_LT01_LOLO_A | BP1591_LT01_LOLO_A | C_LOPRI | BP1591 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.EBBWD.BP1591.LT01
BR4_Tags | BP1591_RmtFailWhileRng_A | Bore | Failed While Running | BP1591_RmtFailWhileRng_A | CAT_P3 | EBBWD-1750B001 | PRIV_ALARMACK | A_P1_SERV | BP1591_RmtFailWhileRng_A | BP1591_RmtFailWhileRng_A | C_LOPRI | BP1591 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.EBBWD.BP1591
BR4_Tags | BP1591_StartFail_A | Bore | Failed to Start | BP1591_StartFail_A | CAT_P3 | EBBWD-1750B001 | PRIV_ALARMACK | A_P1_SERV | BP1591_StartFail_A | BP1591_StartFail_A | C_LOPRI | BP1591 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.EBBWD.BP1591
BR4_Tags | BP1591_StopFail_A | Bore | Failed to Stop | BP1591_StopFail_A | CAT_P3 | EBBWD-1750B001 | PRIV_ALARMACK | A_P1_SERV | BP1591_StopFail_A | BP1591_StopFail_A | C_LOPRI | BP1591 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.EBBWD.BP1591
BR4_Tags | BP1591_OverCurr_A | Bore | Overload | BP1591_OverCurr_A | CAT_P3 | EBBWD-1750B001 | PRIV_ALARMACK | A_P1_SERV | BP1591_OverCurr_A | BP1591_OverCurr_A | C_LOPRI | BP1591 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.EBBWD.BP1591
BR4_Tags | BP1591_ShortCurr_A | Bore | Over Current Short | BP1591_ShortCurr_A | CAT_P3 | EBBWD-1750B001 | PRIV_ALARMACK | A_P1_SERV | BP1591_ShortCurr_A | BP1591_ShortCurr_A | C_LOPRI | BP1591 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.EBBWD.BP1591
BR4_Tags | BP1591_CommnSd_A | Bore | Common Shutdown | BP1591_CommnSd_A | CAT_P3 | EBBWD-1750B001 | PRIV_ALARMACK | A_P1_SERV | BP1591_CommnSd_A | BP1591_CommnSd_A | C_LOPRI | BP1591 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.EBBWD.BP1591
BR4_Tags | BP1591_GenVoltLimit_A | Bore | Gen Voltage Limit | BP1591_GenVoltLimit_A | CAT_P3 | EBBWD-1750B001 | PRIV_ALARMACK | A_P1_SERV | BP1591_GenVoltLimit_A | BP1591_GenVoltLimit_A | C_LOPRI | BP1591 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.EBBWD.BP1591
BR4_Tags | BP1591_GenCurrUnbal_A | Bore | Current Unbalance | BP1591_GenCurrUnbal_A | CAT_P3 | EBBWD-1750B001 | PRIV_ALARMACK | A_P1_SERV | BP1591_GenCurrUnbal_A | BP1591_GenCurrUnbal_A | C_LOPRI | BP1591 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.EBBWD.BP1591
BR4_Tags | BP1591_LT02_LOLO_A | Bore | Internal Fuel Tank LoLo | BP1591_LT02_LOLO_A | CAT_P3 | EBBWD-1750B001 | PRIV_ALARMACK | A_P1_SERV | BP1591_LT02_LOLO_A | BP1591_LT02_LOLO_A | C_LOPRI | BP1591 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.EBBWD.BP1591.LT02
BR4_Tags | BP1591_ISOL_DOOR_A | Bore | Isolator Door Open | BP1591_ISOL_DOOR_A | CAT_P3 | EBBWD-1750B001 | PRIV_ALARMACK | A_P1_SERV | BP1591_ISOL_DOOR_A | BP1591_ISOL_DOOR_A | C_LOPRI | BP1591 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.EBBWD.BP1591
BR4_Tags | BP1591_NoFuelTkSel_A | Bore | No Fuel Tank Selected | BP1591_NoFuelTkSel_A | CAT_P3 | EBBWD-1750B001 | PRIV_ALARMACK | A_P1_SERV | BP1591_NoFuelTkSel_A | BP1591_NoFuelTkSel_A | C_LOPRI | BP1591 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.EBBWD.BP1591
BR4_Tags | BP1591_TT04_A | Bore | Intake Temperature Fault | BP1591_TT04_A | CAT_P3 | EBBWD-1750B001 | PRIV_ALARMACK | A_P1_SERV | BP1591_TT04_A | BP1591_TT04_A | C_LOPRI | BP1591 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.EBBWD.BP1591.TT04
BR4_Tags | BP1591_TT03_A | Bore | Coolant Temp Fault(ECU) | BP1591_TT03_A | CAT_P3 | EBBWD-1750B001 | PRIV_ALARMACK | A_P1_SERV | BP1591_TT03_A | BP1591_TT03_A | C_LOPRI | BP1591 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.EBBWD.BP1591.TT03
BR4_Tags | BP1591_PT04_A | Bore | Oil Pressure Fault | BP1591_PT04_A | CAT_P3 | EBBWD-1750B001 | PRIV_ALARMACK | A_P1_SERV | BP1591_PT04_A | BP1591_PT04_A | C_LOPRI | BP1591 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.EBBWD.BP1591.PT04
BR4_Tags | BP1591_TT01_HIHI_A | Bore | Motor Temp HiHi | BP1591_TT01_HIHI_A | CAT_P3 | EBBWD-1750B001 | PRIV_ALARMACK | A_P1_SERV | BP1591_TT01_HIHI_A | BP1591_TT01_HIHI_A | C_LOPRI | BP1591 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.EBBWD.BP1591.TT01
BR4_Tags | BP1591_PT03_HIHI_A | Bore | Boost Pressure HiHi | BP1591_PT03_HIHI_A | CAT_P3 | EBBWD-1750B001 | PRIV_ALARMACK | A_P1_SERV | BP1591_PT03_HIHI_A | BP1591_PT03_HIHI_A | C_LOPRI | BP1591 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.EBBWD.BP1591.PT03
BR4_Tags | BP1591_Stt_A | Bore | Too Many Starts | BP1591_Stt_A | CAT_P3 | EBBWD-1750B001 | PRIV_ALARMACK | A_P1_SERV | BP1591_Stt_A | BP1591_Stt_A | C_LOPRI | BP1591 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.EBBWD.BP1591
BR4_Tags | BP1591_TT03_HIHI_A | Bore | Coolant Temp HiHi | BP1591_TT03_HIHI_A | CAT_P3 | EBBWD-1750B001 | PRIV_ALARMACK | A_P1_SERV | BP1591_TT03_HIHI_A | BP1591_TT03_HIHI_A | C_LOPRI | BP1591 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.EBBWD.BP1591.TT03
BR4_Tags | BP1591_Commn_A | Bore | Common Alarm | BP1591_Commn_A | CAT_P3 | EBBWD-1750B001 | PRIV_ALARMACK | A_P1_SERV | BP1591_Commn_A | BP1591_Commn_A | C_LOPRI | BP1591 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.EBBWD.BP1591
BR4_Tags | BP1591_ECR_Overide_A | Bore | ECR Override is on | BP1591_ECR_Overide_A | CAT_P3 | EBBWD-1750B001 | PRIV_ALARMACK | A_P1_SERV | BP1591_ECR_Overide_A | BP1591_ECR_Overide_A | C_LOPRI | BP1591 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.EBBWD.BP1591
BR4_Tags | BP1591_LT01_Lo_A | Bore | Bore Level Lo Warn | BP1591_LT01_Lo_A | CAT_P3 | EBBWD-1750B001 | PRIV_ALARMACK | A_P1_SERV | BP1591_LT01_Lo_A | BP1591_LT01_Lo_A | C_LOPRI | BP1591 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.EBBWD.BP1591.LT01
BR4_Tags | BP1591_TT01_Hi_A | Bore | Motor Temp Hi Warn | BP1591_TT01_Hi_A | CAT_P3 | EBBWD-1750B001 | PRIV_ALARMACK | A_P1_SERV | BP1591_TT01_Hi_A | BP1591_TT01_Hi_A | C_LOPRI | BP1591 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.EBBWD.BP1591.TT01
BR4_Tags | BP1591_PT01_Hi_A | Bore | Upstream Pressure Hi Warn | BP1591_PT01_Hi_A | CAT_P3 | EBBWD-1750B001 | PRIV_ALARMACK | A_P1_SERV | BP1591_PT01_Hi_A | BP1591_PT01_Hi_A | C_LOPRI | BP1591 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.EBBWD.BP1591.PT01
BR4_Tags | BP1591_FT01_Lo_A | Bore | Discharge Flow Low Warn | BP1591_FT01_Lo_A | CAT_P3 | EBBWD-1750B001 | PRIV_ALARMACK | A_P1_SERV | BP1591_FT01_Lo_A | BP1591_FT01_Lo_A | C_LOPRI | BP1591 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.EBBWD.BP1591.FT01
BR4_Tags | BP1591_PT02_Hi_A | Bore | Downstream Pressure Hi Warn | BP1591_PT02_Hi_A | CAT_P3 | EBBWD-1750B001 | PRIV_ALARMACK | A_P1_SERV | BP1591_PT02_Hi_A | BP1591_PT02_Hi_A | C_LOPRI | BP1591 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.EBBWD.BP1591.PT02
BR4_Tags | BP1591_LT02_Lo_A | Bore | Internal Fuel Tank Lo Warn | BP1591_LT02_Lo_A | CAT_P3 | EBBWD-1750B001 | PRIV_ALARMACK | A_P1_SERV | BP1591_LT02_Lo_A | BP1591_LT02_Lo_A | C_LOPRI | BP1591 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.EBBWD.BP1591.LT02
BR4_Tags | BP1591_LT03_Lo_A | Bore | External Fuel Tank Lo Warn | BP1591_LT03_Lo_A | CAT_P3 | EBBWD-1750B001 | PRIV_ALARMACK | A_P1_SERV | BP1591_LT03_Lo_A | BP1591_LT03_Lo_A | C_LOPRI | BP1591 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.EBBWD.BP1591.LT03
BR4_Tags | BP1591_PT03_HI_A | Bore | Boost Pressure Hi Warn | BP1591_PT03_HI_A | CAT_P3 | EBBWD-1750B001 | PRIV_ALARMACK | A_P1_SERV | BP1591_PT03_HI_A | BP1591_PT03_HI_A | C_LOPRI | BP1591 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.EBBWD.BP1591.PT03
BR4_Tags | BP1591_PT04Wrn_A | Bore | Oil Pressure Warn | BP1591_PT04Wrn_A | CAT_P3 | EBBWD-1750B001 | PRIV_ALARMACK | A_P1_SERV | BP1591_PT04Wrn_A | BP1591_PT04Wrn_A | C_LOPRI | BP1591 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.EBBWD.BP1591.PT04
BR4_Tags | BP1591_TT03_HI_A | Bore | Coolant Temp Hi Warning | BP1591_TT03_HI_A | CAT_P3 | EBBWD-1750B001 | PRIV_ALARMACK | A_P1_SERV | BP1591_TT03_HI_A | BP1591_TT03_HI_A | C_LOPRI | BP1591 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.EBBWD.BP1591.TT03
BR4_Tags | BP1591_TT04Wrn_A | Bore | Intake Temp Warn | BP1591_TT04Wrn_A | CAT_P3 | EBBWD-1750B001 | PRIV_ALARMACK | A_P1_SERV | BP1591_TT04Wrn_A | BP1591_TT04Wrn_A | C_LOPRI | BP1591 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.EBBWD.BP1591.TT04
BR4_Tags | BP1591_TT03Wrn_A | Bore | Coolant Temp Warn(ECU) | BP1591_TT03Wrn_A | CAT_P3 | EBBWD-1750B001 | PRIV_ALARMACK | A_P1_SERV | BP1591_TT03Wrn_A | BP1591_TT03Wrn_A | C_LOPRI | BP1591 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.EBBWD.BP1591.TT03
BR4_Tags | BP1592_LOS_A | Bore | Drive LOS Alarm | BP1592_LOS_A | CAT_P1 | EBBWD-1750B001 | PRIV_ALARMACK | A_P1_SERV | BP1592_LOS_A | BP1592_LOS_A | C_LOPRI | BP1592 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.BP1592
BR4_Tags | BP1592_ECR_FLT_A | Bore | ECR Fault | BP1592_ECR_FLT_A | CAT_P3 | EBBWD-1750B001 | PRIV_ALARMACK | A_P1_SERV | BP1592_ECR_FLT_A | BP1592_ECR_FLT_A | C_LOPRI | BP1592 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.BP1592
BR4_Tags | BP1592_ELR_FLT_A | Bore | ELR Fault | BP1592_ELR_FLT_A | CAT_P3 | EBBWD-1750B001 | PRIV_ALARMACK | A_P1_SERV | BP1592_ELR_FLT_A | BP1592_ELR_FLT_A | C_LOPRI | BP1592 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.BP1592
BR4_Tags | BP1592_CB_A | Bore | CB Trip | BP1592_CB_A | CAT_P3 | EBBWD-1750B001 | PRIV_ALARMACK | A_P1_SERV | BP1592_CB_A | BP1592_CB_A | C_LOPRI | BP1592 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.BP1592
BR4_Tags | BP1592_ECUShutDown_A | Bore | ECU Trip | BP1592_ECUShutDown_A | CAT_P3 | EBBWD-1750B001 | PRIV_ALARMACK | A_P1_SERV | BP1592_ECUShutDown_A | BP1592_ECUShutDown_A | C_LOPRI | BP1592 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.BP1592
BR4_Tags | BP1592_PT02_HIHI_A | Bore | Downstream Pressure HiHi | BP1592_PT02_HIHI_A | CAT_P3 | EBBWD-1750B001 | PRIV_ALARMACK | A_P1_SERV | BP1592_PT02_HIHI_A | BP1592_PT02_HIHI_A | C_LOPRI | BP1592 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.BP1592.PT02
BR4_Tags | BP1592_FT01_LOLO_A | Bore | Discharge Flow LoLo | BP1592_FT01_LOLO_A | CAT_P3 | EBBWD-1750B001 | PRIV_ALARMACK | A_P1_SERV | BP1592_FT01_LOLO_A | BP1592_FT01_LOLO_A | C_LOPRI | BP1592 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.BP1592.FT01
BR4_Tags | BP1592_LT03_LOLO_A | Bore | External Fuel Tank LoLo | BP1592_LT03_LOLO_A | CAT_P3 | EBBWD-1750B001 | PRIV_ALARMACK | A_P1_SERV | BP1592_LT03_LOLO_A | BP1592_LT03_LOLO_A | C_LOPRI | BP1592 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.BP1592.LT03
BR4_Tags | BP1592_PT01_HIHI_A | Bore | Upstream Pressure HiHI | BP1592_PT01_HIHI_A | CAT_P3 | EBBWD-1750B001 | PRIV_ALARMACK | A_P1_SERV | BP1592_PT01_HIHI_A | BP1592_PT01_HIHI_A | C_LOPRI | BP1592 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.BP1592.PT01
BR4_Tags | BP1592_LT01_LOLO_A | Bore | Bore Level LoLo | BP1592_LT01_LOLO_A | CAT_P3 | EBBWD-1750B001 | PRIV_ALARMACK | A_P1_SERV | BP1592_LT01_LOLO_A | BP1592_LT01_LOLO_A | C_LOPRI | BP1592 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.BP1592.LT01
BR4_Tags | BP1592_RmtFailWhileRng_A | Bore | Failed While Running | BP1592_RmtFailWhileRng_A | CAT_P3 | EBBWD-1750B001 | PRIV_ALARMACK | A_P1_SERV | BP1592_RmtFailWhileRng_A | BP1592_RmtFailWhileRng_A | C_LOPRI | BP1592 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.BP1592
BR4_Tags | BP1592_StartFail_A | Bore | Failed to Start | BP1592_StartFail_A | CAT_P3 | EBBWD-1750B001 | PRIV_ALARMACK | A_P1_SERV | BP1592_StartFail_A | BP1592_StartFail_A | C_LOPRI | BP1592 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.BP1592
BR4_Tags | BP1592_StopFail_A | Bore | Failed to Stop | BP1592_StopFail_A | CAT_P3 | EBBWD-1750B001 | PRIV_ALARMACK | A_P1_SERV | BP1592_StopFail_A | BP1592_StopFail_A | C_LOPRI | BP1592 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.BP1592
BR4_Tags | BP1592_OverCurr_A | Bore | Overload | BP1592_OverCurr_A | CAT_P3 | EBBWD-1750B001 | PRIV_ALARMACK | A_P1_SERV | BP1592_OverCurr_A | BP1592_OverCurr_A | C_LOPRI | BP1592 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.BP1592
BR4_Tags | BP1592_ShortCurr_A | Bore | Over Current Short | BP1592_ShortCurr_A | CAT_P3 | EBBWD-1750B001 | PRIV_ALARMACK | A_P1_SERV | BP1592_ShortCurr_A | BP1592_ShortCurr_A | C_LOPRI | BP1592 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.BP1592
BR4_Tags | BP1592_CommnSd_A | Bore | Common Shutdown | BP1592_CommnSd_A | CAT_P3 | EBBWD-1750B001 | PRIV_ALARMACK | A_P1_SERV | BP1592_CommnSd_A | BP1592_CommnSd_A | C_LOPRI | BP1592 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.BP1592
BR4_Tags | BP1592_GenVoltLimit_A | Bore | Gen Voltage Limit | BP1592_GenVoltLimit_A | CAT_P3 | EBBWD-1750B001 | PRIV_ALARMACK | A_P1_SERV | BP1592_GenVoltLimit_A | BP1592_GenVoltLimit_A | C_LOPRI | BP1592 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.BP1592
BR4_Tags | BP1592_GenCurrUnbal_A | Bore | Current Unbalance | BP1592_GenCurrUnbal_A | CAT_P3 | EBBWD-1750B001 | PRIV_ALARMACK | A_P1_SERV | BP1592_GenCurrUnbal_A | BP1592_GenCurrUnbal_A | C_LOPRI | BP1592 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.BP1592
BR4_Tags | BP1592_LT02_LOLO_A | Bore | Internal Fuel Tank LoLo | BP1592_LT02_LOLO_A | CAT_P3 | EBBWD-1750B001 | PRIV_ALARMACK | A_P1_SERV | BP1592_LT02_LOLO_A | BP1592_LT02_LOLO_A | C_LOPRI | BP1592 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.BP1592.LT02
BR4_Tags | BP1592_ISOL_DOOR_A | Bore | Isolator Door Open | BP1592_ISOL_DOOR_A | CAT_P3 | EBBWD-1750B001 | PRIV_ALARMACK | A_P1_SERV | BP1592_ISOL_DOOR_A | BP1592_ISOL_DOOR_A | C_LOPRI | BP1592 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.BP1592
BR4_Tags | BP1592_NoFuelTkSel_A | Bore | No Fuel Tank Selected | BP1592_NoFuelTkSel_A | CAT_P3 | EBBWD-1750B001 | PRIV_ALARMACK | A_P1_SERV | BP1592_NoFuelTkSel_A | BP1592_NoFuelTkSel_A | C_LOPRI | BP1592 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.BP1592
BR4_Tags | BP1592_TT04_A | Bore | Intake Temperature Fault | BP1592_TT04_A | CAT_P3 | EBBWD-1750B001 | PRIV_ALARMACK | A_P1_SERV | BP1592_TT04_A | BP1592_TT04_A | C_LOPRI | BP1592 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.BP1592.TT04
BR4_Tags | BP1592_TT03_A | Bore | Coolant Temp Fault(ECU) | BP1592_TT03_A | CAT_P3 | EBBWD-1750B001 | PRIV_ALARMACK | A_P1_SERV | BP1592_TT03_A | BP1592_TT03_A | C_LOPRI | BP1592 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.BP1592.TT03
BR4_Tags | BP1592_PT04_A | Bore | Oil Pressure Fault | BP1592_PT04_A | CAT_P3 | EBBWD-1750B001 | PRIV_ALARMACK | A_P1_SERV | BP1592_PT04_A | BP1592_PT04_A | C_LOPRI | BP1592 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.BP1592.PT04
BR4_Tags | BP1592_TT01_HIHI_A | Bore | Motor Temp HiHi | BP1592_TT01_HIHI_A | CAT_P3 | EBBWD-1750B001 | PRIV_ALARMACK | A_P1_SERV | BP1592_TT01_HIHI_A | BP1592_TT01_HIHI_A | C_LOPRI | BP1592 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.BP1592.TT01
BR4_Tags | BP1592_PT03_HIHI_A | Bore | Boost Pressure HiHi | BP1592_PT03_HIHI_A | CAT_P3 | EBBWD-1750B001 | PRIV_ALARMACK | A_P1_SERV | BP1592_PT03_HIHI_A | BP1592_PT03_HIHI_A | C_LOPRI | BP1592 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.BP1592.PT03
BR4_Tags | BP1592_Stt_A | Bore | Too Many Starts | BP1592_Stt_A | CAT_P3 | EBBWD-1750B001 | PRIV_ALARMACK | A_P1_SERV | BP1592_Stt_A | BP1592_Stt_A | C_LOPRI | BP1592 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.BP1592
BR4_Tags | BP1592_TT03_HIHI_A | Bore | Coolant Temp HiHi | BP1592_TT03_HIHI_A | CAT_P3 | EBBWD-1750B001 | PRIV_ALARMACK | A_P1_SERV | BP1592_TT03_HIHI_A | BP1592_TT03_HIHI_A | C_LOPRI | BP1592 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.BP1592.TT03
BR4_Tags | BP1592_Commn_A | Bore | Common Alarm | BP1592_Commn_A | CAT_P3 | EBBWD-1750B001 | PRIV_ALARMACK | A_P1_SERV | BP1592_Commn_A | BP1592_Commn_A | C_LOPRI | BP1592 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.BP1592
BR4_Tags | BP1592_ECR_Overide_A | Bore | ECR Override is on | BP1592_ECR_Overide_A | CAT_P3 | EBBWD-1750B001 | PRIV_ALARMACK | A_P1_SERV | BP1592_ECR_Overide_A | BP1592_ECR_Overide_A | C_LOPRI | BP1592 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.BP1592
BR4_Tags | BP1592_LT01_Lo_A | Bore | Bore Level Lo Warn | BP1592_LT01_Lo_A | CAT_P3 | EBBWD-1750B001 | PRIV_ALARMACK | A_P1_SERV | BP1592_LT01_Lo_A | BP1592_LT01_Lo_A | C_LOPRI | BP1592 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.BP1592.LT01
BR4_Tags | BP1592_TT01_Hi_A | Bore | Motor Temp Hi Warn | BP1592_TT01_Hi_A | CAT_P3 | EBBWD-1750B001 | PRIV_ALARMACK | A_P1_SERV | BP1592_TT01_Hi_A | BP1592_TT01_Hi_A | C_LOPRI | BP1592 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.BP1592.TT01
BR4_Tags | BP1592_PT01_Hi_A | Bore | Upstream Pressure Hi Warn | BP1592_PT01_Hi_A | CAT_P3 | EBBWD-1750B001 | PRIV_ALARMACK | A_P1_SERV | BP1592_PT01_Hi_A | BP1592_PT01_Hi_A | C_LOPRI | BP1592 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.BP1592.PT01
BR4_Tags | BP1592_FT01_Lo_A | Bore | Discharge Flow Low Warn | BP1592_FT01_Lo_A | CAT_P3 | EBBWD-1750B001 | PRIV_ALARMACK | A_P1_SERV | BP1592_FT01_Lo_A | BP1592_FT01_Lo_A | C_LOPRI | BP1592 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.BP1592.FT01
BR4_Tags | BP1592_PT02_Hi_A | Bore | Downstream Pressure Hi Warn | BP1592_PT02_Hi_A | CAT_P3 | EBBWD-1750B001 | PRIV_ALARMACK | A_P1_SERV | BP1592_PT02_Hi_A | BP1592_PT02_Hi_A | C_LOPRI | BP1592 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.BP1592.PT02
BR4_Tags | BP1592_LT02_Lo_A | Bore | Internal Fuel Tank Lo Warn | BP1592_LT02_Lo_A | CAT_P3 | EBBWD-1750B001 | PRIV_ALARMACK | A_P1_SERV | BP1592_LT02_Lo_A | BP1592_LT02_Lo_A | C_LOPRI | BP1592 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.BP1592.LT02
BR4_Tags | BP1592_LT03_Lo_A | Bore | External Fuel Tank Lo Warn | BP1592_LT03_Lo_A | CAT_P3 | EBBWD-1750B001 | PRIV_ALARMACK | A_P1_SERV | BP1592_LT03_Lo_A | BP1592_LT03_Lo_A | C_LOPRI | BP1592 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.BP1592.LT03
BR4_Tags | BP1592_PT03_HI_A | Bore | Boost Pressure Hi Warn | BP1592_PT03_HI_A | CAT_P3 | EBBWD-1750B001 | PRIV_ALARMACK | A_P1_SERV | BP1592_PT03_HI_A | BP1592_PT03_HI_A | C_LOPRI | BP1592 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.BP1592.PT03
BR4_Tags | BP1592_PT04Wrn_A | Bore | Oil Pressure Warn | BP1592_PT04Wrn_A | CAT_P3 | EBBWD-1750B001 | PRIV_ALARMACK | A_P1_SERV | BP1592_PT04Wrn_A | BP1592_PT04Wrn_A | C_LOPRI | BP1592 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.BP1592.PT04
BR4_Tags | BP1592_TT03_HI_A | Bore | Coolant Temp Hi Warning | BP1592_TT03_HI_A | CAT_P3 | EBBWD-1750B001 | PRIV_ALARMACK | A_P1_SERV | BP1592_TT03_HI_A | BP1592_TT03_HI_A | C_LOPRI | BP1592 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.BP1592.TT03
BR4_Tags | BP1592_TT04Wrn_A | Bore | Intake Temp Warn | BP1592_TT04Wrn_A | CAT_P3 | EBBWD-1750B001 | PRIV_ALARMACK | A_P1_SERV | BP1592_TT04Wrn_A | BP1592_TT04Wrn_A | C_LOPRI | BP1592 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.BP1592.TT04
BR4_Tags | BP1592_TT03Wrn_A | Bore | Coolant Temp Warn(ECU) | BP1592_TT03Wrn_A | CAT_P3 | EBBWD-1750B001 | PRIV_ALARMACK | A_P1_SERV | BP1592_TT03Wrn_A | BP1592_TT03Wrn_A | C_LOPRI | BP1592 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.BP1592.TT03
BR4_Tags | BP1593_LOS_A | Bore | Drive LOS Alarm | BP1593_LOS_A | CAT_P1 | EBBWD-1750B001 | PRIV_ALARMACK | A_P1_SERV | BP1593_LOS_A | BP1593_LOS_A | C_LOPRI | BP1593 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.EBBWD.BP1593
BR4_Tags | BP1593_ECR_FLT_A | Bore | ECR Fault | BP1593_ECR_FLT_A | CAT_P3 | EBBWD-1750B001 | PRIV_ALARMACK | A_P1_SERV | BP1593_ECR_FLT_A | BP1593_ECR_FLT_A | C_LOPRI | BP1593 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.EBBWD.BP1593
BR4_Tags | BP1593_ELR_FLT_A | Bore | ELR Fault | BP1593_ELR_FLT_A | CAT_P3 | EBBWD-1750B001 | PRIV_ALARMACK | A_P1_SERV | BP1593_ELR_FLT_A | BP1593_ELR_FLT_A | C_LOPRI | BP1593 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.EBBWD.BP1593
BR4_Tags | BP1593_CB_A | Bore | CB Trip | BP1593_CB_A | CAT_P3 | EBBWD-1750B001 | PRIV_ALARMACK | A_P1_SERV | BP1593_CB_A | BP1593_CB_A | C_LOPRI | BP1593 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.EBBWD.BP1593
BR4_Tags | BP1593_ECUShutDown_A | Bore | ECU Trip | BP1593_ECUShutDown_A | CAT_P3 | EBBWD-1750B001 | PRIV_ALARMACK | A_P1_SERV | BP1593_ECUShutDown_A | BP1593_ECUShutDown_A | C_LOPRI | BP1593 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.EBBWD.BP1593
BR4_Tags | BP1593_PT02_HIHI_A | Bore | Downstream Pressure HiHi | BP1593_PT02_HIHI_A | CAT_P3 | EBBWD-1750B001 | PRIV_ALARMACK | A_P1_SERV | BP1593_PT02_HIHI_A | BP1593_PT02_HIHI_A | C_LOPRI | BP1593 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.EBBWD.BP1593.PT02
BR4_Tags | BP1593_FT01_LOLO_A | Bore | Discharge Flow LoLo | BP1593_FT01_LOLO_A | CAT_P3 | EBBWD-1750B001 | PRIV_ALARMACK | A_P1_SERV | BP1593_FT01_LOLO_A | BP1593_FT01_LOLO_A | C_LOPRI | BP1593 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.EBBWD.BP1593.FT01
BR4_Tags | BP1593_LT03_LOLO_A | Bore | External Fuel Tank LoLo | BP1593_LT03_LOLO_A | CAT_P3 | EBBWD-1750B001 | PRIV_ALARMACK | A_P1_SERV | BP1593_LT03_LOLO_A | BP1593_LT03_LOLO_A | C_LOPRI | BP1593 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.EBBWD.BP1593.LT03
BR4_Tags | BP1593_PT01_HIHI_A | Bore | Upstream Pressure HiHI | BP1593_PT01_HIHI_A | CAT_P3 | EBBWD-1750B001 | PRIV_ALARMACK | A_P1_SERV | BP1593_PT01_HIHI_A | BP1593_PT01_HIHI_A | C_LOPRI | BP1593 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.EBBWD.BP1593.PT01
BR4_Tags | BP1593_LT01_LOLO_A | Bore | Bore Level LoLo | BP1593_LT01_LOLO_A | CAT_P3 | EBBWD-1750B001 | PRIV_ALARMACK | A_P1_SERV | BP1593_LT01_LOLO_A | BP1593_LT01_LOLO_A | C_LOPRI | BP1593 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.EBBWD.BP1593.LT01
BR4_Tags | BP1593_RmtFailWhileRng_A | Bore | Failed While Running | BP1593_RmtFailWhileRng_A | CAT_P3 | EBBWD-1750B001 | PRIV_ALARMACK | A_P1_SERV | BP1593_RmtFailWhileRng_A | BP1593_RmtFailWhileRng_A | C_LOPRI | BP1593 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.EBBWD.BP1593
BR4_Tags | BP1593_StartFail_A | Bore | Failed to Start | BP1593_StartFail_A | CAT_P3 | EBBWD-1750B001 | PRIV_ALARMACK | A_P1_SERV | BP1593_StartFail_A | BP1593_StartFail_A | C_LOPRI | BP1593 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.EBBWD.BP1593
BR4_Tags | BP1593_StopFail_A | Bore | Failed to Stop | BP1593_StopFail_A | CAT_P3 | EBBWD-1750B001 | PRIV_ALARMACK | A_P1_SERV | BP1593_StopFail_A | BP1593_StopFail_A | C_LOPRI | BP1593 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.EBBWD.BP1593
BR4_Tags | BP1593_OverCurr_A | Bore | Overload | BP1593_OverCurr_A | CAT_P3 | EBBWD-1750B001 | PRIV_ALARMACK | A_P1_SERV | BP1593_OverCurr_A | BP1593_OverCurr_A | C_LOPRI | BP1593 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.EBBWD.BP1593
BR4_Tags | BP1593_ShortCurr_A | Bore | Over Current Short | BP1593_ShortCurr_A | CAT_P3 | EBBWD-1750B001 | PRIV_ALARMACK | A_P1_SERV | BP1593_ShortCurr_A | BP1593_ShortCurr_A | C_LOPRI | BP1593 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.EBBWD.BP1593
BR4_Tags | BP1593_CommnSd_A | Bore | Common Shutdown | BP1593_CommnSd_A | CAT_P3 | EBBWD-1750B001 | PRIV_ALARMACK | A_P1_SERV | BP1593_CommnSd_A | BP1593_CommnSd_A | C_LOPRI | BP1593 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.EBBWD.BP1593
BR4_Tags | BP1593_GenVoltLimit_A | Bore | Gen Voltage Limit | BP1593_GenVoltLimit_A | CAT_P3 | EBBWD-1750B001 | PRIV_ALARMACK | A_P1_SERV | BP1593_GenVoltLimit_A | BP1593_GenVoltLimit_A | C_LOPRI | BP1593 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.EBBWD.BP1593
BR4_Tags | BP1593_GenCurrUnbal_A | Bore | Current Unbalance | BP1593_GenCurrUnbal_A | CAT_P3 | EBBWD-1750B001 | PRIV_ALARMACK | A_P1_SERV | BP1593_GenCurrUnbal_A | BP1593_GenCurrUnbal_A | C_LOPRI | BP1593 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.EBBWD.BP1593
BR4_Tags | BP1593_LT02_LOLO_A | Bore | Internal Fuel Tank LoLo | BP1593_LT02_LOLO_A | CAT_P3 | EBBWD-1750B001 | PRIV_ALARMACK | A_P1_SERV | BP1593_LT02_LOLO_A | BP1593_LT02_LOLO_A | C_LOPRI | BP1593 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.EBBWD.BP1593.LT02
BR4_Tags | BP1593_ISOL_DOOR_A | Bore | Isolator Door Open | BP1593_ISOL_DOOR_A | CAT_P3 | EBBWD-1750B001 | PRIV_ALARMACK | A_P1_SERV | BP1593_ISOL_DOOR_A | BP1593_ISOL_DOOR_A | C_LOPRI | BP1593 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.EBBWD.BP1593
BR4_Tags | BP1593_NoFuelTkSel_A | Bore | No Fuel Tank Selected | BP1593_NoFuelTkSel_A | CAT_P3 | EBBWD-1750B001 | PRIV_ALARMACK | A_P1_SERV | BP1593_NoFuelTkSel_A | BP1593_NoFuelTkSel_A | C_LOPRI | BP1593 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.EBBWD.BP1593
BR4_Tags | BP1593_TT04_A | Bore | Intake Temperature Fault | BP1593_TT04_A | CAT_P3 | EBBWD-1750B001 | PRIV_ALARMACK | A_P1_SERV | BP1593_TT04_A | BP1593_TT04_A | C_LOPRI | BP1593 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.EBBWD.BP1593.TT04
BR4_Tags | BP1593_TT03_A | Bore | Coolant Temp Fault(ECU) | BP1593_TT03_A | CAT_P3 | EBBWD-1750B001 | PRIV_ALARMACK | A_P1_SERV | BP1593_TT03_A | BP1593_TT03_A | C_LOPRI | BP1593 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.EBBWD.BP1593.TT03
BR4_Tags | BP1593_PT04_A | Bore | Oil Pressure Fault | BP1593_PT04_A | CAT_P3 | EBBWD-1750B001 | PRIV_ALARMACK | A_P1_SERV | BP1593_PT04_A | BP1593_PT04_A | C_LOPRI | BP1593 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.EBBWD.BP1593.PT04
BR4_Tags | BP1593_TT01_HIHI_A | Bore | Motor Temp HiHi | BP1593_TT01_HIHI_A | CAT_P3 | EBBWD-1750B001 | PRIV_ALARMACK | A_P1_SERV | BP1593_TT01_HIHI_A | BP1593_TT01_HIHI_A | C_LOPRI | BP1593 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.EBBWD.BP1593.TT01
BR4_Tags | BP1593_PT03_HIHI_A | Bore | Boost Pressure HiHi | BP1593_PT03_HIHI_A | CAT_P3 | EBBWD-1750B001 | PRIV_ALARMACK | A_P1_SERV | BP1593_PT03_HIHI_A | BP1593_PT03_HIHI_A | C_LOPRI | BP1593 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.EBBWD.BP1593.PT03
BR4_Tags | BP1593_Stt_A | Bore | Too Many Starts | BP1593_Stt_A | CAT_P3 | EBBWD-1750B001 | PRIV_ALARMACK | A_P1_SERV | BP1593_Stt_A | BP1593_Stt_A | C_LOPRI | BP1593 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.EBBWD.BP1593
BR4_Tags | BP1593_TT03_HIHI_A | Bore | Coolant Temp HiHi | BP1593_TT03_HIHI_A | CAT_P3 | EBBWD-1750B001 | PRIV_ALARMACK | A_P1_SERV | BP1593_TT03_HIHI_A | BP1593_TT03_HIHI_A | C_LOPRI | BP1593 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.EBBWD.BP1593.TT03
BR4_Tags | BP1593_Commn_A | Bore | Common Alarm | BP1593_Commn_A | CAT_P3 | EBBWD-1750B001 | PRIV_ALARMACK | A_P1_SERV | BP1593_Commn_A | BP1593_Commn_A | C_LOPRI | BP1593 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.EBBWD.BP1593
BR4_Tags | BP1593_ECR_Overide_A | Bore | ECR Override is on | BP1593_ECR_Overide_A | CAT_P3 | EBBWD-1750B001 | PRIV_ALARMACK | A_P1_SERV | BP1593_ECR_Overide_A | BP1593_ECR_Overide_A | C_LOPRI | BP1593 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.EBBWD.BP1593
BR4_Tags | BP1593_LT01_Lo_A | Bore | Bore Level Lo Warn | BP1593_LT01_Lo_A | CAT_P3 | EBBWD-1750B001 | PRIV_ALARMACK | A_P1_SERV | BP1593_LT01_Lo_A | BP1593_LT01_Lo_A | C_LOPRI | BP1593 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.EBBWD.BP1593.LT01
BR4_Tags | BP1593_TT01_Hi_A | Bore | Motor Temp Hi Warn | BP1593_TT01_Hi_A | CAT_P3 | EBBWD-1750B001 | PRIV_ALARMACK | A_P1_SERV | BP1593_TT01_Hi_A | BP1593_TT01_Hi_A | C_LOPRI | BP1593 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.EBBWD.BP1593.TT01
BR4_Tags | BP1593_PT01_Hi_A | Bore | Upstream Pressure Hi Warn | BP1593_PT01_Hi_A | CAT_P3 | EBBWD-1750B001 | PRIV_ALARMACK | A_P1_SERV | BP1593_PT01_Hi_A | BP1593_PT01_Hi_A | C_LOPRI | BP1593 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.EBBWD.BP1593.PT01
BR4_Tags | BP1593_FT01_Lo_A | Bore | Discharge Flow Low Warn | BP1593_FT01_Lo_A | CAT_P3 | EBBWD-1750B001 | PRIV_ALARMACK | A_P1_SERV | BP1593_FT01_Lo_A | BP1593_FT01_Lo_A | C_LOPRI | BP1593 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.EBBWD.BP1593.FT01
BR4_Tags | BP1593_PT02_Hi_A | Bore | Downstream Pressure Hi Warn | BP1593_PT02_Hi_A | CAT_P3 | EBBWD-1750B001 | PRIV_ALARMACK | A_P1_SERV | BP1593_PT02_Hi_A | BP1593_PT02_Hi_A | C_LOPRI | BP1593 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.EBBWD.BP1593.PT02
BR4_Tags | BP1593_LT02_Lo_A | Bore | Internal Fuel Tank Lo Warn | BP1593_LT02_Lo_A | CAT_P3 | EBBWD-1750B001 | PRIV_ALARMACK | A_P1_SERV | BP1593_LT02_Lo_A | BP1593_LT02_Lo_A | C_LOPRI | BP1593 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.EBBWD.BP1593.LT02
BR4_Tags | BP1593_LT03_Lo_A | Bore | External Fuel Tank Lo Warn | BP1593_LT03_Lo_A | CAT_P3 | EBBWD-1750B001 | PRIV_ALARMACK | A_P1_SERV | BP1593_LT03_Lo_A | BP1593_LT03_Lo_A | C_LOPRI | BP1593 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.EBBWD.BP1593.LT03
BR4_Tags | BP1593_PT03_HI_A | Bore | Boost Pressure Hi Warn | BP1593_PT03_HI_A | CAT_P3 | EBBWD-1750B001 | PRIV_ALARMACK | A_P1_SERV | BP1593_PT03_HI_A | BP1593_PT03_HI_A | C_LOPRI | BP1593 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.EBBWD.BP1593.PT03
BR4_Tags | BP1593_PT04Wrn_A | Bore | Oil Pressure Warn | BP1593_PT04Wrn_A | CAT_P3 | EBBWD-1750B001 | PRIV_ALARMACK | A_P1_SERV | BP1593_PT04Wrn_A | BP1593_PT04Wrn_A | C_LOPRI | BP1593 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.EBBWD.BP1593.PT04
BR4_Tags | BP1593_TT03_HI_A | Bore | Coolant Temp Hi Warning | BP1593_TT03_HI_A | CAT_P3 | EBBWD-1750B001 | PRIV_ALARMACK | A_P1_SERV | BP1593_TT03_HI_A | BP1593_TT03_HI_A | C_LOPRI | BP1593 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.EBBWD.BP1593.TT03
BR4_Tags | BP1593_TT04Wrn_A | Bore | Intake Temp Warn | BP1593_TT04Wrn_A | CAT_P3 | EBBWD-1750B001 | PRIV_ALARMACK | A_P1_SERV | BP1593_TT04Wrn_A | BP1593_TT04Wrn_A | C_LOPRI | BP1593 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.EBBWD.BP1593.TT04
BR4_Tags | BP1593_TT03Wrn_A | Bore | Coolant Temp Warn(ECU) | BP1593_TT03Wrn_A | CAT_P3 | EBBWD-1750B001 | PRIV_ALARMACK | A_P1_SERV | BP1593_TT03Wrn_A | BP1593_TT03Wrn_A | C_LOPRI | BP1593 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.EBBWD.BP1593.TT03
BR4_Tags | BP1594_LOS_A | Bore | Drive LOS Alarm | BP1594_LOS_A | CAT_P1 | EBBWD-1750B001 | PRIV_ALARMACK | A_P1_SERV | BP1594_LOS_A | BP1594_LOS_A | C_LOPRI | BP1594 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.EBBWD.BP1594
BR4_Tags | BP1594_ECR_FLT_A | Bore | ECR Fault | BP1594_ECR_FLT_A | CAT_P3 | EBBWD-1750B001 | PRIV_ALARMACK | A_P1_SERV | BP1594_ECR_FLT_A | BP1594_ECR_FLT_A | C_LOPRI | BP1594 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.EBBWD.BP1594
BR4_Tags | BP1594_ELR_FLT_A | Bore | ELR Fault | BP1594_ELR_FLT_A | CAT_P3 | EBBWD-1750B001 | PRIV_ALARMACK | A_P1_SERV | BP1594_ELR_FLT_A | BP1594_ELR_FLT_A | C_LOPRI | BP1594 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.EBBWD.BP1594
BR4_Tags | BP1594_CB_A | Bore | CB Trip | BP1594_CB_A | CAT_P3 | EBBWD-1750B001 | PRIV_ALARMACK | A_P1_SERV | BP1594_CB_A | BP1594_CB_A | C_LOPRI | BP1594 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.EBBWD.BP1594
BR4_Tags | BP1594_ECUShutDown_A | Bore | ECU Trip | BP1594_ECUShutDown_A | CAT_P3 | EBBWD-1750B001 | PRIV_ALARMACK | A_P1_SERV | BP1594_ECUShutDown_A | BP1594_ECUShutDown_A | C_LOPRI | BP1594 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.EBBWD.BP1594
BR4_Tags | BP1594_PT02_HIHI_A | Bore | Downstream Pressure HiHi | BP1594_PT02_HIHI_A | CAT_P3 | EBBWD-1750B001 | PRIV_ALARMACK | A_P1_SERV | BP1594_PT02_HIHI_A | BP1594_PT02_HIHI_A | C_LOPRI | BP1594 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.EBBWD.BP1594.PT02
BR4_Tags | BP1594_FT01_LOLO_A | Bore | Discharge Flow LoLo | BP1594_FT01_LOLO_A | CAT_P3 | EBBWD-1750B001 | PRIV_ALARMACK | A_P1_SERV | BP1594_FT01_LOLO_A | BP1594_FT01_LOLO_A | C_LOPRI | BP1594 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.EBBWD.BP1594.FT01
BR4_Tags | BP1594_LT03_LOLO_A | Bore | External Fuel Tank LoLo | BP1594_LT03_LOLO_A | CAT_P3 | EBBWD-1750B001 | PRIV_ALARMACK | A_P1_SERV | BP1594_LT03_LOLO_A | BP1594_LT03_LOLO_A | C_LOPRI | BP1594 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.EBBWD.BP1594.LT03
BR4_Tags | BP1594_PT01_HIHI_A | Bore | Upstream Pressure HiHI | BP1594_PT01_HIHI_A | CAT_P3 | EBBWD-1750B001 | PRIV_ALARMACK | A_P1_SERV | BP1594_PT01_HIHI_A | BP1594_PT01_HIHI_A | C_LOPRI | BP1594 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.EBBWD.BP1594.PT01
BR4_Tags | BP1594_LT01_LOLO_A | Bore | Bore Level LoLo | BP1594_LT01_LOLO_A | CAT_P3 | EBBWD-1750B001 | PRIV_ALARMACK | A_P1_SERV | BP1594_LT01_LOLO_A | BP1594_LT01_LOLO_A | C_LOPRI | BP1594 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.EBBWD.BP1594.LT01
BR4_Tags | BP1594_RmtFailWhileRng_A | Bore | Failed While Running | BP1594_RmtFailWhileRng_A | CAT_P3 | EBBWD-1750B001 | PRIV_ALARMACK | A_P1_SERV | BP1594_RmtFailWhileRng_A | BP1594_RmtFailWhileRng_A | C_LOPRI | BP1594 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.EBBWD.BP1594
BR4_Tags | BP1594_StartFail_A | Bore | Failed to Start | BP1594_StartFail_A | CAT_P3 | EBBWD-1750B001 | PRIV_ALARMACK | A_P1_SERV | BP1594_StartFail_A | BP1594_StartFail_A | C_LOPRI | BP1594 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.EBBWD.BP1594
BR4_Tags | BP1594_StopFail_A | Bore | Failed to Stop | BP1594_StopFail_A | CAT_P3 | EBBWD-1750B001 | PRIV_ALARMACK | A_P1_SERV | BP1594_StopFail_A | BP1594_StopFail_A | C_LOPRI | BP1594 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.EBBWD.BP1594
BR4_Tags | BP1594_OverCurr_A | Bore | Overload | BP1594_OverCurr_A | CAT_P3 | EBBWD-1750B001 | PRIV_ALARMACK | A_P1_SERV | BP1594_OverCurr_A | BP1594_OverCurr_A | C_LOPRI | BP1594 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.EBBWD.BP1594
BR4_Tags | BP1594_ShortCurr_A | Bore | Over Current Short | BP1594_ShortCurr_A | CAT_P3 | EBBWD-1750B001 | PRIV_ALARMACK | A_P1_SERV | BP1594_ShortCurr_A | BP1594_ShortCurr_A | C_LOPRI | BP1594 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.EBBWD.BP1594
BR4_Tags | BP1594_CommnSd_A | Bore | Common Shutdown | BP1594_CommnSd_A | CAT_P3 | EBBWD-1750B001 | PRIV_ALARMACK | A_P1_SERV | BP1594_CommnSd_A | BP1594_CommnSd_A | C_LOPRI | BP1594 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.EBBWD.BP1594
BR4_Tags | BP1594_GenVoltLimit_A | Bore | Gen Voltage Limit | BP1594_GenVoltLimit_A | CAT_P3 | EBBWD-1750B001 | PRIV_ALARMACK | A_P1_SERV | BP1594_GenVoltLimit_A | BP1594_GenVoltLimit_A | C_LOPRI | BP1594 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.EBBWD.BP1594
BR4_Tags | BP1594_GenCurrUnbal_A | Bore | Current Unbalance | BP1594_GenCurrUnbal_A | CAT_P3 | EBBWD-1750B001 | PRIV_ALARMACK | A_P1_SERV | BP1594_GenCurrUnbal_A | BP1594_GenCurrUnbal_A | C_LOPRI | BP1594 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.EBBWD.BP1594
BR4_Tags | BP1594_LT02_LOLO_A | Bore | Internal Fuel Tank LoLo | BP1594_LT02_LOLO_A | CAT_P3 | EBBWD-1750B001 | PRIV_ALARMACK | A_P1_SERV | BP1594_LT02_LOLO_A | BP1594_LT02_LOLO_A | C_LOPRI | BP1594 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.EBBWD.BP1594.LT02
BR4_Tags | BP1594_ISOL_DOOR_A | Bore | Isolator Door Open | BP1594_ISOL_DOOR_A | CAT_P3 | EBBWD-1750B001 | PRIV_ALARMACK | A_P1_SERV | BP1594_ISOL_DOOR_A | BP1594_ISOL_DOOR_A | C_LOPRI | BP1594 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.EBBWD.BP1594
BR4_Tags | BP1594_NoFuelTkSel_A | Bore | No Fuel Tank Selected | BP1594_NoFuelTkSel_A | CAT_P3 | EBBWD-1750B001 | PRIV_ALARMACK | A_P1_SERV | BP1594_NoFuelTkSel_A | BP1594_NoFuelTkSel_A | C_LOPRI | BP1594 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.EBBWD.BP1594
BR4_Tags | BP1594_TT04_A | Bore | Intake Temperature Fault | BP1594_TT04_A | CAT_P3 | EBBWD-1750B001 | PRIV_ALARMACK | A_P1_SERV | BP1594_TT04_A | BP1594_TT04_A | C_LOPRI | BP1594 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.EBBWD.BP1594.TT04
BR4_Tags | BP1594_TT03_A | Bore | Coolant Temp Fault(ECU) | BP1594_TT03_A | CAT_P3 | EBBWD-1750B001 | PRIV_ALARMACK | A_P1_SERV | BP1594_TT03_A | BP1594_TT03_A | C_LOPRI | BP1594 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.EBBWD.BP1594.TT03
BR4_Tags | BP1594_PT04_A | Bore | Oil Pressure Fault | BP1594_PT04_A | CAT_P3 | EBBWD-1750B001 | PRIV_ALARMACK | A_P1_SERV | BP1594_PT04_A | BP1594_PT04_A | C_LOPRI | BP1594 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.EBBWD.BP1594.PT04
BR4_Tags | BP1594_TT01_HIHI_A | Bore | Motor Temp HiHi | BP1594_TT01_HIHI_A | CAT_P3 | EBBWD-1750B001 | PRIV_ALARMACK | A_P1_SERV | BP1594_TT01_HIHI_A | BP1594_TT01_HIHI_A | C_LOPRI | BP1594 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.EBBWD.BP1594.TT01
BR4_Tags | BP1594_PT03_HIHI_A | Bore | Boost Pressure HiHi | BP1594_PT03_HIHI_A | CAT_P3 | EBBWD-1750B001 | PRIV_ALARMACK | A_P1_SERV | BP1594_PT03_HIHI_A | BP1594_PT03_HIHI_A | C_LOPRI | BP1594 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.EBBWD.BP1594.PT03
BR4_Tags | BP1594_Stt_A | Bore | Too Many Starts | BP1594_Stt_A | CAT_P3 | EBBWD-1750B001 | PRIV_ALARMACK | A_P1_SERV | BP1594_Stt_A | BP1594_Stt_A | C_LOPRI | BP1594 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.EBBWD.BP1594
BR4_Tags | BP1594_TT03_HIHI_A | Bore | Coolant Temp HiHi | BP1594_TT03_HIHI_A | CAT_P3 | EBBWD-1750B001 | PRIV_ALARMACK | A_P1_SERV | BP1594_TT03_HIHI_A | BP1594_TT03_HIHI_A | C_LOPRI | BP1594 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.EBBWD.BP1594.TT03
BR4_Tags | BP1594_Commn_A | Bore | Common Alarm | BP1594_Commn_A | CAT_P3 | EBBWD-1750B001 | PRIV_ALARMACK | A_P1_SERV | BP1594_Commn_A | BP1594_Commn_A | C_LOPRI | BP1594 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.EBBWD.BP1594
BR4_Tags | BP1594_ECR_Overide_A | Bore | ECR Override is on | BP1594_ECR_Overide_A | CAT_P3 | EBBWD-1750B001 | PRIV_ALARMACK | A_P1_SERV | BP1594_ECR_Overide_A | BP1594_ECR_Overide_A | C_LOPRI | BP1594 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.EBBWD.BP1594
BR4_Tags | BP1594_LT01_Lo_A | Bore | Bore Level Lo Warn | BP1594_LT01_Lo_A | CAT_P3 | EBBWD-1750B001 | PRIV_ALARMACK | A_P1_SERV | BP1594_LT01_Lo_A | BP1594_LT01_Lo_A | C_LOPRI | BP1594 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.EBBWD.BP1594.LT01
BR4_Tags | BP1594_TT01_Hi_A | Bore | Motor Temp Hi Warn | BP1594_TT01_Hi_A | CAT_P3 | EBBWD-1750B001 | PRIV_ALARMACK | A_P1_SERV | BP1594_TT01_Hi_A | BP1594_TT01_Hi_A | C_LOPRI | BP1594 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.EBBWD.BP1594.TT01
BR4_Tags | BP1594_PT01_Hi_A | Bore | Upstream Pressure Hi Warn | BP1594_PT01_Hi_A | CAT_P3 | EBBWD-1750B001 | PRIV_ALARMACK | A_P1_SERV | BP1594_PT01_Hi_A | BP1594_PT01_Hi_A | C_LOPRI | BP1594 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.EBBWD.BP1594.PT01
BR4_Tags | BP1594_FT01_Lo_A | Bore | Discharge Flow Low Warn | BP1594_FT01_Lo_A | CAT_P3 | EBBWD-1750B001 | PRIV_ALARMACK | A_P1_SERV | BP1594_FT01_Lo_A | BP1594_FT01_Lo_A | C_LOPRI | BP1594 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.EBBWD.BP1594.FT01
BR4_Tags | BP1594_PT02_Hi_A | Bore | Downstream Pressure Hi Warn | BP1594_PT02_Hi_A | CAT_P3 | EBBWD-1750B001 | PRIV_ALARMACK | A_P1_SERV | BP1594_PT02_Hi_A | BP1594_PT02_Hi_A | C_LOPRI | BP1594 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.EBBWD.BP1594.PT02
BR4_Tags | BP1594_LT02_Lo_A | Bore | Internal Fuel Tank Lo Warn | BP1594_LT02_Lo_A | CAT_P3 | EBBWD-1750B001 | PRIV_ALARMACK | A_P1_SERV | BP1594_LT02_Lo_A | BP1594_LT02_Lo_A | C_LOPRI | BP1594 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.EBBWD.BP1594.LT02
BR4_Tags | BP1594_LT03_Lo_A | Bore | External Fuel Tank Lo Warn | BP1594_LT03_Lo_A | CAT_P3 | EBBWD-1750B001 | PRIV_ALARMACK | A_P1_SERV | BP1594_LT03_Lo_A | BP1594_LT03_Lo_A | C_LOPRI | BP1594 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.EBBWD.BP1594.LT03
BR4_Tags | BP1594_PT03_HI_A | Bore | Boost Pressure Hi Warn | BP1594_PT03_HI_A | CAT_P3 | EBBWD-1750B001 | PRIV_ALARMACK | A_P1_SERV | BP1594_PT03_HI_A | BP1594_PT03_HI_A | C_LOPRI | BP1594 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.EBBWD.BP1594.PT03
BR4_Tags | BP1594_PT04Wrn_A | Bore | Oil Pressure Warn | BP1594_PT04Wrn_A | CAT_P3 | EBBWD-1750B001 | PRIV_ALARMACK | A_P1_SERV | BP1594_PT04Wrn_A | BP1594_PT04Wrn_A | C_LOPRI | BP1594 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.EBBWD.BP1594.PT04
BR4_Tags | BP1594_TT03_HI_A | Bore | Coolant Temp Hi Warning | BP1594_TT03_HI_A | CAT_P3 | EBBWD-1750B001 | PRIV_ALARMACK | A_P1_SERV | BP1594_TT03_HI_A | BP1594_TT03_HI_A | C_LOPRI | BP1594 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.EBBWD.BP1594.TT03
BR4_Tags | BP1594_TT04Wrn_A | Bore | Intake Temp Warn | BP1594_TT04Wrn_A | CAT_P3 | EBBWD-1750B001 | PRIV_ALARMACK | A_P1_SERV | BP1594_TT04Wrn_A | BP1594_TT04Wrn_A | C_LOPRI | BP1594 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.EBBWD.BP1594.TT04
BR4_Tags | BP1594_TT03Wrn_A | Bore | Coolant Temp Warn(ECU) | BP1594_TT03Wrn_A | CAT_P3 | EBBWD-1750B001 | PRIV_ALARMACK | A_P1_SERV | BP1594_TT03Wrn_A | BP1594_TT03Wrn_A | C_LOPRI | BP1594 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.EBBWD.BP1594.TT03
BR4_Tags | EBP03_DCOK01_A | Bypass Panel EBP03 | 24V I/O Supply Fault | EBP03_DCOK01_A | CAT_P3 | EBBWD-1750B001 | PRIV_ALARMACK | A_P1_SERV | EBP03_DCOK01_A | EBP03_DCOK01_A | C_LOPRI | EBP03 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.EBBWD.EBP03
BR4_Tags | EBP03_DCOK02_A | Bypass Panel EBP03 | 24V Supply Fault | EBP03_DCOK02_A | CAT_P3 | EBBWD-1750B001 | PRIV_ALARMACK | A_P1_SERV | EBP03_DCOK02_A | EBP03_DCOK02_A | C_LOPRI | EBP03 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.EBBWD.EBP03
BR4_Tags | EBP03_DCR_Flt_A | Bypass Panel EBP03 | Decontactor Fault | EBP03_DCR_Flt_A | CAT_P3 | EBBWD-1750B001 | PRIV_ALARMACK | A_P1_SERV | EBP03_DCR_Flt_A | EBP03_DCR_Flt_A | C_LOPRI | EBP03 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.EBBWD.EBP03.DCR
BR4_Tags | EBP03_ECR_A | Bypass Panel EBP03 | ECR Fault | EBP03_ECR_A | CAT_P3 | EBBWD-1750B001 | PRIV_ALARMACK | A_P1_SERV | EBP03_ECR_A | EBP03_ECR_A | C_LOPRI | EBP03 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.EBBWD.EBP03
BR4_Tags | EBP03_ELR_A | Bypass Panel EBP03 | Earth Leakage Fault | EBP03_ELR_A | CAT_P3 | EBBWD-1750B001 | PRIV_ALARMACK | A_P1_SERV | EBP03_ELR_A | EBP03_ELR_A | C_LOPRI | EBP03 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.EBBWD.EBP03
BR4_Tags | EBP03_FT01_ChOK_A | Bypass Panel EBP03 | FT01 Channel Fault | EBP03_FT01_ChOK_A | CAT_P3 | EBBWD-1750B001 | PRIV_ALARMACK | A_P1_SERV | EBP03_FT01_ChOK_A | EBP03_FT01_ChOK_A | C_LOPRI | EBP03 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.EBBWD.EBP03.FT01
BR4_Tags | EBP03_FT01_LoLo_A | Bypass Panel EBP03 | Flow Low Trip | EBP03_FT01_LoLo_A | CAT_P3 | EBBWD-1750B001 | PRIV_ALARMACK | A_P1_SERV | EBP03_FT01_LoLo_A | EBP03_FT01_LoLo_A | C_LOPRI | EBP03 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.EBBWD.EBP03.FT01
BR4_Tags | EBP03_GEN_FLT_A | Bypass Panel EBP03 | Generator Fault | EBP03_GEN_FLT_A | CAT_P3 | EBBWD-1750B001 | PRIV_ALARMACK | A_P1_SERV | EBP03_GEN_FLT_A | EBP03_GEN_FLT_A | C_LOPRI | EBP03 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.EBBWD.EBP03
BR4_Tags | EBP03_LOS01_A | Bypass Panel EBP03 | Lock Off Stop Trip | EBP03_LOS01_A | CAT_P1 | EBBWD-1750B001 | PRIV_ALARMACK | A_P1_SERV | Lock Off Stop Trip | EBP03_LOS01_A | C_LOPRI | EBP03 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.EBBWD.EBP03.LOS01
BR4_Tags | EBP03_LT01_ChOK_A | Bypass Panel EBP03 | LT01 Channel Fault | EBP03_LT01_ChOK_A | CAT_P3 | EBBWD-1750B001 | PRIV_ALARMACK | A_P1_SERV | EBP03_LT01_ChOK_A | EBP03_LT01_ChOK_A | C_LOPRI | EBP03 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.EBBWD.EBP03.LT01
BR4_Tags | EBP03_LT01_LoLo_A | Bypass Panel EBP03 | Bore Level Low | EBP03_LT01_LoLo_A | CAT_P3 | EBBWD-1750B001 | PRIV_ALARMACK | A_P1_SERV | EBP03_LT01_LoLo_A | EBP03_LT01_LoLo_A | C_LOPRI | EBP03 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.EBBWD.EBP03.LT01
BR4_Tags | EBP03_PLCCommsFlt_A | Bypass Panel EBP03 | PLC Comms Fault | EBP03_PLCCommsFlt_A | CAT_P3 | EBBWD-1750B001 | PRIV_ALARMACK | A_P1_SERV | EBP03_PLCCommsFlt_A | EBP03_PLCCommsFlt_A | C_LOPRI | EBP03 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.EBBWD.EBP03
BR4_Tags | EBP03_PR01_A | Bypass Panel EBP03 | Protection Relay Fault | EBP03_PR01_A | CAT_P3 | EBBWD-1750B001 | PRIV_ALARMACK | A_P1_SERV | EBP03_PR01_A | EBP03_PR01_A | C_LOPRI | EBP03 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.EBBWD.EBP03
BR4_Tags | EBP03_PT01_ChOK_A | Bypass Panel EBP03 | PT01 Channel Fault | EBP03_PT01_ChOK_A | CAT_P3 | EBBWD-1750B001 | PRIV_ALARMACK | A_P1_SERV | EBP03_PT01_ChOK_A | EBP03_PT01_ChOK_A | C_LOPRI | EBP03 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.EBBWD.EBP03.PT01
BR4_Tags | EBP03_PT01_HiHi_A | Bypass Panel EBP03 | Upstream Preesure HiHi | EBP03_PT01_HiHi_A | CAT_P3 | EBBWD-1750B001 | PRIV_ALARMACK | A_P1_SERV | EBP03_PT01_HiHi_A | EBP03_PT01_HiHi_A | C_LOPRI | EBP03 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.EBBWD.EBP03.PT01
BR4_Tags | EBP03_PT02_ChOK_A | Bypass Panel EBP03 | PT02 Channel Fault | EBP03_PT02_ChOK_A | CAT_P3 | EBBWD-1750B001 | PRIV_ALARMACK | A_P1_SERV | EBP03_PT02_ChOK_A | EBP03_PT02_ChOK_A | C_LOPRI | EBP03 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.EBBWD.EBP03.PT02
BR4_Tags | EBP03_PT02_HiHi_A | Bypass Panel EBP03 | Upstream Preesure HiHi | EBP03_PT02_HiHi_A | CAT_P3 | EBBWD-1750B001 | PRIV_ALARMACK | A_P1_SERV | EBP03_PT02_HiHi_A | EBP03_PT02_HiHi_A | C_LOPRI | EBP03 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.EBBWD.EBP03.PT02
BR4_Tags | EBP03_R0S1OK_A | Bypass Panel EBP03 | PLC Card Fault | EBP03_R0S1OK_A | CAT_P3 | EBBWD-1750B001 | PRIV_ALARMACK | A_P1_SERV | EBP03_R0S1OK_A | EBP03_R0S1OK_A | C_LOPRI | EBP03 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.EBBWD.EBP03
BR4_Tags | EBP03_R0S2OK_A | Bypass Panel EBP03 | PLC Card Fault | EBP03_R0S2OK_A | CAT_P3 | EBBWD-1750B001 | PRIV_ALARMACK | A_P1_SERV | EBP03_R0S2OK_A | EBP03_R0S2OK_A | C_LOPRI | EBP03 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.EBBWD.EBP03
BR4_Tags | EBP03_R0S3OK_A | Bypass Panel EBP03 | PLC Card Fault | EBP03_R0S3OK_A | CAT_P3 | EBBWD-1750B001 | PRIV_ALARMACK | A_P1_SERV | EBP03_R0S3OK_A | EBP03_R0S3OK_A | C_LOPRI | EBP03 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.EBBWD.EBP03
BR4_Tags | EBP03_SD01Flt_A | Bypass Panel EBP03 | Surge Diverter Fault | EBP03_SD01Flt_A | CAT_P3 | EBBWD-1750B001 | PRIV_ALARMACK | A_P1_SERV | EBP03_SD01Flt_A | EBP03_SD01Flt_A | C_LOPRI | EBP03 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.EBBWD.EBP03
BR4_Tags | EBP03_Stt_A | Bypass Panel EBP03 | Too Many Starts | EBP03_Stt_A | CAT_P3 | EBBWD-1750B001 | PRIV_ALARMACK | A_P1_SERV | EBP03_Stt_A | EBP03_Stt_A | C_LOPRI | EBP03 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.EBBWD.EBP03
BR4_Tags | EBP03_SttFail_A | Bypass Panel EBP03 | Failed to Start | EBP03_SttFail_A | CAT_P3 | EBBWD-1750B001 | PRIV_ALARMACK | A_P1_SERV | EBP03_SttFail_A | EBP03_SttFail_A | C_LOPRI | EBP03 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.EBBWD.EBP03
BR4_Tags | EBP03_TT01_HiHi_A | Bypass Panel EBP03 | Motor Temp HiHi | EBP03_TT01_HiHi_A | CAT_P3 | EBBWD-1750B001 | PRIV_ALARMACK | A_P1_SERV | EBP03_TT01_HiHi_A | EBP03_TT01_HiHi_A | C_LOPRI | EBP03 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.EBBWD.EBP03.TT01
BR4_Tags | EBP03GEN_LS01_A | Bypass Panel EBP03 | Generator Low Fuel | EBP03GEN_LS01_A | CAT_P3 | EBBWD-1750B001 | PRIV_ALARMACK | A_P1_SERV | EBP03GEN_LS01_A | EBP03GEN_LS01_A | C_LOPRI | EBP03 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.EBBWD.EBP03
BR4_Tags | EBP03GEN_SttFail_A | Bypass Panel EBP03 | Generator Failed to Start | EBP03GEN_SttFail_A | CAT_P3 | EBBWD-1750B001 | PRIV_ALARMACK | A_P1_SERV | EBP03GEN_SttFail_A | EBP03GEN_SttFail_A | C_LOPRI | EBP03 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.EBBWD.EBP03
BR4_Tags | EBP03SST_CommsFlt_A | Bypass Panel EBP03 | Soft Starter Comms Fault | EBP03SST_CommsFlt_A | CAT_P3 | EBBWD-1750B001 | PRIV_ALARMACK | A_P1_SERV | EBP03SST_CommsFlt_A | EBP03SST_CommsFlt_A | C_LOPRI | EBP03 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.EBBWD.EBP03
BR4_Tags | EBP03SST_FLT_A | Bypass Panel EBP03 | Soft Starter Fault | EBP03SST_FLT_A | CAT_P3 | EBBWD-1750B001 | PRIV_ALARMACK | A_P1_SERV | EBP03SST_FLT_A | EBP03SST_FLT_A | C_LOPRI | EBP03 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.EBBWD.EBP03
BR4_Tags | EBP03415AC_A | Bypass Panel EBP03 | 415V AC Failed | EBP03415AC_A | CAT_P3 | EBBWD-1750B001 | PRIV_ALARMACK | A_P1_SERV | EBP03415AC_A | EBP03415AC_A | C_LOPRI | EBP03 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.EBBWD.EBP03
BR4_Tags | EBP03_CommsFlt_A | Bypass Panel EBP03 | Comms Fault | EBP03_CommsFlt_A | CAT_P3 | EBBWD-1750B001 | PRIV_ALARMACK | A_P1_SERV | EBP03_CommsFlt_A | EBP03_CommsFlt_A | C_LOPRI | EBP03 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.EBBWD.EBP03
BR4_Tags | EBP04_DCOK01_A | Bypass Panel EBP04 | 24V I/O Supply Fault | EBP04_DCOK01_A | CAT_P3 | EBBWD-1750B001 | PRIV_ALARMACK | A_P1_SERV | EBP04_DCOK01_A | EBP04_DCOK01_A | C_LOPRI | EBP04 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.EBBWD.EBP04
BR4_Tags | EBP04_DCOK02_A | Bypass Panel EBP04 | 24V Supply Fault | EBP04_DCOK02_A | CAT_P3 | EBBWD-1750B001 | PRIV_ALARMACK | A_P1_SERV | EBP04_DCOK02_A | EBP04_DCOK02_A | C_LOPRI | EBP04 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.EBBWD.EBP04
BR4_Tags | EBP04_DCR_Flt_A | Bypass Panel EBP04 | Decontactor Fault | EBP04_DCR_Flt_A | CAT_P3 | EBBWD-1750B001 | PRIV_ALARMACK | A_P1_SERV | EBP04_DCR_Flt_A | EBP04_DCR_Flt_A | C_LOPRI | EBP04 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.EBBWD.EBP04.DCR
BR4_Tags | EBP04_ECR_A | Bypass Panel EBP04 | ECR Fault | EBP04_ECR_A | CAT_P3 | EBBWD-1750B001 | PRIV_ALARMACK | A_P1_SERV | EBP04_ECR_A | EBP04_ECR_A | C_LOPRI | EBP04 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.EBBWD.EBP04
BR4_Tags | EBP04_ELR_A | Bypass Panel EBP04 | Earth Leakage Fault | EBP04_ELR_A | CAT_P3 | EBBWD-1750B001 | PRIV_ALARMACK | A_P1_SERV | EBP04_ELR_A | EBP04_ELR_A | C_LOPRI | EBP04 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.EBBWD.EBP04
BR4_Tags | EBP04_FT01_ChOK_A | Bypass Panel EBP04 | FT01 Channel Fault | EBP04_FT01_ChOK_A | CAT_P3 | EBBWD-1750B001 | PRIV_ALARMACK | A_P1_SERV | EBP04_FT01_ChOK_A | EBP04_FT01_ChOK_A | C_LOPRI | EBP04 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.EBBWD.EBP04.FT01
BR4_Tags | EBP04_FT01_LoLo_A | Bypass Panel EBP04 | Flow Low Trip | EBP04_FT01_LoLo_A | CAT_P3 | EBBWD-1750B001 | PRIV_ALARMACK | A_P1_SERV | EBP04_FT01_LoLo_A | EBP04_FT01_LoLo_A | C_LOPRI | EBP04 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.EBBWD.EBP04.FT01
BR4_Tags | EBP04_GEN_FLT_A | Bypass Panel EBP04 | Generator Fault | EBP04_GEN_FLT_A | CAT_P3 | EBBWD-1750B001 | PRIV_ALARMACK | A_P1_SERV | EBP04_GEN_FLT_A | EBP04_GEN_FLT_A | C_LOPRI | EBP04 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.EBBWD.EBP04
BR4_Tags | EBP04_LOS01_A | Bypass Panel EBP04 | Lock Off Stop Trip | EBP04_LOS01_A | CAT_P1 | EBBWD-1750B001 | PRIV_ALARMACK | A_P1_SERV | Lock Off Stop Trip | EBP04_LOS01_A | C_LOPRI | EBP04 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.EBBWD.EBP04.LOS01
BR4_Tags | EBP04_LT01_ChOK_A | Bypass Panel EBP04 | LT01 Channel Fault | EBP04_LT01_ChOK_A | CAT_P3 | EBBWD-1750B001 | PRIV_ALARMACK | A_P1_SERV | EBP04_LT01_ChOK_A | EBP04_LT01_ChOK_A | C_LOPRI | EBP04 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.EBBWD.EBP04.LT01
BR4_Tags | EBP04_LT01_LoLo_A | Bypass Panel EBP04 | Bore Level Low | EBP04_LT01_LoLo_A | CAT_P3 | EBBWD-1750B001 | PRIV_ALARMACK | A_P1_SERV | EBP04_LT01_LoLo_A | EBP04_LT01_LoLo_A | C_LOPRI | EBP04 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.EBBWD.EBP04.LT01
BR4_Tags | EBP04_PLCCommsFlt_A | Bypass Panel EBP04 | PLC Comms Fault | EBP04_PLCCommsFlt_A | CAT_P3 | EBBWD-1750B001 | PRIV_ALARMACK | A_P1_SERV | EBP04_PLCCommsFlt_A | EBP04_PLCCommsFlt_A | C_LOPRI | EBP04 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.EBBWD.EBP04
BR4_Tags | EBP04_PR01_A | Bypass Panel EBP04 | Protection Relay Fault | EBP04_PR01_A | CAT_P3 | EBBWD-1750B001 | PRIV_ALARMACK | A_P1_SERV | EBP04_PR01_A | EBP04_PR01_A | C_LOPRI | EBP04 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.EBBWD.EBP04
BR4_Tags | EBP04_PT01_ChOK_A | Bypass Panel EBP04 | PT01 Channel Fault | EBP04_PT01_ChOK_A | CAT_P3 | EBBWD-1750B001 | PRIV_ALARMACK | A_P1_SERV | EBP04_PT01_ChOK_A | EBP04_PT01_ChOK_A | C_LOPRI | EBP04 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.EBBWD.EBP04.PT01
BR4_Tags | EBP04_PT01_HiHi_A | Bypass Panel EBP04 | Upstream Preesure HiHi | EBP04_PT01_HiHi_A | CAT_P3 | EBBWD-1750B001 | PRIV_ALARMACK | A_P1_SERV | EBP04_PT01_HiHi_A | EBP04_PT01_HiHi_A | C_LOPRI | EBP04 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.EBBWD.EBP04.PT01
BR4_Tags | EBP04_PT02_ChOK_A | Bypass Panel EBP04 | PT02 Channel Fault | EBP04_PT02_ChOK_A | CAT_P3 | EBBWD-1750B001 | PRIV_ALARMACK | A_P1_SERV | EBP04_PT02_ChOK_A | EBP04_PT02_ChOK_A | C_LOPRI | EBP04 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.EBBWD.EBP04.PT02
BR4_Tags | EBP04_PT02_HiHi_A | Bypass Panel EBP04 | Upstream Preesure HiHi | EBP04_PT02_HiHi_A | CAT_P3 | EBBWD-1750B001 | PRIV_ALARMACK | A_P1_SERV | EBP04_PT02_HiHi_A | EBP04_PT02_HiHi_A | C_LOPRI | EBP04 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.EBBWD.EBP04.PT02
BR4_Tags | EBP04_R0S1OK_A | Bypass Panel EBP04 | PLC Card Fault | EBP04_R0S1OK_A | CAT_P3 | EBBWD-1750B001 | PRIV_ALARMACK | A_P1_SERV | EBP04_R0S1OK_A | EBP04_R0S1OK_A | C_LOPRI | EBP04 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.EBBWD.EBP04
BR4_Tags | EBP04_R0S2OK_A | Bypass Panel EBP04 | PLC Card Fault | EBP04_R0S2OK_A | CAT_P3 | EBBWD-1750B001 | PRIV_ALARMACK | A_P1_SERV | EBP04_R0S2OK_A | EBP04_R0S2OK_A | C_LOPRI | EBP04 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.EBBWD.EBP04
BR4_Tags | EBP04_R0S3OK_A | Bypass Panel EBP04 | PLC Card Fault | EBP04_R0S3OK_A | CAT_P3 | EBBWD-1750B001 | PRIV_ALARMACK | A_P1_SERV | EBP04_R0S3OK_A | EBP04_R0S3OK_A | C_LOPRI | EBP04 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.EBBWD.EBP04
BR4_Tags | EBP04_SD01Flt_A | Bypass Panel EBP04 | Surge Diverter Fault | EBP04_SD01Flt_A | CAT_P3 | EBBWD-1750B001 | PRIV_ALARMACK | A_P1_SERV | EBP04_SD01Flt_A | EBP04_SD01Flt_A | C_LOPRI | EBP04 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.EBBWD.EBP04
BR4_Tags | EBP04_Stt_A | Bypass Panel EBP04 | Too Many Starts | EBP04_Stt_A | CAT_P3 | EBBWD-1750B001 | PRIV_ALARMACK | A_P1_SERV | EBP04_Stt_A | EBP04_Stt_A | C_LOPRI | EBP04 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.EBBWD.EBP04
BR4_Tags | EBP04_SttFail_A | Bypass Panel EBP04 | Failed to Start | EBP04_SttFail_A | CAT_P3 | EBBWD-1750B001 | PRIV_ALARMACK | A_P1_SERV | EBP04_SttFail_A | EBP04_SttFail_A | C_LOPRI | EBP04 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.EBBWD.EBP04
BR4_Tags | EBP04_TT01_HiHi_A | Bypass Panel EBP04 | Motor Temp HiHi | EBP04_TT01_HiHi_A | CAT_P3 | EBBWD-1750B001 | PRIV_ALARMACK | A_P1_SERV | EBP04_TT01_HiHi_A | EBP04_TT01_HiHi_A | C_LOPRI | EBP04 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.EBBWD.EBP04.TT01
BR4_Tags | EBP04GEN_LS01_A | Bypass Panel EBP04 | Generator Low Fuel | EBP04GEN_LS01_A | CAT_P3 | EBBWD-1750B001 | PRIV_ALARMACK | A_P1_SERV | EBP04GEN_LS01_A | EBP04GEN_LS01_A | C_LOPRI | EBP04 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.EBBWD.EBP04
BR4_Tags | EBP04GEN_SttFail_A | Bypass Panel EBP04 | Generator Failed to Start | EBP04GEN_SttFail_A | CAT_P3 | EBBWD-1750B001 | PRIV_ALARMACK | A_P1_SERV | EBP04GEN_SttFail_A | EBP04GEN_SttFail_A | C_LOPRI | EBP04 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.EBBWD.EBP04
BR4_Tags | EBP04SST_CommsFlt_A | Bypass Panel EBP04 | Soft Starter Comms Fault | EBP04SST_CommsFlt_A | CAT_P3 | EBBWD-1750B001 | PRIV_ALARMACK | A_P1_SERV | EBP04SST_CommsFlt_A | EBP04SST_CommsFlt_A | C_LOPRI | EBP04 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.EBBWD.EBP04
BR4_Tags | EBP04SST_FLT_A | Bypass Panel EBP04 | Soft Starter Fault | EBP04SST_FLT_A | CAT_P3 | EBBWD-1750B001 | PRIV_ALARMACK | A_P1_SERV | EBP04SST_FLT_A | EBP04SST_FLT_A | C_LOPRI | EBP04 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.EBBWD.EBP04
BR4_Tags | EBP04415AC_A | Bypass Panel EBP04 | 415V AC Failed | EBP04415AC_A | CAT_P3 | EBBWD-1750B001 | PRIV_ALARMACK | A_P1_SERV | EBP04415AC_A | EBP04415AC_A | C_LOPRI | EBP04 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.EBBWD.EBP04
BR4_Tags | EBP04_CommsFlt_A | Bypass Panel EBP04 | Comms Fault | EBP04_CommsFlt_A | CAT_P3 | EBBWD-1750B001 | PRIV_ALARMACK | A_P1_SERV | EBP04_CommsFlt_A | EBP04_CommsFlt_A | C_LOPRI | EBP04 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.EBBWD.EBP04
BR4_Tags | EBP02_DCOK01_A | Bypass Panel EBP02 | 24V I/O Supply Fault | EBP02_DCOK01_A | CAT_P3 | EBBWD-1750B001 | PRIV_ALARMACK | A_P1_SERV | EBP02_DCOK01_A | EBP02_DCOK01_A | C_LOPRI | EBP02 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.EBBWD.EBP02
BR4_Tags | EBP02_DCOK02_A | Bypass Panel EBP02 | 24V Supply Fault | EBP02_DCOK02_A | CAT_P3 | EBBWD-1750B001 | PRIV_ALARMACK | A_P1_SERV | EBP02_DCOK02_A | EBP02_DCOK02_A | C_LOPRI | EBP02 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.EBBWD.EBP02
BR4_Tags | EBP02_DCR_Flt_A | Bypass Panel EBP02 | Decontactor Fault | EBP02_DCR_Flt_A | CAT_P3 | EBBWD-1750B001 | PRIV_ALARMACK | A_P1_SERV | EBP02_DCR_Flt_A | EBP02_DCR_Flt_A | C_LOPRI | EBP02 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.EBBWD.EBP02.DCR
BR4_Tags | EBP02_ECR_A | Bypass Panel EBP02 | ECR Fault | EBP02_ECR_A | CAT_P3 | EBBWD-1750B001 | PRIV_ALARMACK | A_P1_SERV | EBP02_ECR_A | EBP02_ECR_A | C_LOPRI | EBP02 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.EBBWD.EBP02
BR4_Tags | EBP02_ELR_A | Bypass Panel EBP02 | Earth Leakage Fault | EBP02_ELR_A | CAT_P3 | EBBWD-1750B001 | PRIV_ALARMACK | A_P1_SERV | EBP02_ELR_A | EBP02_ELR_A | C_LOPRI | EBP02 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.EBBWD.EBP02
BR4_Tags | EBP02_FT01_ChOK_A | Bypass Panel EBP02 | FT01 Channel Fault | EBP02_FT01_ChOK_A | CAT_P3 | EBBWD-1750B001 | PRIV_ALARMACK | A_P1_SERV | EBP02_FT01_ChOK_A | EBP02_FT01_ChOK_A | C_LOPRI | EBP02 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.EBBWD.EBP02.FT01
BR4_Tags | EBP02_FT01_LoLo_A | Bypass Panel EBP02 | Flow Low Trip | EBP02_FT01_LoLo_A | CAT_P3 | EBBWD-1750B001 | PRIV_ALARMACK | A_P1_SERV | EBP02_FT01_LoLo_A | EBP02_FT01_LoLo_A | C_LOPRI | EBP02 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.EBBWD.EBP02.FT01
BR4_Tags | EBP02_GEN_FLT_A | Bypass Panel EBP02 | Generator Fault | EBP02_GEN_FLT_A | CAT_P3 | EBBWD-1750B001 | PRIV_ALARMACK | A_P1_SERV | EBP02_GEN_FLT_A | EBP02_GEN_FLT_A | C_LOPRI | EBP02 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.EBBWD.EBP02
BR4_Tags | EBP02_LOS01_A | Bypass Panel EBP02 | Lock Off Stop Trip | EBP02_LOS01_A | CAT_P1 | EBBWD-1750B001 | PRIV_ALARMACK | A_P1_SERV | Lock Off Stop Trip | EBP02_LOS01_A | C_LOPRI | EBP02 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.EBBWD.EBP02.LOS01
BR4_Tags | EBP02_LT01_ChOK_A | Bypass Panel EBP02 | LT01 Channel Fault | EBP02_LT01_ChOK_A | CAT_P3 | EBBWD-1750B001 | PRIV_ALARMACK | A_P1_SERV | EBP02_LT01_ChOK_A | EBP02_LT01_ChOK_A | C_LOPRI | EBP02 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.EBBWD.EBP02.LT01
BR4_Tags | EBP02_LT01_LoLo_A | Bypass Panel EBP02 | Bore Level Low | EBP02_LT01_LoLo_A | CAT_P3 | EBBWD-1750B001 | PRIV_ALARMACK | A_P1_SERV | EBP02_LT01_LoLo_A | EBP02_LT01_LoLo_A | C_LOPRI | EBP02 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.EBBWD.EBP02.LT01
BR4_Tags | EBP02_PLCCommsFlt_A | Bypass Panel EBP02 | PLC Comms Fault | EBP02_PLCCommsFlt_A | CAT_P3 | EBBWD-1750B001 | PRIV_ALARMACK | A_P1_SERV | EBP02_PLCCommsFlt_A | EBP02_PLCCommsFlt_A | C_LOPRI | EBP02 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.EBBWD.EBP02
BR4_Tags | EBP02_PR01_A | Bypass Panel EBP02 | Protection Relay Fault | EBP02_PR01_A | CAT_P3 | EBBWD-1750B001 | PRIV_ALARMACK | A_P1_SERV | EBP02_PR01_A | EBP02_PR01_A | C_LOPRI | EBP02 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.EBBWD.EBP02
BR4_Tags | EBP02_PT01_ChOK_A | Bypass Panel EBP02 | PT01 Channel Fault | EBP02_PT01_ChOK_A | CAT_P3 | EBBWD-1750B001 | PRIV_ALARMACK | A_P1_SERV | EBP02_PT01_ChOK_A | EBP02_PT01_ChOK_A | C_LOPRI | EBP02 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.EBBWD.EBP02.PT01
BR4_Tags | EBP02_PT01_HiHi_A | Bypass Panel EBP02 | Upstream Preesure HiHi | EBP02_PT01_HiHi_A | CAT_P3 | EBBWD-1750B001 | PRIV_ALARMACK | A_P1_SERV | EBP02_PT01_HiHi_A | EBP02_PT01_HiHi_A | C_LOPRI | EBP02 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.EBBWD.EBP02.PT01
BR4_Tags | EBP02_PT02_ChOK_A | Bypass Panel EBP02 | PT02 Channel Fault | EBP02_PT02_ChOK_A | CAT_P3 | EBBWD-1750B001 | PRIV_ALARMACK | A_P1_SERV | EBP02_PT02_ChOK_A | EBP02_PT02_ChOK_A | C_LOPRI | EBP02 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.EBBWD.EBP02.PT02
BR4_Tags | EBP02_PT02_HiHi_A | Bypass Panel EBP02 | Upstream Preesure HiHi | EBP02_PT02_HiHi_A | CAT_P3 | EBBWD-1750B001 | PRIV_ALARMACK | A_P1_SERV | EBP02_PT02_HiHi_A | EBP02_PT02_HiHi_A | C_LOPRI | EBP02 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.EBBWD.EBP02.PT02
BR4_Tags | EBP02_R0S1OK_A | Bypass Panel EBP02 | PLC Card Fault | EBP02_R0S1OK_A | CAT_P3 | EBBWD-1750B001 | PRIV_ALARMACK | A_P1_SERV | EBP02_R0S1OK_A | EBP02_R0S1OK_A | C_LOPRI | EBP02 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.EBBWD.EBP02
BR4_Tags | EBP02_R0S2OK_A | Bypass Panel EBP02 | PLC Card Fault | EBP02_R0S2OK_A | CAT_P3 | EBBWD-1750B001 | PRIV_ALARMACK | A_P1_SERV | EBP02_R0S2OK_A | EBP02_R0S2OK_A | C_LOPRI | EBP02 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.EBBWD.EBP02
BR4_Tags | EBP02_R0S3OK_A | Bypass Panel EBP02 | PLC Card Fault | EBP02_R0S3OK_A | CAT_P3 | EBBWD-1750B001 | PRIV_ALARMACK | A_P1_SERV | EBP02_R0S3OK_A | EBP02_R0S3OK_A | C_LOPRI | EBP02 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.EBBWD.EBP02
BR4_Tags | EBP02_SD01Flt_A | Bypass Panel EBP02 | Surge Diverter Fault | EBP02_SD01Flt_A | CAT_P3 | EBBWD-1750B001 | PRIV_ALARMACK | A_P1_SERV | EBP02_SD01Flt_A | EBP02_SD01Flt_A | C_LOPRI | EBP02 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.EBBWD.EBP02
BR4_Tags | EBP02_Stt_A | Bypass Panel EBP02 | Too Many Starts | EBP02_Stt_A | CAT_P3 | EBBWD-1750B001 | PRIV_ALARMACK | A_P1_SERV | EBP02_Stt_A | EBP02_Stt_A | C_LOPRI | EBP02 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.EBBWD.EBP02
BR4_Tags | EBP02_SttFail_A | Bypass Panel EBP02 | Failed to Start | EBP02_SttFail_A | CAT_P3 | EBBWD-1750B001 | PRIV_ALARMACK | A_P1_SERV | EBP02_SttFail_A | EBP02_SttFail_A | C_LOPRI | EBP02 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.EBBWD.EBP02
BR4_Tags | EBP02_TT01_HiHi_A | Bypass Panel EBP02 | Motor Temp HiHi | EBP02_TT01_HiHi_A | CAT_P3 | EBBWD-1750B001 | PRIV_ALARMACK | A_P1_SERV | EBP02_TT01_HiHi_A | EBP02_TT01_HiHi_A | C_LOPRI | EBP02 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.EBBWD.EBP02.TT01
BR4_Tags | EBP02GEN_LS01_A | Bypass Panel EBP02 | Generator Low Fuel | EBP02GEN_LS01_A | CAT_P3 | EBBWD-1750B001 | PRIV_ALARMACK | A_P1_SERV | EBP02GEN_LS01_A | EBP02GEN_LS01_A | C_LOPRI | EBP02 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.EBBWD.EBP02
BR4_Tags | EBP02GEN_SttFail_A | Bypass Panel EBP02 | Generator Failed to Start | EBP02GEN_SttFail_A | CAT_P3 | EBBWD-1750B001 | PRIV_ALARMACK | A_P1_SERV | EBP02GEN_SttFail_A | EBP02GEN_SttFail_A | C_LOPRI | EBP02 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.EBBWD.EBP02
BR4_Tags | EBP02SST_CommsFlt_A | Bypass Panel EBP02 | Soft Starter Comms Fault | EBP02SST_CommsFlt_A | CAT_P3 | EBBWD-1750B001 | PRIV_ALARMACK | A_P1_SERV | EBP02SST_CommsFlt_A | EBP02SST_CommsFlt_A | C_LOPRI | EBP02 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.EBBWD.EBP02
BR4_Tags | EBP02SST_FLT_A | Bypass Panel EBP02 | Soft Starter Fault | EBP02SST_FLT_A | CAT_P3 | EBBWD-1750B001 | PRIV_ALARMACK | A_P1_SERV | EBP02SST_FLT_A | EBP02SST_FLT_A | C_LOPRI | EBP02 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.EBBWD.EBP02
BR4_Tags | EBP02415AC_A | Bypass Panel EBP02 | 415V AC Failed | EBP02415AC_A | CAT_P3 | EBBWD-1750B001 | PRIV_ALARMACK | A_P1_SERV | EBP02415AC_A | EBP02415AC_A | C_LOPRI | EBP02 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.EBBWD.EBP02
BR4_Tags | EBP02_CommsFlt_A | Bypass Panel EBP02 | Comms Fault | EBP02_CommsFlt_A | CAT_P3 | EBBWD-1750B001 | PRIV_ALARMACK | A_P1_SERV | EBP02_CommsFlt_A | EBP02_CommsFlt_A | C_LOPRI | EBP02 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.EBBWD.EBP02
BR4_Tags | BP1590_VSGComms_A | Bore | VSG Controller Comms Fault | BP1590_VSGComms_A | CAT_P3 | EBBWD-1750B001 | PRIV_ALARMACK | A_P1_SERV | Comap Controller Comms Fault | BP1590_VSGComms_A | C_LOPRI | BP1590 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.EBBWD.BP1590
BR4_Tags | BP1591_VSGComms_A | Bore | VSG Controller Comms Fault | BP1591_VSGComms_A | CAT_P3 | EBBWD-1750B001 | PRIV_ALARMACK | A_P1_SERV | Comap Controller Comms Fault | BP1591_VSGComms_A | C_LOPRI | BP1591 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.EBBWD.BP1591
BR4_Tags | BP1592_VSGComms_A | Bore | VSG Controller Comms Fault | BP1592_VSGComms_A | CAT_P3 | EBBWD-1750B001 | PRIV_ALARMACK | A_P1_SERV | Comap Controller Comms Fault | BP1592_VSGComms_A | C_LOPRI | BP1592 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.BP1592
BR4_Tags | BP1593_VSGComms_A | Bore | VSG Controller Comms Fault | BP1593_VSGComms_A | CAT_P3 | EBBWD-1750B001 | PRIV_ALARMACK | A_P1_SERV | Comap Controller Comms Fault | BP1593_VSGComms_A | C_LOPRI | BP1593 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.EBBWD.BP1593
BR4_Tags | BP1594_VSGComms_A | Bore | VSG Controller Comms Fault | BP1594_VSGComms_A | CAT_P3 | EBBWD-1750B001 | PRIV_ALARMACK | A_P1_SERV | Comap Controller Comms Fault | BP1594_VSGComms_A | C_LOPRI | BP1594 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.EBBWD.BP1594
BR4_Tags | BP1590_CommsFlt_A | Bore | Comms to BPL751 Failed | BP1590_CommsFlt_A | CAT_P3 | EBBWD-1750B001 | PRIV_ALARMACK | A_P1_SERV | Comms to BPL751 Failed | BP1590_CommsFlt_A | C_LOPRI | BP1590 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.EBBWD.BP1590
BR4_Tags | BP1591_CommsFlt_A | Bore | Comms to BPL751 Failed | BP1591_CommsFlt_A | CAT_P3 | EBBWD-1750B001 | PRIV_ALARMACK | A_P1_SERV | Comms to BPL751 Failed | BP1591_CommsFlt_A | C_LOPRI | BP1591 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.EBBWD.BP1591
BR4_Tags | BP1592_CommsFlt_A | Bore | Comms to BPL751 Failed | BP1592_CommsFlt_A | CAT_P3 | EBBWD-1750B001 | PRIV_ALARMACK | A_P1_SERV | Comms to BPL751 Failed | BP1592_CommsFlt_A | C_LOPRI | BP1592 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.BP1592
BR4_Tags | BP1593_CommsFlt_A | Bore | Comms to BPL751 Failed | BP1593_CommsFlt_A | CAT_P3 | EBBWD-1750B001 | PRIV_ALARMACK | A_P1_SERV | Comms to BPL751 Failed | BP1593_CommsFlt_A | C_LOPRI | BP1593 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.EBBWD.BP1593
BR4_Tags | BP1594_CommsFlt_A | Bore | Comms to BPL751 Failed | BP1594_CommsFlt_A | CAT_P3 | EBBWD-1750B001 | PRIV_ALARMACK | A_P1_SERV | Comms to BPL751 Failed | BP1594_CommsFlt_A | C_LOPRI | BP1594 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.EBBWD.BP1594
BR4_Tags | WSPB2_CommsFlt_A | Bore | WSPB2 Comms Failed | WSPB2_CommsFlt_A | CAT_P3 | WBBWD-1750B004 | PRIV_ALARMACK | A_P1_SERV | WSPB2 Comms Failed | WSPB2_CommsFlt_A | C_LOPRI | WSPB2 | Class_Equipment | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.WSPB2
BR4_Tags | WSPB2_PT01_Hi_A | Bore | WSPB2 High Upstream Pressure Warning | WSPB2_PT01_Hi_A | CAT_P3 | WBBWD-1750B004 | PRIV_ALARMACK | A_P1_SERV | WSPB2 High Upstream Pressure Warning | WSPB2_PT01_Hi_A | C_LOPRI | WSPB2 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.WSPB2.PT01
BR4_Tags | WSPB2_PT01_HiHi_A | Bore | WSPB2 High Upstream Pressure Shutdown | WSPB2_PT01_HiHi_A | CAT_P3 | WBBWD-1750B004 | PRIV_ALARMACK | A_P1_SERV | WSPB2 High Upstream Pressure Shutdown | WSPB2_PT01_HiHi_A | C_LOPRI | WSPB2 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.WSPB2.PT01
BR4_Tags | WSPB2_PT02_Hi_A | Bore | WSPB2 High Downstream Pressure Warning | WSPB2_PT02_Hi_A | CAT_P3 | WBBWD-1750B004 | PRIV_ALARMACK | A_P1_SERV | WSPB2 High Downstream Pressure Warning | WSPB2_PT02_Hi_A | C_LOPRI | WSPB2 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.WSPB2.PT02
BR4_Tags | WSPB2_PT02_HiHi_A | Bore | WSPB2 High Downstream Pressure Shutdown | WSPB2_PT02_HiHi_A | CAT_P3 | WBBWD-1750B004 | PRIV_ALARMACK | A_P1_SERV | WSPB2 High Downstream Pressure Shutdown | WSPB2_PT02_HiHi_A | C_LOPRI | WSPB2 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.WATER.WBBWD.WSPB2.PT02
BR4_Tags | BPL503_ATPFlt_A | DLC Computer | ATP Fault Trip Alarm | BPL503_ATPFlt_A | CAT_P3 | BP1DLC1 | PRIV_ALARMACK | A_LD_TLO1 | ATP Fault Trip Alarm | BPL503_ATPFlt_A | C_LOPRI | TrainComms | Class_Process | BR4_Cluster1 | BR4.OUTLOADING.BTL501.DLC01.TrainComms
BR4_Tags | BPL503_ATPTpd_A | DLC Computer | ATP Transponder Trip Alarm | BPL503_ATPTpd_A | CAT_P3 | BP1DLC1 | PRIV_ALARMACK | A_LD_TLO1 | ATP Transponder Trip Alarm | BPL503_ATPTpd_A | C_LOPRI | TrainComms | Class_Process | BR4_Cluster1 | BR4.OUTLOADING.BTL501.DLC01.TrainComms
BR4_Tags | BPL503_ATSATPComms_A | DLC Computer | ATS ATP Communications Trip Alarm | BPL503_ATSATPComms_A | CAT_P3 | BP1DLC1 | PRIV_ALARMACK | A_LD_TLO1 | ATS ATP Communications Trip Alarm | BPL503_ATSATPComms_A | C_LOPRI | TrainComms | Class_Process | BR4_Cluster1 | BR4.OUTLOADING.BTL501.DLC01.TrainComms
BR4_Tags | BPL503_ATSDLCComms_A | DLC Computer | ATS DLC Communications Trip Alarm | BPL503_ATSDLCComms_A | CAT_P3 | BP1DLC1 | PRIV_ALARMACK | A_LD_TLO1 | ATS DLC Communications Trip Alarm | BPL503_ATSDLCComms_A | C_LOPRI | TrainComms | Class_Process | BR4_Cluster1 | BR4.OUTLOADING.BTL501.DLC01.TrainComms
BR4_Tags | BPL503_BPL501CommsFlt_A | Brockman 4 DLC | BPL503 BTL501 Communications Fault Alarm | BPL503_BPL501CommsFlt_A | CAT_P3 | BPL503 | PRIV_ALARMACK | A_LD_TLO1 | BPL503 BTL501 Communications Fault Alarm | BPL503_BPL501CommsFlt_A | C_LOPRI | BPL503 | Class_Equipment | BR4_Cluster1 | BR4.OUTLOADING.BTL501.DLC01.TrainComms
BR4_Tags | BPL503_BPL501IOScan_A | Brockman 4 DLC | BPL503 BPL501 Scanner Communications Fault A | BPL503_BPL501IOScan_A | CAT_P3 | BPL503 | PRIV_ALARMACK | A_LD_TLO1 | BPL503 BPL501 Scanner Communications Fault A | BPL503_BPL501IOScan_A | C_LOPRI | BPL503 | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL503
BR4_Tags | BPL503_BPL803CommsFlt_A | Brockman 4 DLC | BPL503 BPL803 Communications Fault Alarm | BPL503_BPL803CommsFlt_A | CAT_P3 | BPL503 | PRIV_ALARMACK | A_LD_TLO1 | BPL503 BPL803 Communications Fault Alarm | BPL503_BPL803CommsFlt_A | C_LOPRI | BPL503 | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL503
BR4_Tags | BPL503_BrkAppFlt_A | DLC Computer | Brake Apply Fail To Stop Alarm | BPL503_BrkAppFlt_A | CAT_P3 | BP1DLC1 | PRIV_ALARMACK | A_LD_TLO1 | Brake Apply Fail To Stop Alarm | BPL503_BrkAppFlt_A | C_LOPRI | TrainShutdowns | Class_Process | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL503
BR4_Tags | BPL503_BrkPressHi_A | DLC Computer | Brake Pipe Pressure High Alarm | BPL503_BrkPressHi_A | CAT_P3 | BP1DLC1 | PRIV_ALARMACK | A_LD_TLO1 | Brake Pipe Pressure High Alarm | BPL503_BrkPressHi_A | C_LOPRI | TrainBrakes | Class_Process | BR4_Cluster1 | BR4.OUTLOADING.BTL501.DLC01.TrainBrakes
BR4_Tags | BPL503_BTL501DLC01MBComms_A | Brockman 4 DLC | BPL501 Modbus Communications Failed Alarm | BPL503_BTL501DLC01MBComms_A | CAT_P3 | BP1DLC1 | PRIV_ALARMACK | A_LD_TLO1 | BPL501 Modbus Communications Failed Alarm | BPL503_BTL501DLC01MBComms_A | C_LOPRI | DLCLink | Class_Process | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL503
BR4_Tags | BTL501_GreenLightSeqFlt_A | BTL501 Entry/Exit Lights | Green Light Request Before TLO GrpStt Fault | BTL501_GreenLightSeqFlt_A | CAT_P3 |  | PRIV_ALARMACK | A_LD_TLO1 | Green Light Request Before TLO GrpStt Fault | BTL501_GreenLightSeqFlt_A |  |  |  | BR4_Cluster1 | BR4.OUTLOADING.BTL501.Lights
BR4_Tags | BPL503_CABAxl1Flt_A | DLC Computer | Cabin Loco Locked Axle 1 Alarm | BPL503_CABAxl1Flt_A | CAT_P3 | BP1DLC1 | PRIV_ALARMACK | A_LD_TLO1 | Cabin Loco Locked Axle 1 Alarm | BPL503_CABAxl1Flt_A | C_LOPRI | TrainCabin | Class_Process | BR4_Cluster1 | BR4.OUTLOADING.BTL501.DLC01.TrainCabin
BR4_Tags | BPL503_CABAxl2Flt_A | DLC Computer | Cabin Loco Locked Axle 2 Alarm | BPL503_CABAxl2Flt_A | CAT_P3 | BP1DLC1 | PRIV_ALARMACK | A_LD_TLO1 | Cabin Loco Locked Axle 2 Alarm | BPL503_CABAxl2Flt_A | C_LOPRI | TrainCabin | Class_Process | BR4_Cluster1 | BR4.OUTLOADING.BTL501.DLC01.TrainCabin
BR4_Tags | BPL503_CABAxl3Flt_A | DLC Computer | Cabin Loco Locked Axle 3 Alarm | BPL503_CABAxl3Flt_A | CAT_P3 | BP1DLC1 | PRIV_ALARMACK | A_LD_TLO1 | Cabin Loco Locked Axle 3 Alarm | BPL503_CABAxl3Flt_A | C_LOPRI | TrainCabin | Class_Process | BR4_Cluster1 | BR4.OUTLOADING.BTL501.DLC01.TrainCabin
BR4_Tags | BPL503_CABAxl4Flt_A | DLC Computer | Cabin Loco Locked Axle 4 Alarm | BPL503_CABAxl4Flt_A | CAT_P3 | BP1DLC1 | PRIV_ALARMACK | A_LD_TLO1 | Cabin Loco Locked Axle 4 Alarm | BPL503_CABAxl4Flt_A | C_LOPRI | TrainCabin | Class_Process | BR4_Cluster1 | BR4.OUTLOADING.BTL501.DLC01.TrainCabin
BR4_Tags | BPL503_CABAxl5Flt_A | DLC Computer | Cabin Loco Locked Axle 5 Alarm | BPL503_CABAxl5Flt_A | CAT_P3 | BP1DLC1 | PRIV_ALARMACK | A_LD_TLO1 | Cabin Loco Locked Axle 5 Alarm | BPL503_CABAxl5Flt_A | C_LOPRI | TrainCabin | Class_Process | BR4_Cluster1 | BR4.OUTLOADING.BTL501.DLC01.TrainCabin
BR4_Tags | BPL503_CABAxl6Flt_A | DLC Computer | Cabin Loco Locked Axle 6 Alarm | BPL503_CABAxl6Flt_A | CAT_P3 | BP1DLC1 | PRIV_ALARMACK | A_LD_TLO1 | Cabin Loco Locked Axle 6 Alarm | BPL503_CABAxl6Flt_A | C_LOPRI | TrainCabin | Class_Process | BR4_Cluster1 | BR4.OUTLOADING.BTL501.DLC01.TrainCabin
BR4_Tags | BPL503_CABBatFlt_A | DLC Computer | Cabin Shutdown No Battery Charge Alarm | BPL503_CABBatFlt_A | CAT_P3 | BP1DLC1 | PRIV_ALARMACK | A_LD_TLO1 | Cabin Shutdown No Battery Charge Alarm | BPL503_CABBatFlt_A | C_LOPRI | TrainCabin | Class_Process | BR4_Cluster1 | BR4.OUTLOADING.BTL501.DLC01.TrainCabin
BR4_Tags | BPL503_CABCrnkPressHi_A | DLC Computer | Cabin Shutdown Crankcase Oil Pressure Alarm | BPL503_CABCrnkPressHi_A | CAT_P3 | BP1DLC1 | PRIV_ALARMACK | A_LD_TLO1 | Cabin Shutdown Crankcase Oil Pressure Alarm | BPL503_CABCrnkPressHi_A | C_LOPRI | TrainCabin | Class_Process | BR4_Cluster1 | BR4.OUTLOADING.BTL501.DLC01.TrainCabin
BR4_Tags | BPL503_CABElectCtrl_A | DLC Computer | Cabin Shutdown Electrical Control Alarm | BPL503_CABElectCtrl_A | CAT_P3 | BP1DLC1 | PRIV_ALARMACK | A_LD_TLO1 | Cabin Shutdown Electrical Control Alarm | BPL503_CABElectCtrl_A | C_LOPRI | TrainCabin | Class_Process | BR4_Cluster1 | BR4.OUTLOADING.BTL501.DLC01.TrainCabin
BR4_Tags | BPL503_CABEngOSpd_A | DLC Computer | Cabin Shutdown Engine Overspeed Alarm | BPL503_CABEngOSpd_A | CAT_P3 | BP1DLC1 | PRIV_ALARMACK | A_LD_TLO1 | Cabin Shutdown Engine Overspeed Alarm | BPL503_CABEngOSpd_A | C_LOPRI | TrainCabin | Class_Process | BR4_Cluster1 | BR4.OUTLOADING.BTL501.DLC01.TrainCabin
BR4_Tags | BPL503_CABOilPressLo_A | DLC Computer | Cabin Shutdown Low Oil Pressure Alarm | BPL503_CABOilPressLo_A | CAT_P3 | BP1DLC1 | PRIV_ALARMACK | A_LD_TLO1 | Cabin Shutdown Low Oil Pressure Alarm | BPL503_CABOilPressLo_A | C_LOPRI | TrainCabin | Class_Process | BR4_Cluster1 | BR4.OUTLOADING.BTL501.DLC01.TrainCabin
BR4_Tags | BPL503_CABWtrFlwLo_A | DLC Computer | Cabin Shutdown Low Water Flow Alarm | BPL503_CABWtrFlwLo_A | CAT_P3 | BP1DLC1 | PRIV_ALARMACK | A_LD_TLO1 | Cabin Shutdown Low Water Flow Alarm | BPL503_CABWtrFlwLo_A | C_LOPRI | TrainCabin | Class_Process | BR4_Cluster1 | BR4.OUTLOADING.BTL501.DLC01.TrainCabin
BR4_Tags | BPL503_CABWtrPressLo_A | DLC Computer | Cabin Shutdown Low Water Pressureure Alarm | BPL503_CABWtrPressLo_A | CAT_P3 | BP1DLC1 | PRIV_ALARMACK | A_LD_TLO1 | Cabin Shutdown Low Water Pressureure Alarm | BPL503_CABWtrPressLo_A | C_LOPRI | TrainCabin | Class_Process | BR4_Cluster1 | BR4.OUTLOADING.BTL501.DLC01.TrainCabin
BR4_Tags | BPL503_CPUEthModLinkOK_A | Brockman 4 DLC | Ethernet Module Link Status Alarm | BPL503_CPUEthModLinkOK_A | CAT_P3 | BPL503 | PRIV_ALARMACK | A_LD_TLO1 | Ethernet Module Link Status Alarm | BPL503_CPUEthModLinkOK_A | C_LOPRI | BPL503 | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL503
BR4_Tags | BPL503_CPUEthModRnng_A | Brockman 4 DLC | Ethernet Module Module Not Running Alarm | BPL503_CPUEthModRnng_A | CAT_P3 | BPL503 | PRIV_ALARMACK | A_LD_TLO1 | Ethernet Module Module Not Running Alarm | BPL503_CPUEthModRnng_A | C_LOPRI | BPL503 | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL503
BR4_Tags | BPL503_CtrlEStopFlt_A | DLC Computer | Train Loadout Control E-Stop Trip Alarm | BPL503_CtrlEStopFlt_A | CAT_P3 | BP1DLC1 | PRIV_ALARMACK | A_LD_TLO1 | Train Loadout Control E-Stop Trip Alarm | BPL503_CtrlEStopFlt_A | C_LOPRI | DLCEStop | Class_Process | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL503
BR4_Tags | BPL503_D0R0S0OK_A | Brockman 4 DLC | BPL503 Rack 00 Slot 00 Hardware Fault Alarm | BPL503_D0R0S0OK_A | CAT_P3 | BPL503 | PRIV_ALARMACK | A_LD_TLO1 | BPL503 Rack 00 Slot 00 Hardware Fault Alarm | BPL503_D0R0S0OK_A | C_LOPRI | BPL503 | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL503
BR4_Tags | BPL503_D0R0S1OK_A | Brockman 4 DLC | BPL503 Rack 00 Slot 01 Hardware Fault Alarm | BPL503_D0R0S1OK_A | CAT_P3 | BPL503 | PRIV_ALARMACK | A_LD_TLO1 | BPL503 Rack 00 Slot 01 Hardware Fault Alarm | BPL503_D0R0S1OK_A | C_LOPRI | BPL503 | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL503
BR4_Tags | BPL503_D0R0S2OK_A | Brockman 4 DLC | BPL503 Rack 00 Slot 02 Hardware Fault Alarm | BPL503_D0R0S2OK_A | CAT_P3 | BPL503 | PRIV_ALARMACK | A_LD_TLO1 | BPL503 Rack 00 Slot 02 Hardware Fault Alarm | BPL503_D0R0S2OK_A | C_LOPRI | BPL503 | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL503 | Slot2_A
BR4_Tags | BPL503_D0R0S3OK_A | Brockman 4 DLC | BPL503 Rack 00 Slot 03 Hardware Fault Alarm | BPL503_D0R0S3OK_A | CAT_P3 | BPL503 | PRIV_ALARMACK | A_LD_TLO1 | BPL503 Rack 00 Slot 03 Hardware Fault Alarm | BPL503_D0R0S3OK_A | C_LOPRI | BPL503 | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL503 | Slot3_A
BR4_Tags | BPL503_DropHOK_A | Brockman 4 DLC | Drop H Island NIP Module or Island Bus Fault | BPL503_DropHOK_A | CAT_P3 | BPL503 | PRIV_ALARMACK | A_LD_TLO1 | Drop H Island NIP Module or Island Bus Fault | BPL503_DropHOK_A | C_LOPRI | BPL503 | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL503
BR4_Tags | BPL503_EBrkAppFlt_A | DLC Computer | Train E-Brake Applied Trip Alarm | BPL503_EBrkAppFlt_A | CAT_P3 | BP1DLC1 | PRIV_ALARMACK | A_LD_TLO1 | Train E-Brake Applied Trip Alarm | BPL503_EBrkAppFlt_A | C_LOPRI | TrainBrakes | Class_Process | BR4_Cluster1 | BR4.OUTLOADING.BTL501.DLC01.TrainBrakes
BR4_Tags | BPL503_EOTBatLo_A | DLC Computer | EOT Battery Low Warning Alarm | BPL503_EOTBatLo_A | CAT_P3 | BP1DLC1 | PRIV_ALARMACK | A_LD_TLO1 | EOT Battery Low Warning Alarm | BPL503_EOTBatLo_A | C_LOPRI | TrainGeneral | Class_Process | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL503
BR4_Tags | BPL503_EOTComms_A | DLC Computer | EOT Communications Warning Alarm | BPL503_EOTComms_A | CAT_P3 | BP1DLC1 | PRIV_ALARMACK | A_LD_TLO1 | EOT Communications Warning Alarm | BPL503_EOTComms_A | C_LOPRI | TrainGeneral | Class_Process | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL503
BR4_Tags | BPL503_EPICDLCComms_A | DLC Computer | EPIC DLC Communications Trip Alarm | BPL503_EPICDLCComms_A | CAT_P3 | BP1DLC1 | PRIV_ALARMACK | A_LD_TLO1 | EPIC DLC Communications Trip Alarm | BPL503_EPICDLCComms_A | C_LOPRI | TrainComms | Class_Process | BR4_Cluster1 | BR4.OUTLOADING.BTL501.DLC01.TrainComms
BR4_Tags | BPL503_EstopRstReq_A | DLC Computer | E-Stop Reset Required Warning Alarm | BPL503_EstopRstReq_A | CAT_P3 | BP1DLC1 | PRIV_ALARMACK | A_LD_TLO1 | E-Stop Reset Required Warning Alarm | BPL503_EstopRstReq_A | C_LOPRI | DLCLink | Class_Process | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL503
BR4_Tags | BPL503_EStopShutFlt_A | DLC Computer | Train E-Stop Shutdown Trip Alarm | BPL503_EStopShutFlt_A | CAT_P3 | BP1DLC1 | PRIV_ALARMACK | A_LD_TLO1 | Train E-Stop Shutdown Trip Alarm | BPL503_EStopShutFlt_A | C_LOPRI | DLCEStop | Class_Process | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL503
BR4_Tags | BPL503_GPSLss_A | DLC Computer | GPS Data Loss Alarm | BPL503_GPSLss_A | CAT_P3 | BP1DLC1 | PRIV_ALARMACK | A_LD_TLO1 | GPS Data Loss Alarm | BPL503_GPSLss_A | C_LOPRI | TrainComms | Class_Process | BR4_Cluster1 | BR4.OUTLOADING.BTL501.DLC01.TrainComms
BR4_Tags | BPL503_GrdTneLss_A | DLC Computer | Guard Tone Loss Trip Alarm | BPL503_GrdTneLss_A | CAT_P3 | BP1DLC1 | PRIV_ALARMACK | A_LD_TLO1 | Guard Tone Loss Trip Alarm | BPL503_GrdTneLss_A | C_LOPRI | TrainShutdowns | Class_Process | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL503
BR4_Tags | BPL503_MainPressLo_A | DLC Computer | Low Main Reservoir Pressure Alarm | BPL503_MainPressLo_A | CAT_P3 | BP1DLC1 | PRIV_ALARMACK | A_LD_TLO1 | Low Main Reservoir Pressure Alarm | BPL503_MainPressLo_A | C_LOPRI | TrainShutdowns | Class_Process | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL503
BR4_Tags | BPL503_ManVigLss_A | DLC Computer | Manual Mode Vigilance Loss Alarm | BPL503_ManVigLss_A | CAT_P3 | BP1DLC1 | PRIV_ALARMACK | A_LD_TLO1 | Manual Mode Vigilance Loss Alarm | BPL503_ManVigLss_A | C_LOPRI | DLCLinkMode | Class_Process | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL503
BR4_Tags | BPL503_NOE1LinkOK_A | Brockman 4 DLC | NOE Module Slot 1 Link Status Alarm | BPL503_NOE1LinkOK_A | CAT_P3 | BPL503 | PRIV_ALARMACK | A_LD_TLO1 | NOE Module Slot 1 Link Status Alarm | BPL503_NOE1LinkOK_A | C_LOPRI | BPL503 | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL503
BR4_Tags | BPL503_NOE1Rnng_A | Brockman 4 DLC | NOE Module Slot 1 Module Not Running Alarm | BPL503_NOE1Rnng_A | CAT_P3 | BPL503 | PRIV_ALARMACK | A_LD_TLO1 | NOE Module Slot 1 Module Not Running Alarm | BPL503_NOE1Rnng_A | C_LOPRI | BPL503 | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL503 | Slot1_A
BR4_Tags | BPL503_OSpd_A | DLC Computer | Overspeed Error Trip Alarm | BPL503_OSpd_A | CAT_P3 | BP1DLC1 | PRIV_ALARMACK | A_LD_TLO1 | Overspeed Error Trip Alarm | BPL503_OSpd_A | C_LOPRI | TrainComms | Class_Process | BR4_Cluster1 | BR4.OUTLOADING.BTL501.DLC01.TrainComms
BR4_Tags | BPL503_PLCForStdby_A | Brockman 4 DLC | PLC Forced to Standby Mode Warning Alarm | BPL503_PLCForStdby_A | CAT_P3 | BP1DLC1 | PRIV_ALARMACK | A_LD_TLO1 | PLC Forced to Standby Mode Warning Alarm | BPL503_PLCForStdby_A | C_LOPRI | DLCLink | Class_Process | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL503
BR4_Tags | BPL503_RadLnkLss_A | DLC Computer | Train Loco Radio Link Loss Alarm | BPL503_RadLnkLss_A | CAT_P3 | BP1DLC1 | PRIV_ALARMACK | A_LD_TLO1 | Train Loco Radio Link Loss Alarm | BPL503_RadLnkLss_A | C_LOPRI | TrainShutdowns | Class_Process | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL503
BR4_Tags | BPL503_TacLss_A | DLC Computer | Train Tachometer Loss Trip Alarm | BPL503_TacLss_A | CAT_P3 | BP1DLC1 | PRIV_ALARMACK | A_LD_TLO1 | Train Tachometer Loss Trip Alarm | BPL503_TacLss_A | C_LOPRI | TrainShutdowns | Class_Process | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL503
BR4_Tags | BPL503_TIMDLCComms_A | DLC Computer | TIM DLC Communications Trip Alarm | BPL503_TIMDLCComms_A | CAT_P3 | BP1DLC1 | PRIV_ALARMACK | A_LD_TLO1 | TIM DLC Communications Trip Alarm | BPL503_TIMDLCComms_A | C_LOPRI | TrainComms | Class_Process | BR4_Cluster1 | BR4.OUTLOADING.BTL501.DLC01.TrainComms
BR4_Tags | BPL503_TL2Flt_A | DLC Computer | Train Fault Detected T/L 2 Alarm | BPL503_TL2Flt_A | CAT_P3 | BP1DLC1 | PRIV_ALARMACK | A_LD_TLO1 | Train Fault Detected T/L 2 Alarm | BPL503_TL2Flt_A | C_LOPRI | TrainComms | Class_Process | BR4_Cluster1 | BR4.OUTLOADING.BTL501.DLC01.TrainComms
BR4_Tags | BPL503_TrnCtrl_A | DLC Computer | Trainline Control Error Trip Alarm | BPL503_TrnCtrl_A | CAT_P3 | BP1DLC1 | PRIV_ALARMACK | A_LD_TLO1 | Trainline Control Error Trip Alarm | BPL503_TrnCtrl_A | C_LOPRI | TrainComms | Class_Process | BR4_Cluster1 | BR4.OUTLOADING.BTL501.DLC01.TrainComms
BR4_Tags | BPL503_TrnForStdby_A | Brockman 4 DLC | Train Forced to Standby Mode Warning Alarm | BPL503_TrnForStdby_A | CAT_P3 | BP1DLC1 | PRIV_ALARMACK | A_LD_TLO1 | Train Forced to Standby Mode Warning Alarm | BPL503_TrnForStdby_A | C_LOPRI | DLCLink | Class_Process | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL503
BR4_Tags | BPL503H03_CntrlPwrOK_A | Brockman 4 DLC | Drop H Slot 03 Module Control Power Alarm | BPL503H03_CntrlPwrOK_A | CAT_P3 | BPL503 | PRIV_ALARMACK | A_LD_TLO1 | Drop H Slot 03 Module Control Power Alarm | BPL503H03_CntrlPwrOK_A | C_LOPRI | BPL503DropH | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL503.DropH
BR4_Tags | BPL503H03_OK_A | Brockman 4 DLC | Drop H Slot 03 Alarm | BPL503H03_OK_A | CAT_P3 | BPL503 | PRIV_ALARMACK | A_LD_TLO1 | Drop H Slot 03 Alarm | BPL503H03_OK_A | C_LOPRI | BPL503DropH | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL503.DropH | Slot3_A
BR4_Tags | BPL503H04_CntrlPwrOK_A | Brockman 4 DLC | Drop H Slot 04 Module Control Power Alarm | BPL503H04_CntrlPwrOK_A | CAT_P3 | BPL503 | PRIV_ALARMACK | A_LD_TLO1 | Drop H Slot 04 Module Control Power Alarm | BPL503H04_CntrlPwrOK_A | C_LOPRI | BPL503DropH | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL503.DropH
BR4_Tags | BPL503H04_OK_A | Brockman 4 DLC | Drop H Slot 04 Alarm | BPL503H04_OK_A | CAT_P3 | BPL503 | PRIV_ALARMACK | A_LD_TLO1 | Drop H Slot 04 Alarm | BPL503H04_OK_A | C_LOPRI | BPL503DropH | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL503.DropH | Slot4_A
BR4_Tags | BPL503H05_AICh1OK_A | Brockman 4 DLC | Slot 05 Channel 1 General Fault | BPL503H05_AICh1OK_A | CAT_P3 | BPL503 | PRIV_ALARMACK | A_LD_TLO1 | Slot 05 Channel 1 General Fault | BPL503H05_AICh1OK_A | C_LOPRI | BPL503DropH | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL503.DropH
BR4_Tags | BPL503H05_OK_A | Brockman 4 DLC | Drop H Slot 05 Alarm | BPL503H05_OK_A | CAT_P3 | BPL503 | PRIV_ALARMACK | A_LD_TLO1 | Drop H Slot 05 Alarm | BPL503H05_OK_A | C_LOPRI | BPL503DropH | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL503.DropH | Slot5_A
BR4_Tags | BTL501DLC01_ATPByp_A | Brockman 4 DLC | ATP Transponder Bypass Alarm | BTL501DLC01_ATPByp_A | CAT_P3 | BP1DLC1 | PRIV_ALARMACK | A_LD_TLO1 | ATP Transponder Bypass Alarm | BTL501DLC01_ATPByp_A | C_LOPRI | TrainShutdowns | Class_Process | BR4_Cluster1 | BR4.OUTLOADING.BTL501.DLC01
BR4_Tags | BTL501DLC01_AutoBell_A | Brockman 4 DLC | Automatic Mode Bell Warning Alarm | BTL501DLC01_AutoBell_A | CAT_P4 | BP1DLC1 | PRIV_ALARMACK | A_LD_TLO1 | Automatic Mode Bell Warning Alarm | BTL501DLC01_AutoBell_A | C_EVENT | DLCLinkMode | Class_Process | BR4_Cluster1 | BR4.OUTLOADING.BTL501.DLC01
BR4_Tags | BTL501DLC01_EBrk_A | Brockman 4 DLC | Emergency Brake Activated Alarm | BTL501DLC01_EBrk_A | CAT_P3 | BP1DLC1 | PRIV_ALARMACK | A_LD_TLO1 | Emergency Brake Activated Alarm | BTL501DLC01_EBrk_A | C_LOPRI | TrainBrakes | Class_Process | BR4_Cluster1 | BR4.OUTLOADING.BTL501.DLC01.TrainBrakes
BR4_Tags | BTL501DLC01_Estop_A | Brockman 4 DLC | Emergency Stop Activated Alarm | BTL501DLC01_Estop_A | CAT_P3 | BP1DLC1 | PRIV_ALARMACK | A_LD_TLO1 | Emergency Stop Activated Alarm | BTL501DLC01_Estop_A | C_LOPRI | DLCEStop | Class_Process | BR4_Cluster1 | BR4.OUTLOADING.BTL501.DLC01
BR4_Tags | BTL501DLC01_EStopShut_A | Brockman 4 DLC | Emergency Stop Shutdown Trip Alarm | BTL501DLC01_EStopShut_A | CAT_P3 | BP1DLC1 | PRIV_ALARMACK | A_LD_TLO1 | Emergency Stop Shutdown Trip Alarm | BTL501DLC01_EStopShut_A | C_LOPRI | DLCEStop | Class_Process | BR4_Cluster1 | BR4.OUTLOADING.BTL501.DLC01
BR4_Tags | BTL501DLC01_GrdTneFlt_A | Brockman 4 DLC | Guard Tone Snoop Radio Fault Alarm | BTL501DLC01_GrdTneFlt_A | CAT_P3 | BP1DLC1 | PRIV_ALARMACK | A_LD_TLO1 | Guard Tone Snoop Radio Fault Alarm | BTL501DLC01_GrdTneFlt_A | C_LOPRI | DLCEStop | Class_Process | BR4_Cluster1 | BR4.OUTLOADING.BTL501.DLC01
BR4_Tags | BTL501DLC01_IndBrkAuto_A | Brockman 4 DLC | Train Independent Brake Automatic Trip Alarm | BTL501DLC01_IndBrkAuto_A | CAT_P3 | BP1DLC1 | PRIV_ALARMACK | A_LD_TLO1 | Train Independent Brake Automatic Trip Alarm | BTL501DLC01_IndBrkAuto_A | C_LOPRI | TrainBrakes | Class_Process | BR4_Cluster1 | BR4.OUTLOADING.BTL501.DLC01.TrainBrakes
BR4_Tags | BTL501DLC01_IndBrkFlt_A | Brockman 4 DLC | Independent Brake Lift Trip Alarm | BTL501DLC01_IndBrkFlt_A | CAT_P3 | BP1DLC1 | PRIV_ALARMACK | A_LD_TLO1 | Independent Brake Lift Trip Alarm | BTL501DLC01_IndBrkFlt_A | C_LOPRI | TrainBrakes | Class_Process | BR4_Cluster1 | BR4.OUTLOADING.BTL501.DLC01.TrainBrakes
BR4_Tags | BTL501DLC01_IndBrkStdby_A | Brockman 4 DLC | Independent Brake Standby Trip Alarm | BTL501DLC01_IndBrkStdby_A | CAT_P3 | BP1DLC1 | PRIV_ALARMACK | A_LD_TLO1 | Independent Brake Standby Trip Alarm | BTL501DLC01_IndBrkStdby_A | C_LOPRI | TrainBrakes | Class_Process | BR4_Cluster1 | BR4.OUTLOADING.BTL501.DLC01.TrainBrakes
BR4_Tags | BTL501DLC01_LnkFlt_A | Brockman 4 DLC | Train Link Failure Alarm | BTL501DLC01_LnkFlt_A | CAT_P3 | BP1DLC1 | PRIV_ALARMACK | A_LD_TLO1 | Train Link Failure Alarm | BTL501DLC01_LnkFlt_A | C_LOPRI | DLCLink | Class_Process | BR4_Cluster1 | BR4.OUTLOADING.BTL501.DLC01
BR4_Tags | BTL501DLC01_ManBell_A | Brockman 4 DLC | Manual Mode Bell Warning Alarm | BTL501DLC01_ManBell_A | CAT_P3 | BP1DLC1 | PRIV_ALARMACK | A_LD_TLO1 | Manual Mode Bell Warning Alarm | BTL501DLC01_ManBell_A | C_LOPRI | DLCLinkMode | Class_Process | BR4_Cluster1 | BR4.OUTLOADING.BTL501.DLC01
BR4_Tags | BTL501DLC01_ManIndBrkAuto_A | Brockman 4 DLC | Independent Brake On, Manual to Automatic Al | BTL501DLC01_ManIndBrkAuto_A | CAT_P3 | BP1DLC1 | PRIV_ALARMACK | A_LD_TLO1 | Independent Brake On, Manual to Automatic Al | BTL501DLC01_ManIndBrkAuto_A | C_LOPRI | TrainBrakes | Class_Process | BR4_Cluster1 | BR4.OUTLOADING.BTL501.DLC01.TrainBrakes
BR4_Tags | BTL501DLC01_ManOSpd_A | Brockman 4 DLC | Manual Mode Overspeed Trip Alarm | BTL501DLC01_ManOSpd_A | CAT_P3 | BP1DLC1 | PRIV_ALARMACK | A_LD_TLO1 | Manual Mode Overspeed Trip Alarm | BTL501DLC01_ManOSpd_A | C_LOPRI | DLCLinkMode | Class_Process | BR4_Cluster1 | BR4.OUTLOADING.BTL501.DLC01
BR4_Tags | BTL501DLC01_TrnIT01_A | Brockman 4 DLC | Train Traction Current Low Alarm | BTL501DLC01_TrnIT01_A | CAT_P3 | BP1DLC1 | PRIV_ALARMACK | A_LD_TLO1 | Train Traction Current Low Alarm | BTL501DLC01_TrnIT01_A | C_LOPRI | TrainGeneral | Class_Process | BR4_Cluster1 | BR4.OUTLOADING.BTL501.DLC01
BR4_Tags | BTL501DLC01_TrnLnk_E | Brockman 4 DLC | Train Linked Event Alarm | BTL501DLC01_TrnLnk_E | CAT_P4 | BP1DLC1 | PRIV_ALARMACK | A_LD_TLO1 | Train Linked Event Alarm | BTL501DLC01_TrnLnk_E | C_EVENT | DLCLink | Class_Process | BR4_Cluster1 | BR4.OUTLOADING.BTL501.DLC01
BR4_Tags | BTL501DLC01_TrnSpdFlt_A | Brockman 4 DLC | Train Speed Differential Trip Alarm | BTL501DLC01_TrnSpdFlt_A | CAT_P3 | BP1DLC1 | PRIV_ALARMACK | A_LD_TLO1 | Train Speed Differential Trip Alarm | BTL501DLC01_TrnSpdFlt_A | C_LOPRI | TrainGeneral | Class_Process | BR4_Cluster1 | BR4.OUTLOADING.BTL501.DLC01
BR4_Tags | BTL501DLC01_TrnSpdOR_E | Brockman 4 DLC | Train Speed Override | BTL501DLC01_TrnSpdOR_E | CAT_P4 | BP1DLC1 | PRIV_ALARMACK | A_LD_TLO1 | Train Speed Override | BTL501DLC01_TrnSpdOR_E | C_EVENT | TrainGeneral | Class_Process | BR4_Cluster1 | BR4.OUTLOADING.BTL501.DLC01
BR4_Tags | BTL501DLC01_TrnSpdZero_E | Brockman 4 DLC | Train Speed Setpoint Set To Zero | BTL501DLC01_TrnSpdZero_E | CAT_P4 | BP1DLC1 | PRIV_ALARMACK | A_LD_TLO1 | Train Speed Setpoint Set To Zero | BTL501DLC01_TrnSpdZero_E | C_EVENT | TrainGeneral | Class_Process | BR4_Cluster1 | BR4.OUTLOADING.BTL501.DLC01
BR4_Tags | BTL501DLC01DCOK05_A | Brockman 4 DLC | Guard Tone 12VDC Supply Trip Alarm | BTL501DLC01DCOK05_A | CAT_P3 | BP1DLC1 | PRIV_ALARMACK | A_LD_TLO1 | Guard Tone 12VDC Supply Trip Alarm | BTL501DLC01DCOK05_A | C_LOPRI | BPL503Power | Class_Process | BR4_Cluster1 | BR4.OUTLOADING.BTL501.DLC01
BR4_Tags | BTL501DLC01DCOK03_A | Brockman 4 DLC | Computer 48VDC Supply Trip Alarm | BTL501DLC01DCOK03_A | CAT_P3 | BP1DLC1 | PRIV_ALARMACK | A_LD_TLO1 | Computer 48VDC Supply Trip Alarm | BTL501DLC01DCOK03_A | C_LOPRI | BPL503Power | Class_Process | BR4_Cluster1 | BR4.OUTLOADING.BTL501.DLC01
BR4_Tags | BTL501DLC01DCOK01_A | Brockman 4 DLC | Safety Circuit 24VDC Supply Trip Alarm | BTL501DLC01DCOK01_A | CAT_P3 | BP1DLC1 | PRIV_ALARMACK | A_LD_TLO1 | Safety Circuit 24VDC Supply Trip Alarm | BTL501DLC01DCOK01_A | C_LOPRI | BPL503Power | Class_Process | BR4_Cluster1 | BR4.OUTLOADING.BTL501.DLC01
BR4_Tags | BTL501DLC01ESI_A | Brockman 4 DLC | PLC Emergency Shutdown Circuit Fault | BTL501DLC01ESI_A | CAT_P3 | BP1DLC1 | PRIV_ALARMACK | A_LD_TLO1 | PLC Emergency Shutdown Circuit Fault | BTL501DLC01ESI_A | C_LOPRI | DLCEStop | Class_Process | BR4_Cluster1 | BR4.OUTLOADING.BTL501.DLC01
BR4_Tags | BTL501DLC01JS02_BW_A | Brockman 4 DLC | Train Loadout Control Room Joystick Broken W | BTL501DLC01JS02_BW_A | CAT_P3 | BP1DLC1 | PRIV_ALARMACK | A_LD_TLO1 | Train Loadout Control Room Joystick Broken W | BTL501DLC01JS02_BW_A | C_LOPRI | DLCJoystick | Class_Process | BR4_Cluster1 | BR4.OUTLOADING.BTL501.DLC01
BR4_Tags | BTL501DLC01JS0x_IndBrk_A | Brockman 4 DLC | Controlling Joystick Manual Attendance Indep | BTL501DLC01JS0x_IndBrk_A | CAT_P3 | BP1DLC1 | PRIV_ALARMACK | A_LD_TLO1 | Controlling Joystick Manual Attendance Indep | BTL501DLC01JS0x_IndBrk_A | C_LOPRI | DLCJoystick | Class_Process | BR4_Cluster1 | BR4.OUTLOADING.BTL501.DLC01
BR4_Tags | BTL501DLC01JS0x_Neut_A | Brockman 4 DLC | Controlling Joystick In Neutral Position Ala | BTL501DLC01JS0x_Neut_A | CAT_P3 | BP1DLC1 | PRIV_ALARMACK | A_LD_TLO1 | Controlling Joystick In Neutral Position Ala | BTL501DLC01JS0x_Neut_A | C_LOPRI | DLCJoystick | Class_Process | BR4_Cluster1 | BR4.OUTLOADING.BTL501.DLC01
BR4_Tags | BTL501DLC01JS0x_NeutFlt_A | Brockman 4 DLC | Controlling Joystick Manual Selected With Jo | BTL501DLC01JS0x_NeutFlt_A | CAT_P3 | BP1DLC1 | PRIV_ALARMACK | A_LD_TLO1 | Controlling Joystick Manual Selected With Jo | BTL501DLC01JS0x_NeutFlt_A | C_LOPRI | DLCJoystick | Class_Process | BR4_Cluster1 | BR4.OUTLOADING.BTL501.DLC01
BR4_Tags | BTL501DLC01JS0x_Pos_A | Brockman 4 DLC | Controlling Joystick Analog/Digital Discrepa | BTL501DLC01JS0x_Pos_A | CAT_P3 | BP1DLC1 | PRIV_ALARMACK | A_LD_TLO1 | Controlling Joystick Analog/Digital Discrepa | BTL501DLC01JS0x_Pos_A | C_LOPRI | DLCJoystick | Class_Process | BR4_Cluster1 | BR4.OUTLOADING.BTL501.DLC01
BR4_Tags | BTL501DLC01JS0xC_Pwr_A | Brockman 4 DLC | Controlling Joystick Manual Attendance Power | BTL501DLC01JS0xC_Pwr_A | CAT_P3 | BP1DLC1 | PRIV_ALARMACK | A_LD_TLO1 | Controlling Joystick Manual Attendance Power | BTL501DLC01JS0xC_Pwr_A | C_LOPRI | DLCJoystick | Class_Process | BR4_Cluster1 | BR4.OUTLOADING.BTL501.DLC01
BR4_Tags | BTL501DLC01JS0xC_Req_A | Brockman 4 DLC | Controlling Joystick Manual Attendance Requi | BTL501DLC01JS0xC_Req_A | CAT_P3 | BP1DLC1 | PRIV_ALARMACK | A_LD_TLO1 | Controlling Joystick Manual Attendance Requi | BTL501DLC01JS0xC_Req_A | C_LOPRI | DLCJoystick | Class_Process | BR4_Cluster1 | BR4.OUTLOADING.BTL501.DLC01
BR4_Tags | BTL501DLC01ES01_A | Brockman 4 DLC | Train Loadout-Control Room E Stop Activated | BTL501DLC01ES01_A | CAT_P3 | BP1DLC1 | PRIV_ALARMACK | A_LD_TLO1 | Train Loadout-Control Room E Stop Activated | BTL501DLC01ES01_A | C_LOPRI | DLCEStop | Class_Process | BR4_Cluster1 | BR4.OUTLOADING.BTL501.DLC01
BR4_Tags | BTL501DLC01DCOK02_A | Brockman 4 DLC | PLC 24VDC Supply Trip Alarm | BTL501DLC01DCOK02_A | CAT_P3 | BP1DLC1 | PRIV_ALARMACK | A_LD_TLO1 | PLC 24VDC Supply Trip Alarm | BTL501DLC01DCOK02_A | C_LOPRI | BPL503Power | Class_Process | BR4_Cluster1 | BR4.OUTLOADING.BTL501.DLC01
BR4_Tags | BTL501DLC01DCOK04_A | Brockman 4 DLC | Snoop & Data Radios 12VDC Supply Trip Alarm | BTL501DLC01DCOK04_A | CAT_P3 | BP1DLC1 | PRIV_ALARMACK | A_LD_TLO1 | Snoop & Data Radios 12VDC Supply Trip Alarm | BTL501DLC01DCOK04_A | C_LOPRI | BPL503Power | Class_Process | BR4_Cluster1 | BR4.OUTLOADING.BTL501.DLC01
BR4_Tags | BTL501DLC01SES1A_A | Brockman 4 DLC | Safety PLC Applied E-Stop Alarm | BTL501DLC01SES1A_A | CAT_P3 | BP1DLC1 | PRIV_ALARMACK | A_LD_TLO1 | Safety PLC Applied E-Stop Alarm | BTL501DLC01SES1A_A | C_LOPRI | DLCEStop | Class_Process | BR4_Cluster1 | BR4.OUTLOADING.BTL501.DLC01
BR4_Tags | BTL501DLC01_TrnMv_E | Brockman 4 DLC | Train Moving Event | BTL501DLC01_TrnMv_E | CAT_P4 | BP1DLC1 | PRIV_ALARMACK | A_LD_TLO1 | Train Moving Event | BTL501DLC01_TrnMv_E | C_EVENT | TrainGeneral | Class_Process | BR4_Cluster1 | BR4.OUTLOADING.BTL501.DLC01
BR4_Tags | BTL501DLC01JS0x_BW_A | Brockman 4 DLC | Remote Joystick Broken Wire Alarm | BTL501DLC01JS0x_BW_A | CAT_P3 | BP1DLC1 | PRIV_ALARMACK | A_LD_TLO1 | Remote Joystick Broken Wire Alarm | BTL501DLC01JS0x_BW_A | C_LOPRI | DLCJoystick | Class_Process | BR4_Cluster1 | BR4.OUTLOADING.BTL501.DLC01
BR4_Tags | BPL503_D0R0S4OK_A | Brockman 4 DLC | BPL503 Rack 00 Slot 04 Hardware Fault Alarm | BPL503_D0R0S4OK_A | CAT_P3 | BPL503 | PRIV_ALARMACK | A_LD_TLO1 | BPL503 Rack 00 Slot 04 Hardware Fault Alarm | BPL503_D0R0S4OK_A | C_LOPRI | BPL503 | Class_Process | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL503
BR4_Tags | BPL803HC01A_BW_A | Brockman 4 DLC | Admin Joystick Broken Wire Alarm | BPL803HC01A_BW_A | CAT_P3 | BP1DLC1 | PRIV_ALARMACK | A_LD_TLO1 | Admin Joystick Broken Wire Alarm | BPL803HC01A_BW_A | C_LOPRI | DLCJoystick | Class_Process | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL803
BR4_Tags | BPL802HC01A_BW_A | Brockman 4 DLC | OC Joystick Broken Wire Alarm | BPL802HC01A_BW_A | CAT_P3 | BP1DLC1 | PRIV_ALARMACK | A_LD_TLO1 | OC Joystick Broken Wire Alarm | BPL802HC01A_BW_A | C_LOPRI | DLCJoystick | Class_Process | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL802
BR4_Tags | BPL503_LocoRolling_A | DLC Computer | DLC Local Rolling Alarm | BPL503_LocoRolling_A | CAT_P3 | BP1DLC1 | PRIV_ALARMACK | A_LD_TLO1 | DLC Local Rolling Alarm | BPL503_LocoRolling_A | C_LOPRI | TrainGeneral | Class_Process | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL503
BR4_Tags | BPL503H05_AICh1OCE_E | Brockman 4 DLC | DLC TLO CR Joystick Over Current Error | BPL503H05_AICh1OCE_E | CAT_P4 | BP1DLC1 | PRIV_ALARMACK | A_LD_TLO1 | DLC TLO CR Joystick Over Current Error | BPL503H05_AICh1OCE_E | C_EVENT | DLCJoystick | Class_Process | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL503.DropH
BR4_Tags | BPL503H05_AICh1UCE_E | Brockman 4 DLC | DLC TLO CR Joystick Under Current Error | BPL503H05_AICh1UCE_E | CAT_P4 | BP1DLC1 | PRIV_ALARMACK | A_LD_TLO1 | DLC TLO CR Joystick Under Current Error | BPL503H05_AICh1UCE_E | C_EVENT | DLCJoystick | Class_Process | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL503.DropH
BR4_Tags | BPL503_SpareStat44_A | DLC Computer | DLC Spare Stat 44 | BPL503_SpareStat44_A | CAT_P3 | BPL503 | PRIV_ALARMACK | A_LD_TLO1 | DLC Spare Stat 44 | BPL503_SpareStat44_A | C_LOPRI | BPL503 | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL503
BR4_Tags | BPL503_SpareStat68_A | DLC Computer | DLC Spare Stat 68 | BPL503_SpareStat68_A | CAT_P3 | BPL503 | PRIV_ALARMACK | A_LD_TLO1 | DLC Spare Stat 68 | BPL503_SpareStat68_A | C_LOPRI | BPL503 | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL503
BR4_Tags | BPL503_SpareStat70_A | DLC Computer | DLC Spare Stat 70 | BPL503_SpareStat70_A | CAT_P3 | BPL503 | PRIV_ALARMACK | A_LD_TLO1 | DLC Spare Stat 70 | BPL503_SpareStat70_A | C_LOPRI | BPL503 | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL503
BR4_Tags | BPL503_SpareStat71_A | DLC Computer | DLC Spare Stat 71 | BPL503_SpareStat71_A | CAT_P3 | BPL503 | PRIV_ALARMACK | A_LD_TLO1 | DLC Spare Stat 71 | BPL503_SpareStat71_A | C_LOPRI | BPL503 | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL503
BR4_Tags | BPL503_SpareStat72_A | DLC Computer | DLC Spare Stat 72 | BPL503_SpareStat72_A | CAT_P3 | BPL503 | PRIV_ALARMACK | A_LD_TLO1 | DLC Spare Stat 72 | BPL503_SpareStat72_A | C_LOPRI | BPL503 | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL503
BR4_Tags | BPL503_SpareStat73_A | DLC Computer | DLC Spare Stat 73 | BPL503_SpareStat73_A | CAT_P3 | BPL503 | PRIV_ALARMACK | A_LD_TLO1 | DLC Spare Stat 73 | BPL503_SpareStat73_A | C_LOPRI | BPL503 | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL503
BR4_Tags | BPL503_SpareStat74_A | DLC Computer | DLC Spare Stat 74 | BPL503_SpareStat74_A | CAT_P3 | BPL503 | PRIV_ALARMACK | A_LD_TLO1 | DLC Spare Stat 74 | BPL503_SpareStat74_A | C_LOPRI | BPL503 | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL503
BR4_Tags | BPL503_SpareStat75_A | DLC Computer | DLC Spare Stat 75 | BPL503_SpareStat75_A | CAT_P3 | BPL503 | PRIV_ALARMACK | A_LD_TLO1 | DLC Spare Stat 75 | BPL503_SpareStat75_A | C_LOPRI | BPL503 | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL503
BR4_Tags | BPL503_SpareStat89_A | DLC Computer | DLC Spare Stat 89 | BPL503_SpareStat89_A | CAT_P3 | BPL503 | PRIV_ALARMACK | A_LD_TLO1 | DLC Spare Stat 89 | BPL503_SpareStat89_A | C_LOPRI | BPL503 | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL503
BR4_Tags | BPL503_SpareStat90_A | DLC Computer | DLC Spare Stat 90 | BPL503_SpareStat90_A | CAT_P3 | BPL503 | PRIV_ALARMACK | A_LD_TLO1 | DLC Spare Stat 90 | BPL503_SpareStat90_A | C_LOPRI | BPL503 | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL503
BR4_Tags | BPL503_SpareStat91_A | DLC Computer | DLC Spare Stat 91 | BPL503_SpareStat91_A | CAT_P3 | BPL503 | PRIV_ALARMACK | A_LD_TLO1 | DLC Spare Stat 91 | BPL503_SpareStat91_A | C_LOPRI | BPL503 | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL503
BR4_Tags | BTI501CT01_Fault_A | Speed Camera | Speed Camera No.1 Fault | BTI501CT01_Fault_A | CAT_P2 | BP1DLC1 | PRIV_ALARMACK | A_LD_TLO1 | Speed Camera No.1 Fault | BTI501CT01_Fault_A | C_HIPRI | TrainGeneral | Class_Process | BR4_Cluster1 | BR4.OUTLOADING.BTL501
BR4_Tags | BTI501CT02_Fault_A | Speed Camera | Speed Camera No.2 Fault | BTI501CT02_Fault_A | CAT_P2 | BP1DLC1 | PRIV_ALARMACK | A_LD_TLO1 | Speed Camera No.2 Fault | BTI501CT02_Fault_A | C_HIPRI | TrainGeneral | Class_Process | BR4_Cluster1 | BR4.OUTLOADING.BTL501
BR4_Tags | BTL501DLC01_EntryFlt_A | Brockman 4 DLC | Entry Fault as Train Approaching Loadout | BTL501DLC01_EntryFlt_A | CAT_P2 | BP1DLC1 | PRIV_ALARMACK | A_LD_TLO1 | Entry fault as train approaching loadout | BTL501DLC01_EntryFlt_A | C_HIPRI | BPL503 | Class_Process | BR4_Cluster1 | BR4.OUTLOADING.BTL501.DLC01
BR4_Tags | BTL501CH01FLT_ChPrtFlt_A | Brockman 4 DLC | TLO Chute Protection Fault | BTL501CH01FLT_ChPrtFlt_A | CAT_P2 | BP1DLC1 | PRIV_ALARMACK | A_LD_TLO1 | Chute not raised when train linkd and inTLO area | BTL501CH01FLT_ChPrtFlt_A | C_HIPRI | BPL503 | Class_Process | BR4_Cluster1 | BR4.OUTLOADING.BTL501.CH01
BR4_Tags | BTL501DLC01_DLCLocnErr_A | Brockman 4 DLC | DLC Reporting Wrong Location | BTL501DLC01_DLCLocnErr_A | CAT_P3 | BP1DLC1 | PRIV_ALARMACK | A_LD_TLO1 | DLC reported wrong location at TagReader PE1&2 | BTL501DLC01_DLCLocnErr_A | C_LOPRI | BPL503 | Class_Process | BR4_Cluster1 | BR4.OUTLOADING.BTL501.DLC01
BR4_Tags | BTL501DLC01_DLCLocnErrTrp_A | Brockman 4 DLC | DLC Loco Location Incorrect-Park With Caution | BTL501DLC01_DLCLocnErrTrp_A | CAT_P2 | BP1DLC1 | PRIV_ALARMACK | A_LD_TLO1 | DLC Loco location Incorrect at Link or 230Wgn Ld | BTL501DLC01_DLCLocnErrTrp_A | C_HIPRI | BPL503 | Class_Process | BR4_Cluster1 | BR4.OUTLOADING.BTL501.DLC01
BR4_Tags | BTL501DLC01_RevMvmtIL_A | Brockman 4 DLC | DLC Reverse Movement Command Not Allowed | BTL501DLC01_RevMvmtIL_A | CAT_P3 | BP1DLC1 | PRIV_ALARMACK | A_LD_TLO1 | Reverse movement disabled before reaching TLO | BTL501DLC01_RevMvmtIL_A | C_LOPRI | MANREVMODEIL | Class_Process | BR4_Cluster1 | BR4.OUTLOADING.BTL501.DLC01
BR4_Tags | BTL501DLC01_RPI_IL_A | Brockman 4 DLC | DLC Reverse Protection Interlock Active | BTL501DLC01_RPI_IL_A | CAT_P3 | BP1DLC1 | PRIV_ALARMACK | A_LD_TLO1 | Reverse movement disabled before reaching TLO | BTL501DLC01_RPI_IL_A | C_LOPRI | PLCFORSTDBY | Class_Process | BR4_Cluster1 | BR4.OUTLOADING.BTL501.DLC01
BR4_Tags | BTL501DLC01_FwdMvmtIL_A | Brockman 4 DLC | DLC Forward Movement Command Not Allowed | BTL501DLC01_FwdMvmtIL_A | CAT_P3 | BP1DLC1 | PRIV_ALARMACK | A_LD_TLO1 | Check site LCL occupancy and bin pre-fill level | BTL501DLC01_FwdMvmtIL_A | C_LOPRI | FWDMVMTIL | Class_Process | BR4_Cluster1 | BR4.OUTLOADING.BTL501.DLC01
BR4_Tags | BTL501DLC01_PFP_IL_A | Brockman 4 DLC | DLC Bin Pre-Fill Protection Interlock Active | BTL501DLC01_PFP_IL_A | CAT_P3 | BP1DLC1 | PRIV_ALARMACK | A_LD_TLO1 | Check site bin pre-fill level | BTL501DLC01_PFP_IL_A | C_LOPRI | PLCFORSTDBY | Class_Process | BR4_Cluster1 | BR4.OUTLOADING.BTL501.DLC01
BR4_Tags | BTL501DLC01_PFP_BinWgtFrz_A | Brockman 4 DLC | TLO Bin Weight Signal Frozen | BTL501DLC01_PFP_BinWgtFrz_A | CAT_P3 | BP1DLC1 | PRIV_ALARMACK | A_LD_TLO1 | Check Bin Weight status | BTL501DLC01_PFP_BinWgtFrz_A | C_LOPRI | BPL503 | Class_Process | BR4_Cluster1 | BR4.OUTLOADING.BTL501.DLC01
BR4_Tags | BPL832_CPUEthModLinkOK_A | Vehicle Workshop PLC | CPU Module Ethernet Link Fault | BPL832_CPUEthModLinkOK_A | CAT_P2 | BPL832 | PRIV_ALARMACK | A_P1_FUEL | CPU Module Ethernet Link Fault | BPL832_CPUEthModLinkOK_A | C_HIPRI | BPL832 | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL832
BR4_Tags | BPL832_CPUEthModRnng_A | Vehicle Workshop PLC | CPU Module Ethernet Port Not Running Fault | BPL832_CPUEthModRnng_A | CAT_P2 | BPL832 | PRIV_ALARMACK | A_P1_FUEL | CPU Module Ethernet Port Not Running Fault | BPL832_CPUEthModRnng_A | C_HIPRI | BPL832 | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL832
BR4_Tags | BPL832_NOE5LinkOK_A | Vehicle Workshop PLC | NOE1 Ethernet Link Status Fault | BPL832_NOE5LinkOK_A | CAT_P3 | BPL832 | PRIV_ALARMACK | A_P1_FUEL | NOE Module Slot 5 Link Status | BPL832_NOE5LinkOK_A | C_LOPRI | BPL832 | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL832
BR4_Tags | BPL832_NOE5Rnng_A | Vehicle Workshop PLC | NOE1 Ethernet Module Not Running | BPL832_NOE5Rnng_A | CAT_P3 | BPL832 | PRIV_ALARMACK | A_P1_FUEL | NOE Module Slot 5 Not Running | BPL832_NOE5Rnng_A | C_LOPRI | BPL832 | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL832 | Slot5_A
BR4_Tags | BPL832_R0S1OK_A | Vehicle Workshop PLC | Rack 0 Slot 1 Module Fault | BPL832_R0S1OK_A | CAT_P3 | BPL832 | PRIV_ALARMACK | A_P1_FUEL | Rack 0 Slot 1 Module Fault | BPL832_R0S1OK_A | C_LOPRI | BPL832 | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL832 | Slot1_A
BR4_Tags | BPL832_R0S2OK_A | Vehicle Workshop PLC | Rack 0 Slot 2 Module Fault | BPL832_R0S2OK_A | CAT_P3 | BPL832 | PRIV_ALARMACK | A_P1_FUEL | Rack 0 Slot 2 Module Fault | BPL832_R0S2OK_A | C_LOPRI | BPL832 | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL832 | Slot2_A
BR4_Tags | BPL832_R0S3OK_A | Vehicle Workshop PLC | Rack 0 Slot 3 Module Fault | BPL832_R0S3OK_A | CAT_P3 | BPL832 | PRIV_ALARMACK | A_P1_FUEL | Rack 0 Slot 3 Module Fault | BPL832_R0S3OK_A | C_LOPRI | BPL832 | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL832 | Slot3_A
BR4_Tags | BPL832_R0S6OK_A | Vehicle Workshop PLC | Rack 0 Slot 6 Module Fault | BPL832_R0S6OK_A | CAT_P3 | BPL832 | PRIV_ALARMACK | A_P1_FUEL | Rack 0 Slot 6 Module Fault | BPL832_R0S6OK_A | C_LOPRI | BPL832 | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL832 | Slot6_A
BR4_Tags | BPL832_R0S7OK_A | Vehicle Workshop PLC | Rack 0 Slot 7 Module Fault | BPL832_R0S7OK_A | CAT_P3 | BPL832 | PRIV_ALARMACK | A_P1_FUEL | Rack 0 Slot 7 Module Fault | BPL832_R0S7OK_A | C_LOPRI | BPL832 | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL832 | Slot7_A
BR4_Tags | BPL832_R0S10OK_A | Vehicle Workshop PLC | Rack 0 Slot 10 Module Fault | BPL832_R0S10OK_A | CAT_P3 | BPL832 | PRIV_ALARMACK | A_P1_FUEL | Rack 0 Slot 10 Module Fault | BPL832_R0S10OK_A | C_LOPRI | BPL832 | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL832 | Slot10_A
BR4_Tags | BPL832_R0S11OK_A | Vehicle Workshop PLC | Rack 0 Slot 11 Module Fault | BPL832_R0S11OK_A | CAT_P3 | BPL832 | PRIV_ALARMACK | A_P1_FUEL | Rack 0 Slot 11 Module Fault | BPL832_R0S11OK_A | C_LOPRI | BPL832 | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL832 | Slot11_A
BR4_Tags | BPL832_BPL801CommsOK_A | Vehicle Workshop PLC | InterPLC BPL801 Communications Faulted | BPL832_BPL801CommsOK_A | CAT_P3 | BPL832 | PRIV_ALARMACK | A_P1_FUEL | HV WrkShp 832 to Admin 801 PLC Comms | BPL832_BPL801CommsOK_A | C_LOPRI | BPL832 | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL832
BR4_Tags | BPL832_DropBOK_A | PLC 832 Drop B - B0832LTPN01 | Drop B Island NIP Module or Island Bus Fault | BPL832_DropBOK_A | CAT_P3 | BPL832 | PRIV_ALARMACK | A_P1_FUEL | NIP or Island Bus Fault | BPL832_DropBOK_A | C_LOPRI | BPL832DropB | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL832
BR4_Tags | BPL832_DropCOK_A | PLC 832 Drop C - B0832HVPN01 | Drop C Island NIP Module or Island Bus Fault | BPL832_DropCOK_A | CAT_P3 | BPL832 | PRIV_ALARMACK | A_P1_FUEL | NIP or Island Bus Fault | BPL832_DropCOK_A | C_LOPRI | BPL832DropC | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL832
BR4_Tags | BPL832_DropDOK_A | PLC 832 Drop D - B0832HVPN02 | Drop D Island NIP Module or Island Bus Fault | BPL832_DropDOK_A | CAT_P3 | BPL832 | PRIV_ALARMACK | A_P1_FUEL | NIP or Island Bus Fault | BPL832_DropDOK_A | C_LOPRI | BPL832DropD | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL832
BR4_Tags | BPL832_DropEOK_A | PLC 832 Drop E - B0832HVPN03 | Drop E Island NIP Module or Island Bus Fault | BPL832_DropEOK_A | CAT_P3 | BPL832 | PRIV_ALARMACK | A_P1_FUEL | NIP or Island Bus Fault | BPL832_DropEOK_A | C_LOPRI | BPL832DropE | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL832
BR4_Tags | BPL832_DropFOK_A | PLC 832 Drop F - B0832LVPN01 | Drop F Island NIP Module or Island Bus Fault | BPL832_DropFOK_A | CAT_P3 | BPL832 | PRIV_ALARMACK | A_P1_FUEL | NIP or Island Bus Fault | BPL832_DropFOK_A | C_LOPRI | BPL832DropF | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL832
BR4_Tags | BPL832_DropGOK_A | PLC 832 Drop G - B0832LVPN02 | Drop G Island NIP Module or Island Bus Fault | BPL832_DropGOK_A | CAT_P3 | BPL832 | PRIV_ALARMACK | A_P1_FUEL | NIP or Island Bus Fault | BPL832_DropGOK_A | C_LOPRI | BPL832DropG | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL832
BR4_Tags | BPL832B03_CntrlPwrOK_A | PLC 832 Drop B - B0832LTPN01 | Slot 03 Module Control Power Fault | BPL832B03_CntrlPwrOK_A | CAT_P3 | BPL832 | PRIV_ALARMACK | A_P1_FUEL | Slot 03 Module Control Power Fault | BPL832B03_CntrlPwrOK_A | C_LOPRI | BPL832DropB | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL832.DropB
BR4_Tags | BPL832B03_OK_A | PLC 832 Drop B - B0832LTPN01 | Slot 03 Module Fault | BPL832B03_OK_A | CAT_P3 | BPL832 | PRIV_ALARMACK | A_P1_FUEL | Slot 03 Module Fault | BPL832B03_OK_A | C_LOPRI | BPL832DropB | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL832.DropB | Slot3_A
BR4_Tags | BPL832B04_CntrlPwrOK_A | PLC 832 Drop B - B0832LTPN01 | Slot 04 Module Control Power Fault | BPL832B04_CntrlPwrOK_A | CAT_P3 | BPL832 | PRIV_ALARMACK | A_P1_FUEL | Slot 04 Module Control Power Fault | BPL832B04_CntrlPwrOK_A | C_LOPRI | BPL832DropB | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL832.DropB
BR4_Tags | BPL832B04_OK_A | PLC 832 Drop B - B0832LTPN01 | Slot 04 Module Fault | BPL832B04_OK_A | CAT_P3 | BPL832 | PRIV_ALARMACK | A_P1_FUEL | Slot 04 Module Fault | BPL832B04_OK_A | C_LOPRI | BPL832DropB | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL832.DropB | Slot4_A
BR4_Tags | BPL832B05_CntrlPwrOK_A | PLC 832 Drop B - B0832LTPN01 | Slot 05 Module Control Power Fault | BPL832B05_CntrlPwrOK_A | CAT_P3 | BPL832 | PRIV_ALARMACK | A_P1_FUEL | Slot 05 Module Control Power Fault | BPL832B05_CntrlPwrOK_A | C_LOPRI | BPL832DropB | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL832.DropB
BR4_Tags | BPL832B05_OK_A | PLC 832 Drop B - B0832LTPN01 | Slot 05 Module Fault | BPL832B05_OK_A | CAT_P3 | BPL832 | PRIV_ALARMACK | A_P1_FUEL | Slot 05 Module Fault | BPL832B05_OK_A | C_LOPRI | BPL832DropB | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL832.DropB | Slot5_A
BR4_Tags | BPL832B06_CntrlPwrOK_A | PLC 832 Drop B - B0832LTPN01 | Slot 06 Module Control Power Fault | BPL832B06_CntrlPwrOK_A | CAT_P3 | BPL832 | PRIV_ALARMACK | A_P1_FUEL | Slot 06 Module Control Power Fault | BPL832B06_CntrlPwrOK_A | C_LOPRI | BPL832DropB | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL832.DropB
BR4_Tags | BPL832B06_OK_A | PLC 832 Drop B - B0832LTPN01 | Slot 06 Module Fault | BPL832B06_OK_A | CAT_P3 | BPL832 | PRIV_ALARMACK | A_P1_FUEL | Slot 06 Module Fault | BPL832B06_OK_A | C_LOPRI | BPL832DropB | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL832.DropB | Slot6_A
BR4_Tags | BPL832B07_CntrlPwrOK_A | PLC 832 Drop B - B0832LTPN01 | Slot 07 Module Control Power Fault | BPL832B07_CntrlPwrOK_A | CAT_P3 | BPL832 | PRIV_ALARMACK | A_P1_FUEL | Slot 07 Module Control Power Fault | BPL832B07_CntrlPwrOK_A | C_LOPRI | BPL832DropB | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL832.DropB
BR4_Tags | BPL832B07_OK_A | PLC 832 Drop B - B0832LTPN01 | Slot 07 Module Fault | BPL832B07_OK_A | CAT_P3 | BPL832 | PRIV_ALARMACK | A_P1_FUEL | Slot 07 Module Fault | BPL832B07_OK_A | C_LOPRI | BPL832DropB | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL832.DropB | Slot7_A
BR4_Tags | BPL832B08_CntrlPwrOK_A | PLC 832 Drop B - B0832LTPN01 | Slot 08 Module Control Power Fault | BPL832B08_CntrlPwrOK_A | CAT_P3 | BPL832 | PRIV_ALARMACK | A_P1_FUEL | Slot 08 Module Control Power Fault | BPL832B08_CntrlPwrOK_A | C_LOPRI | BPL832DropB | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL832.DropB
BR4_Tags | BPL832B08_OK_A | PLC 832 Drop B - B0832LTPN01 | Slot 08 Module Fault | BPL832B08_OK_A | CAT_P3 | BPL832 | PRIV_ALARMACK | A_P1_FUEL | Slot 08 Module Fault | BPL832B08_OK_A | C_LOPRI | BPL832DropB | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL832.DropB | Slot8_A
BR4_Tags | BPL832B09_CntrlPwrOK_A | PLC 832 Drop B - B0832LTPN01 | Slot 09 Module Control Power Fault | BPL832B09_CntrlPwrOK_A | CAT_P3 | BPL832 | PRIV_ALARMACK | A_P1_FUEL | Slot 09 Module Control Power Fault | BPL832B09_CntrlPwrOK_A | C_LOPRI | BPL832DropB | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL832.DropB
BR4_Tags | BPL832B09_OK_A | PLC 832 Drop B - B0832LTPN01 | Slot 09 Module Fault | BPL832B09_OK_A | CAT_P3 | BPL832 | PRIV_ALARMACK | A_P1_FUEL | Slot 09 Module Fault | BPL832B09_OK_A | C_LOPRI | BPL832DropB | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL832.DropB | Slot9_A
BR4_Tags | BPL832B10_CntrlPwrOK_A | PLC 832 Drop B - B0832LTPN01 | Slot 10 Module Control Power Fault | BPL832B10_CntrlPwrOK_A | CAT_P3 | BPL832 | PRIV_ALARMACK | A_P1_FUEL | Slot 10 Module Control Power Fault | BPL832B10_CntrlPwrOK_A | C_LOPRI | BPL832DropB | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL832.DropB
BR4_Tags | BPL832B10_OK_A | PLC 832 Drop B - B0832LTPN01 | Slot 10 Module Fault | BPL832B10_OK_A | CAT_P3 | BPL832 | PRIV_ALARMACK | A_P1_FUEL | Slot 10 Module Fault | BPL832B10_OK_A | C_LOPRI | BPL832DropB | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL832.DropB | Slot10_A
BR4_Tags | BPL832B11_CntrlPwrOK_A | PLC 832 Drop B - B0832LTPN01 | Slot 11 Module Control Power Fault | BPL832B11_CntrlPwrOK_A | CAT_P3 | BPL832 | PRIV_ALARMACK | A_P1_FUEL | Slot 11 Module Control Power Fault | BPL832B11_CntrlPwrOK_A | C_LOPRI | BPL832DropB | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL832.DropB
BR4_Tags | BPL832B11_OK_A | PLC 832 Drop B - B0832LTPN01 | Slot 11 Module Fault | BPL832B11_OK_A | CAT_P3 | BPL832 | PRIV_ALARMACK | A_P1_FUEL | Slot 11 Module Fault | BPL832B11_OK_A | C_LOPRI | BPL832DropB | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL832.DropB | Slot11_A
BR4_Tags | BPL832B12_CntrlPwrOK_A | PLC 832 Drop B - B0832LTPN01 | Slot 12 Module Control Power Fault | BPL832B12_CntrlPwrOK_A | CAT_P3 | BPL832 | PRIV_ALARMACK | A_P1_FUEL | Slot 12 Module Control Power Fault | BPL832B12_CntrlPwrOK_A | C_LOPRI | BPL832DropB | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL832.DropB
BR4_Tags | BPL832B12_OK_A | PLC 832 Drop B - B0832LTPN01 | Slot 12 Module Fault | BPL832B12_OK_A | CAT_P3 | BPL832 | PRIV_ALARMACK | A_P1_FUEL | Slot 12 Module Fault | BPL832B12_OK_A | C_LOPRI | BPL832DropB | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL832.DropB | Slot12_A
BR4_Tags | BPL832C03_CntrlPwrOK_A | PLC 832 Drop C - B0832HVPN01 | Slot 03 Module Control Power Fault | BPL832C03_CntrlPwrOK_A | CAT_P3 | BPL832 | PRIV_ALARMACK | A_P1_FUEL | Slot 03 Module Control Power Fault | BPL832C03_CntrlPwrOK_A | C_LOPRI | BPL832DropC | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL832.DropC
BR4_Tags | BPL832C03_OK_A | PLC 832 Drop C - B0832HVPN01 | Slot 03 Module Fault | BPL832C03_OK_A | CAT_P3 | BPL832 | PRIV_ALARMACK | A_P1_FUEL | Slot 03 Module Fault | BPL832C03_OK_A | C_LOPRI | BPL832DropC | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL832.DropC | Slot3_A
BR4_Tags | BPL832C04_CntrlPwrOK_A | PLC 832 Drop C - B0832HVPN01 | Slot 04 Module Control Power Fault | BPL832C04_CntrlPwrOK_A | CAT_P3 | BPL832 | PRIV_ALARMACK | A_P1_FUEL | Slot 04 Module Control Power Fault | BPL832C04_CntrlPwrOK_A | C_LOPRI | BPL832DropC | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL832.DropC
BR4_Tags | BPL832C04_OK_A | PLC 832 Drop C - B0832HVPN01 | Slot 04 Module Fault | BPL832C04_OK_A | CAT_P3 | BPL832 | PRIV_ALARMACK | A_P1_FUEL | Slot 04 Module Fault | BPL832C04_OK_A | C_LOPRI | BPL832DropC | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL832.DropC | Slot4_A
BR4_Tags | BPL832C05_CntrlPwrOK_A | PLC 832 Drop C - B0832HVPN01 | Slot 05 Module Control Power Fault | BPL832C05_CntrlPwrOK_A | CAT_P3 | BPL832 | PRIV_ALARMACK | A_P1_FUEL | Slot 05 Module Control Power Fault | BPL832C05_CntrlPwrOK_A | C_LOPRI | BPL832DropC | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL832.DropC
BR4_Tags | BPL832C05_OK_A | PLC 832 Drop C - B0832HVPN01 | Slot 05 Module Fault | BPL832C05_OK_A | CAT_P3 | BPL832 | PRIV_ALARMACK | A_P1_FUEL | Slot 05 Module Fault | BPL832C05_OK_A | C_LOPRI | BPL832DropC | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL832.DropC | Slot5_A
BR4_Tags | BPL832C06_CntrlPwrOK_A | PLC 832 Drop C - B0832HVPN01 | Slot 06 Module Control Power Fault | BPL832C06_CntrlPwrOK_A | CAT_P3 | BPL832 | PRIV_ALARMACK | A_P1_FUEL | Slot 06 Module Control Power Fault | BPL832C06_CntrlPwrOK_A | C_LOPRI | BPL832DropC | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL832.DropC
BR4_Tags | BPL832C06_OK_A | PLC 832 Drop C - B0832HVPN01 | Slot 06 Module Fault | BPL832C06_OK_A | CAT_P3 | BPL832 | PRIV_ALARMACK | A_P1_FUEL | Slot 06 Module Fault | BPL832C06_OK_A | C_LOPRI | BPL832DropC | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL832.DropC | Slot6_A
BR4_Tags | BPL832C07_CntrlPwrOK_A | PLC 832 Drop C - B0832HVPN01 | Slot 07 Module Control Power Fault | BPL832C07_CntrlPwrOK_A | CAT_P3 | BPL832 | PRIV_ALARMACK | A_P1_FUEL | Slot 07 Module Control Power Fault | BPL832C07_CntrlPwrOK_A | C_LOPRI | BPL832DropC | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL832.DropC
BR4_Tags | BPL832C07_OK_A | PLC 832 Drop C - B0832HVPN01 | Slot 07 Module Fault | BPL832C07_OK_A | CAT_P3 | BPL832 | PRIV_ALARMACK | A_P1_FUEL | Slot 07 Module Fault | BPL832C07_OK_A | C_LOPRI | BPL832DropC | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL832.DropC | Slot7_A
BR4_Tags | BPL832C08_CntrlPwrOK_A | PLC 832 Drop C - B0832HVPN01 | Slot 08 Module Control Power Fault | BPL832C08_CntrlPwrOK_A | CAT_P3 | BPL832 | PRIV_ALARMACK | A_P1_FUEL | Slot 08 Module Control Power Fault | BPL832C08_CntrlPwrOK_A | C_LOPRI | BPL832DropC | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL832.DropC
BR4_Tags | BPL832C08_OK_A | PLC 832 Drop C - B0832HVPN01 | Slot 08 Module Fault | BPL832C08_OK_A | CAT_P3 | BPL832 | PRIV_ALARMACK | A_P1_FUEL | Slot 08 Module Fault | BPL832C08_OK_A | C_LOPRI | BPL832DropC | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL832.DropC | Slot8_A
BR4_Tags | BPL832C09_CntrlPwrOK_A | PLC 832 Drop C - B0832HVPN01 | Slot 09 Module Control Power Fault | BPL832C09_CntrlPwrOK_A | CAT_P3 | BPL832 | PRIV_ALARMACK | A_P1_FUEL | Slot 09 Module Control Power Fault | BPL832C09_CntrlPwrOK_A | C_LOPRI | BPL832DropC | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL832.DropC
BR4_Tags | BPL832C09_OK_A | PLC 832 Drop C - B0832HVPN01 | Slot 09 Module Fault | BPL832C09_OK_A | CAT_P3 | BPL832 | PRIV_ALARMACK | A_P1_FUEL | Slot 09 Module Fault | BPL832C09_OK_A | C_LOPRI | BPL832DropC | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL832.DropC | Slot9_A
BR4_Tags | BPL832C10_CntrlPwrOK_A | PLC 832 Drop C - B0832HVPN01 | Slot 10 Module Control Power Fault | BPL832C10_CntrlPwrOK_A | CAT_P3 | BPL832 | PRIV_ALARMACK | A_P1_FUEL | Slot 10 Module Control Power Fault | BPL832C10_CntrlPwrOK_A | C_LOPRI | BPL832DropC | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL832.DropC
BR4_Tags | BPL832C10_OK_A | PLC 832 Drop C - B0832HVPN01 | Slot 10 Module Fault | BPL832C10_OK_A | CAT_P3 | BPL832 | PRIV_ALARMACK | A_P1_FUEL | Slot 10 Module Fault | BPL832C10_OK_A | C_LOPRI | BPL832DropC | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL832.DropC | Slot10_A
BR4_Tags | BPL832C11_CntrlPwrOK_A | PLC 832 Drop C - B0832HVPN01 | Slot 11 Module Control Power Fault | BPL832C11_CntrlPwrOK_A | CAT_P3 | BPL832 | PRIV_ALARMACK | A_P1_FUEL | Slot 11 Module Control Power Fault | BPL832C11_CntrlPwrOK_A | C_LOPRI | BPL832DropC | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL832.DropC
BR4_Tags | BPL832C11_OK_A | PLC 832 Drop C - B0832HVPN01 | Slot 11 Module Fault | BPL832C11_OK_A | CAT_P3 | BPL832 | PRIV_ALARMACK | A_P1_FUEL | Slot 11 Module Fault | BPL832C11_OK_A | C_LOPRI | BPL832DropC | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL832.DropC | Slot11_A
BR4_Tags | BPL832C12_CntrlPwrOK_A | PLC 832 Drop C - B0832HVPN01 | Slot 12 Module Control Power Fault | BPL832C12_CntrlPwrOK_A | CAT_P3 | BPL832 | PRIV_ALARMACK | A_P1_FUEL | Slot 12 Module Control Power Fault | BPL832C12_CntrlPwrOK_A | C_LOPRI | BPL832DropC | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL832.DropC
BR4_Tags | BPL832C12_OK_A | PLC 832 Drop C - B0832HVPN01 | Slot 12 Module Fault | BPL832C12_OK_A | CAT_P3 | BPL832 | PRIV_ALARMACK | A_P1_FUEL | Slot 12 Module Fault | BPL832C12_OK_A | C_LOPRI | BPL832DropC | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL832.DropC | Slot12_A
BR4_Tags | BPL832D03_CntrlPwrOK_A | PLC 832 Drop D - B0832HVPN02 | Slot 03 Module Control Power Fault | BPL832D03_CntrlPwrOK_A | CAT_P3 | BPL832 | PRIV_ALARMACK | A_P1_FUEL | Slot 03 Module Control Power Fault | BPL832D03_CntrlPwrOK_A | C_LOPRI | BPL832DropD | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL832.DropD
BR4_Tags | BPL832D03_OK_A | PLC 832 Drop D - B0832HVPN02 | Slot 03 Module Fault | BPL832D03_OK_A | CAT_P3 | BPL832 | PRIV_ALARMACK | A_P1_FUEL | Slot 03 Module Fault | BPL832D03_OK_A | C_LOPRI | BPL832DropD | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL832.DropD | Slot3_A
BR4_Tags | BPL832D04_CntrlPwrOK_A | PLC 832 Drop D - B0832HVPN02 | Slot 04 Module Control Power Fault | BPL832D04_CntrlPwrOK_A | CAT_P3 | BPL832 | PRIV_ALARMACK | A_P1_FUEL | Slot 04 Module Control Power Fault | BPL832D04_CntrlPwrOK_A | C_LOPRI | BPL832DropD | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL832.DropD
BR4_Tags | BPL832D04_OK_A | PLC 832 Drop D - B0832HVPN02 | Slot 04 Module Fault | BPL832D04_OK_A | CAT_P3 | BPL832 | PRIV_ALARMACK | A_P1_FUEL | Slot 04 Module Fault | BPL832D04_OK_A | C_LOPRI | BPL832DropD | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL832.DropD | Slot4_A
BR4_Tags | BPL832D05_CntrlPwrOK_A | PLC 832 Drop D - B0832HVPN02 | Slot 05 Module Control Power Fault | BPL832D05_CntrlPwrOK_A | CAT_P3 | BPL832 | PRIV_ALARMACK | A_P1_FUEL | Slot 05 Module Control Power Fault | BPL832D05_CntrlPwrOK_A | C_LOPRI | BPL832DropD | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL832.DropD
BR4_Tags | BPL832D05_OK_A | PLC 832 Drop D - B0832HVPN02 | Slot 05 Module Fault | BPL832D05_OK_A | CAT_P3 | BPL832 | PRIV_ALARMACK | A_P1_FUEL | Slot 05 Module Fault | BPL832D05_OK_A | C_LOPRI | BPL832DropD | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL832.DropD | Slot5_A
BR4_Tags | BPL832D06_CntrlPwrOK_A | PLC 832 Drop D - B0832HVPN02 | Slot 06 Module Control Power Fault | BPL832D06_CntrlPwrOK_A | CAT_P3 | BPL832 | PRIV_ALARMACK | A_P1_FUEL | Slot 06 Module Control Power Fault | BPL832D06_CntrlPwrOK_A | C_LOPRI | BPL832DropD | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL832.DropD
BR4_Tags | BPL832D06_OK_A | PLC 832 Drop D - B0832HVPN02 | Slot 06 Module Fault | BPL832D06_OK_A | CAT_P3 | BPL832 | PRIV_ALARMACK | A_P1_FUEL | Slot 06 Module Fault | BPL832D06_OK_A | C_LOPRI | BPL832DropD | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL832.DropD | Slot6_A
BR4_Tags | BPL832D07_CntrlPwrOK_A | PLC 832 Drop D - B0832HVPN02 | Slot 07 Module Control Power Fault | BPL832D07_CntrlPwrOK_A | CAT_P3 | BPL832 | PRIV_ALARMACK | A_P1_FUEL | Slot 07 Module Control Power Fault | BPL832D07_CntrlPwrOK_A | C_LOPRI | BPL832DropD | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL832.DropD
BR4_Tags | BPL832D07_OK_A | PLC 832 Drop D - B0832HVPN02 | Slot 07 Module Fault | BPL832D07_OK_A | CAT_P3 | BPL832 | PRIV_ALARMACK | A_P1_FUEL | Slot 07 Module Fault | BPL832D07_OK_A | C_LOPRI | BPL832DropD | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL832.DropD | Slot7_A
BR4_Tags | BPL832D08_CntrlPwrOK_A | PLC 832 Drop D - B0832HVPN02 | Slot 08 Module Control Power Fault | BPL832D08_CntrlPwrOK_A | CAT_P3 | BPL832 | PRIV_ALARMACK | A_P1_FUEL | Slot 08 Module Control Power Fault | BPL832D08_CntrlPwrOK_A | C_LOPRI | BPL832DropD | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL832.DropD
BR4_Tags | BPL832D08_OK_A | PLC 832 Drop D - B0832HVPN02 | Slot 08 Module Fault | BPL832D08_OK_A | CAT_P3 | BPL832 | PRIV_ALARMACK | A_P1_FUEL | Slot 08 Module Fault | BPL832D08_OK_A | C_LOPRI | BPL832DropD | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL832.DropD | Slot8_A
BR4_Tags | BPL832D09_CntrlPwrOK_A | PLC 832 Drop D - B0832HVPN02 | Slot 09 Module Control Power Fault | BPL832D09_CntrlPwrOK_A | CAT_P3 | BPL832 | PRIV_ALARMACK | A_P1_FUEL | Slot 09 Module Control Power Fault | BPL832D09_CntrlPwrOK_A | C_LOPRI | BPL832DropD | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL832.DropD
BR4_Tags | BPL832D09_OK_A | PLC 832 Drop D - B0832HVPN02 | Slot 09 Module Fault | BPL832D09_OK_A | CAT_P3 | BPL832 | PRIV_ALARMACK | A_P1_FUEL | Slot 09 Module Fault | BPL832D09_OK_A | C_LOPRI | BPL832DropD | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL832.DropD | Slot9_A
BR4_Tags | BPL832D10_CntrlPwrOK_A | PLC 832 Drop D - B0832HVPN02 | Slot 10 Module Control Power Fault | BPL832D10_CntrlPwrOK_A | CAT_P3 | BPL832 | PRIV_ALARMACK | A_P1_FUEL | Slot 10 Module Control Power Fault | BPL832D10_CntrlPwrOK_A | C_LOPRI | BPL832DropD | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL832.DropD
BR4_Tags | BPL832D10_OK_A | PLC 832 Drop D - B0832HVPN02 | Slot 10 Module Fault | BPL832D10_OK_A | CAT_P3 | BPL832 | PRIV_ALARMACK | A_P1_FUEL | Slot 10 Module Fault | BPL832D10_OK_A | C_LOPRI | BPL832DropD | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL832.DropD | Slot10_A
BR4_Tags | BPL832D11_CntrlPwrOK_A | PLC 832 Drop D - B0832HVPN02 | Slot 11 Module Control Power Fault | BPL832D11_CntrlPwrOK_A | CAT_P3 | BPL832 | PRIV_ALARMACK | A_P1_FUEL | Slot 11 Module Control Power Fault | BPL832D11_CntrlPwrOK_A | C_LOPRI | BPL832DropD | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL832.DropD
BR4_Tags | BPL832D11_OK_A | PLC 832 Drop D - B0832HVPN02 | Slot 11 Module Fault | BPL832D11_OK_A | CAT_P3 | BPL832 | PRIV_ALARMACK | A_P1_FUEL | Slot 11 Module Fault | BPL832D11_OK_A | C_LOPRI | BPL832DropD | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL832.DropD | Slot11_A
BR4_Tags | BPL832D12_CntrlPwrOK_A | PLC 832 Drop D - B0832HVPN02 | Slot 12 Module Control Power Fault | BPL832D12_CntrlPwrOK_A | CAT_P3 | BPL832 | PRIV_ALARMACK | A_P1_FUEL | Slot 12 Module Control Power Fault | BPL832D12_CntrlPwrOK_A | C_LOPRI | BPL832DropD | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL832.DropD
BR4_Tags | BPL832D12_OK_A | PLC 832 Drop D - B0832HVPN02 | Slot 12 Module Fault | BPL832D12_OK_A | CAT_P3 | BPL832 | PRIV_ALARMACK | A_P1_FUEL | Slot 12 Module Fault | BPL832D12_OK_A | C_LOPRI | BPL832DropD | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL832.DropD | Slot12_A
BR4_Tags | BPL832E03_CntrlPwrOK_A | PLC 832 Drop E - B0832HVPN03 | Slot 03 Module Control Power Fault | BPL832E03_CntrlPwrOK_A | CAT_P3 | BPL832 | PRIV_ALARMACK | A_P1_FUEL | Slot 03 Module Control Power Fault | BPL832E03_CntrlPwrOK_A | C_LOPRI | BPL832DropE | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL832.DropE
BR4_Tags | BPL832E03_OK_A | PLC 832 Drop E - B0832HVPN03 | Slot 03 Module Fault | BPL832E03_OK_A | CAT_P3 | BPL832 | PRIV_ALARMACK | A_P1_FUEL | Slot 03 Module Fault | BPL832E03_OK_A | C_LOPRI | BPL832DropE | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL832.DropE | Slot3_A
BR4_Tags | BPL832E04_CntrlPwrOK_A | PLC 832 Drop E - B0832HVPN03 | Slot 04 Module Control Power Fault | BPL832E04_CntrlPwrOK_A | CAT_P3 | BPL832 | PRIV_ALARMACK | A_P1_FUEL | Slot 04 Module Control Power Fault | BPL832E04_CntrlPwrOK_A | C_LOPRI | BPL832DropE | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL832.DropE
BR4_Tags | BPL832E04_OK_A | PLC 832 Drop E - B0832HVPN03 | Slot 04 Module Fault | BPL832E04_OK_A | CAT_P3 | BPL832 | PRIV_ALARMACK | A_P1_FUEL | Slot 04 Module Fault | BPL832E04_OK_A | C_LOPRI | BPL832DropE | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL832.DropE | Slot4_A
BR4_Tags | BPL832E05_CntrlPwrOK_A | PLC 832 Drop E - B0832HVPN03 | Slot 05 Module Control Power Fault | BPL832E05_CntrlPwrOK_A | CAT_P3 | BPL832 | PRIV_ALARMACK | A_P1_FUEL | Slot 05 Module Control Power Fault | BPL832E05_CntrlPwrOK_A | C_LOPRI | BPL832DropE | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL832.DropE
BR4_Tags | BPL832E05_OK_A | PLC 832 Drop E - B0832HVPN03 | Slot 05 Module Fault | BPL832E05_OK_A | CAT_P3 | BPL832 | PRIV_ALARMACK | A_P1_FUEL | Slot 05 Module Fault | BPL832E05_OK_A | C_LOPRI | BPL832DropE | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL832.DropE | Slot5_A
BR4_Tags | BPL832E06_CntrlPwrOK_A | PLC 832 Drop E - B0832HVPN03 | Slot 06 Module Control Power Fault | BPL832E06_CntrlPwrOK_A | CAT_P3 | BPL832 | PRIV_ALARMACK | A_P1_FUEL | Slot 06 Module Control Power Fault | BPL832E06_CntrlPwrOK_A | C_LOPRI | BPL832DropE | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL832.DropE
BR4_Tags | BPL832E06_OK_A | PLC 832 Drop E - B0832HVPN03 | Slot 06 Module Fault | BPL832E06_OK_A | CAT_P3 | BPL832 | PRIV_ALARMACK | A_P1_FUEL | Slot 06 Module Fault | BPL832E06_OK_A | C_LOPRI | BPL832DropE | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL832.DropE | Slot6_A
BR4_Tags | BPL832E07_CntrlPwrOK_A | PLC 832 Drop E - B0832HVPN03 | Slot 07 Module Control Power Fault | BPL832E07_CntrlPwrOK_A | CAT_P3 | BPL832 | PRIV_ALARMACK | A_P1_FUEL | Slot 07 Module Control Power Fault | BPL832E07_CntrlPwrOK_A | C_LOPRI | BPL832DropE | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL832.DropE
BR4_Tags | BPL832E07_OK_A | PLC 832 Drop E - B0832HVPN03 | Slot 07 Module Fault | BPL832E07_OK_A | CAT_P3 | BPL832 | PRIV_ALARMACK | A_P1_FUEL | Slot 07 Module Fault | BPL832E07_OK_A | C_LOPRI | BPL832DropE | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL832.DropE | Slot7_A
BR4_Tags | BPL832E08_CntrlPwrOK_A | PLC 832 Drop E - B0832HVPN03 | Slot 08 Module Control Power Fault | BPL832E08_CntrlPwrOK_A | CAT_P3 | BPL832 | PRIV_ALARMACK | A_P1_FUEL | Slot 08 Module Control Power Fault | BPL832E08_CntrlPwrOK_A | C_LOPRI | BPL832DropE | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL832.DropE
BR4_Tags | BPL832E08_OK_A | PLC 832 Drop E - B0832HVPN03 | Slot 08 Module Fault | BPL832E08_OK_A | CAT_P3 | BPL832 | PRIV_ALARMACK | A_P1_FUEL | Slot 08 Module Fault | BPL832E08_OK_A | C_LOPRI | BPL832DropE | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL832.DropE | Slot8_A
BR4_Tags | BPL832E09_CntrlPwrOK_A | PLC 832 Drop E - B0832HVPN03 | Slot 09 Module Control Power Fault | BPL832E09_CntrlPwrOK_A | CAT_P3 | BPL832 | PRIV_ALARMACK | A_P1_FUEL | Slot 09 Module Control Power Fault | BPL832E09_CntrlPwrOK_A | C_LOPRI | BPL832DropE | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL832.DropE
BR4_Tags | BPL832E09_OK_A | PLC 832 Drop E - B0832HVPN03 | Slot 09 Module Fault | BPL832E09_OK_A | CAT_P3 | BPL832 | PRIV_ALARMACK | A_P1_FUEL | Slot 09 Module Fault | BPL832E09_OK_A | C_LOPRI | BPL832DropE | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL832.DropE | Slot9_A
BR4_Tags | BPL832E10_CntrlPwrOK_A | PLC 832 Drop E - B0832HVPN03 | Slot 10 Module Control Power Fault | BPL832E10_CntrlPwrOK_A | CAT_P3 | BPL832 | PRIV_ALARMACK | A_P1_FUEL | Slot 10 Module Control Power Fault | BPL832E10_CntrlPwrOK_A | C_LOPRI | BPL832DropE | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL832.DropE
BR4_Tags | BPL832E10_OK_A | PLC 832 Drop E - B0832HVPN03 | Slot 10 Module Fault | BPL832E10_OK_A | CAT_P3 | BPL832 | PRIV_ALARMACK | A_P1_FUEL | Slot 10 Module Fault | BPL832E10_OK_A | C_LOPRI | BPL832DropE | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL832.DropE | Slot10_A
BR4_Tags | BPL832E11_CntrlPwrOK_A | PLC 832 Drop E - B0832HVPN03 | Slot 11 Module Control Power Fault | BPL832E11_CntrlPwrOK_A | CAT_P3 | BPL832 | PRIV_ALARMACK | A_P1_FUEL | Slot 11 Module Control Power Fault | BPL832E11_CntrlPwrOK_A | C_LOPRI | BPL832DropE | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL832.DropE
BR4_Tags | BPL832E11_OK_A | PLC 832 Drop E - B0832HVPN03 | Slot 11 Module Fault | BPL832E11_OK_A | CAT_P3 | BPL832 | PRIV_ALARMACK | A_P1_FUEL | Slot 11 Module Fault | BPL832E11_OK_A | C_LOPRI | BPL832DropE | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL832.DropE | Slot11_A
BR4_Tags | BPL832E12_CntrlPwrOK_A | PLC 832 Drop E - B0832HVPN03 | Slot 12 Module Control Power Fault | BPL832E12_CntrlPwrOK_A | CAT_P3 | BPL832 | PRIV_ALARMACK | A_P1_FUEL | Slot 12 Module Control Power Fault | BPL832E12_CntrlPwrOK_A | C_LOPRI | BPL832DropE | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL832.DropE
BR4_Tags | BPL832E12_OK_A | PLC 832 Drop E - B0832HVPN03 | Slot 12 Module Fault | BPL832E12_OK_A | CAT_P3 | BPL832 | PRIV_ALARMACK | A_P1_FUEL | Slot 12 Module Fault | BPL832E12_OK_A | C_LOPRI | BPL832DropE | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL832.DropE | Slot12_A
BR4_Tags | BPL832F03_CntrlPwrOK_A | PLC 832 Drop F - B0832LVPN01 | Slot 03 Module Control Power Fault | BPL832F03_CntrlPwrOK_A | CAT_P3 | BPL832 | PRIV_ALARMACK | A_P1_FUEL | Slot 03 Module Control Power Fault | BPL832F03_CntrlPwrOK_A | C_LOPRI | BPL832DropF | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL832.DropF
BR4_Tags | BPL832F03_OK_A | PLC 832 Drop F - B0832LVPN01 | Slot 03 Module Fault | BPL832F03_OK_A | CAT_P3 | BPL832 | PRIV_ALARMACK | A_P1_FUEL | Slot 03 Module Fault | BPL832F03_OK_A | C_LOPRI | BPL832DropF | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL832.DropF | Slot3_A
BR4_Tags | BPL832F04_CntrlPwrOK_A | PLC 832 Drop F - B0832LVPN01 | Slot 04 Module Control Power Fault | BPL832F04_CntrlPwrOK_A | CAT_P3 | BPL832 | PRIV_ALARMACK | A_P1_FUEL | Slot 04 Module Control Power Fault | BPL832F04_CntrlPwrOK_A | C_LOPRI | BPL832DropF | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL832.DropF
BR4_Tags | BPL832F04_OK_A | PLC 832 Drop F - B0832LVPN01 | Slot 04 Module Fault | BPL832F04_OK_A | CAT_P3 | BPL832 | PRIV_ALARMACK | A_P1_FUEL | Slot 04 Module Fault | BPL832F04_OK_A | C_LOPRI | BPL832DropF | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL832.DropF | Slot4_A
BR4_Tags | BPL832F05_CntrlPwrOK_A | PLC 832 Drop F - B0832LVPN01 | Slot 05 Module Control Power Fault | BPL832F05_CntrlPwrOK_A | CAT_P3 | BPL832 | PRIV_ALARMACK | A_P1_FUEL | Slot 05 Module Control Power Fault | BPL832F05_CntrlPwrOK_A | C_LOPRI | BPL832DropF | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL832.DropF
BR4_Tags | BPL832F05_OK_A | PLC 832 Drop F - B0832LVPN01 | Slot 05 Module Fault | BPL832F05_OK_A | CAT_P3 | BPL832 | PRIV_ALARMACK | A_P1_FUEL | Slot 05 Module Fault | BPL832F05_OK_A | C_LOPRI | BPL832DropF | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL832.DropF | Slot5_A
BR4_Tags | BPL832F06_CntrlPwrOK_A | PLC 832 Drop F - B0832LVPN01 | Slot 06 Module Control Power Fault | BPL832F06_CntrlPwrOK_A | CAT_P3 | BPL832 | PRIV_ALARMACK | A_P1_FUEL | Slot 06 Module Control Power Fault | BPL832F06_CntrlPwrOK_A | C_LOPRI | BPL832DropF | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL832.DropF
BR4_Tags | BPL832F06_OK_A | PLC 832 Drop F - B0832LVPN01 | Slot 06 Module Fault | BPL832F06_OK_A | CAT_P3 | BPL832 | PRIV_ALARMACK | A_P1_FUEL | Slot 06 Module Fault | BPL832F06_OK_A | C_LOPRI | BPL832DropF | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL832.DropF | Slot6_A
BR4_Tags | BPL832F07_CntrlPwrOK_A | PLC 832 Drop F - B0832LVPN01 | Slot 07 Module Control Power Fault | BPL832F07_CntrlPwrOK_A | CAT_P3 | BPL832 | PRIV_ALARMACK | A_P1_FUEL | Slot 07 Module Control Power Fault | BPL832F07_CntrlPwrOK_A | C_LOPRI | BPL832DropF | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL832.DropF
BR4_Tags | BPL832F07_OK_A | PLC 832 Drop F - B0832LVPN01 | Slot 07 Module Fault | BPL832F07_OK_A | CAT_P3 | BPL832 | PRIV_ALARMACK | A_P1_FUEL | Slot 07 Module Fault | BPL832F07_OK_A | C_LOPRI | BPL832DropF | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL832.DropF | Slot7_A
BR4_Tags | BPL832F08_CntrlPwrOK_A | PLC 832 Drop F - B0832LVPN01 | Slot 08 Module Control Power Fault | BPL832F08_CntrlPwrOK_A | CAT_P3 | BPL832 | PRIV_ALARMACK | A_P1_FUEL | Slot 08 Module Control Power Fault | BPL832F08_CntrlPwrOK_A | C_LOPRI | BPL832DropF | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL832.DropF
BR4_Tags | BPL832F08_OK_A | PLC 832 Drop F - B0832LVPN01 | Slot 08 Module Fault | BPL832F08_OK_A | CAT_P3 | BPL832 | PRIV_ALARMACK | A_P1_FUEL | Slot 08 Module Fault | BPL832F08_OK_A | C_LOPRI | BPL832DropF | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL832.DropF | Slot8_A
BR4_Tags | BPL832F09_CntrlPwrOK_A | PLC 832 Drop F - B0832LVPN01 | Slot 09 Module Control Power Fault | BPL832F09_CntrlPwrOK_A | CAT_P3 | BPL832 | PRIV_ALARMACK | A_P1_FUEL | Slot 09 Module Control Power Fault | BPL832F09_CntrlPwrOK_A | C_LOPRI | BPL832DropF | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL832.DropF
BR4_Tags | BPL832F09_OK_A | PLC 832 Drop F - B0832LVPN01 | Slot 09 Module Fault | BPL832F09_OK_A | CAT_P3 | BPL832 | PRIV_ALARMACK | A_P1_FUEL | Slot 09 Module Fault | BPL832F09_OK_A | C_LOPRI | BPL832DropF | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL832.DropF | Slot9_A
BR4_Tags | BPL832G03_CntrlPwrOK_A | PLC 832 Drop G - B0832LVPN02 | Slot 03 Module Control Power Fault | BPL832G03_CntrlPwrOK_A | CAT_P3 | BPL832 | PRIV_ALARMACK | A_P1_FUEL | Slot 03 Module Control Power Fault | BPL832G03_CntrlPwrOK_A | C_LOPRI | BPL832DropG | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL832.DropG
BR4_Tags | BPL832G03_OK_A | PLC 832 Drop G - B0832LVPN02 | Slot 03 Module Fault | BPL832G03_OK_A | CAT_P3 | BPL832 | PRIV_ALARMACK | A_P1_FUEL | Slot 03 Module Fault | BPL832G03_OK_A | C_LOPRI | BPL832DropG | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL832.DropG | Slot3_A
BR4_Tags | BPL832G04_CntrlPwrOK_A | PLC 832 Drop G - B0832LVPN02 | Slot 04 Module Control Power Fault | BPL832G04_CntrlPwrOK_A | CAT_P3 | BPL832 | PRIV_ALARMACK | A_P1_FUEL | Slot 04 Module Control Power Fault | BPL832G04_CntrlPwrOK_A | C_LOPRI | BPL832DropG | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL832.DropG
BR4_Tags | BPL832G04_OK_A | PLC 832 Drop G - B0832LVPN02 | Slot 04 Module Fault | BPL832G04_OK_A | CAT_P3 | BPL832 | PRIV_ALARMACK | A_P1_FUEL | Slot 04 Module Fault | BPL832G04_OK_A | C_LOPRI | BPL832DropG | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL832.DropG | Slot4_A
BR4_Tags | BPL832G05_CntrlPwrOK_A | PLC 832 Drop G - B0832LVPN02 | Slot 05 Module Control Power Fault | BPL832G05_CntrlPwrOK_A | CAT_P3 | BPL832 | PRIV_ALARMACK | A_P1_FUEL | Slot 05 Module Control Power Fault | BPL832G05_CntrlPwrOK_A | C_LOPRI | BPL832DropG | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL832.DropG
BR4_Tags | BPL832G05_OK_A | PLC 832 Drop G - B0832LVPN02 | Slot 05 Module Fault | BPL832G05_OK_A | CAT_P3 | BPL832 | PRIV_ALARMACK | A_P1_FUEL | Slot 05 Module Fault | BPL832G05_OK_A | C_LOPRI | BPL832DropG | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL832.DropG | Slot5_A
BR4_Tags | BPL832G06_CntrlPwrOK_A | PLC 832 Drop G - B0832LVPN02 | Slot 06 Module Control Power Fault | BPL832G06_CntrlPwrOK_A | CAT_P3 | BPL832 | PRIV_ALARMACK | A_P1_FUEL | Slot 06 Module Control Power Fault | BPL832G06_CntrlPwrOK_A | C_LOPRI | BPL832DropG | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL832.DropG
BR4_Tags | BPL832G06_OK_A | PLC 832 Drop G - B0832LVPN02 | Slot 06 Module Fault | BPL832G06_OK_A | CAT_P3 | BPL832 | PRIV_ALARMACK | A_P1_FUEL | Slot 06 Module Fault | BPL832G06_OK_A | C_LOPRI | BPL832DropG | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL832.DropG | Slot6_A
BR4_Tags | BPL832G07_CntrlPwrOK_A | PLC 832 Drop G - B0832LVPN02 | Slot 07 Module Control Power Fault | BPL832G07_CntrlPwrOK_A | CAT_P3 | BPL832 | PRIV_ALARMACK | A_P1_FUEL | Slot 07 Module Control Power Fault | BPL832G07_CntrlPwrOK_A | C_LOPRI | BPL832DropG | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL832.DropG
BR4_Tags | BPL832G07_OK_A | PLC 832 Drop G - B0832LVPN02 | Slot 07 Module Fault | BPL832G07_OK_A | CAT_P3 | BPL832 | PRIV_ALARMACK | A_P1_FUEL | Slot 07 Module Fault | BPL832G07_OK_A | C_LOPRI | BPL832DropG | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL832.DropG | Slot7_A
BR4_Tags | BPL832G08_CntrlPwrOK_A | PLC 832 Drop G - B0832LVPN02 | Slot 08 Module Control Power Fault | BPL832G08_CntrlPwrOK_A | CAT_P3 | BPL832 | PRIV_ALARMACK | A_P1_FUEL | Slot 08 Module Control Power Fault | BPL832G08_CntrlPwrOK_A | C_LOPRI | BPL832DropG | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL832.DropG
BR4_Tags | BPL832G08_OK_A | PLC 832 Drop G - B0832LVPN02 | Slot 08 Module Fault | BPL832G08_OK_A | CAT_P3 | BPL832 | PRIV_ALARMACK | A_P1_FUEL | Slot 08 Module Fault | BPL832G08_OK_A | C_LOPRI | BPL832DropG | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL832.DropG | Slot8_A
BR4_Tags | BPL832PN01STR01_A | Vehicle Workshop PLC | Lock Off Stops Statutory Relay | BPL832PN01STR01_A | CAT_P1 | BPL832 | PRIV_ALARMACK | A_P1_FUEL | Lock Off Stops Statutory Relay | BPL832PN01STR01_A | C_LOPRI | BPL832 | Class_Process | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL832
BR4_Tags | BPP840PS01_A | HV WrkShp Donax TC50 Pump | Filter Blocked | BPP840PS01_A | CAT_P3 | HVWORKSHOP1 | PRIV_ALARMACK | A_P1_FUEL | Filter High Pressure | BPP840PS01_A | C_LOPRI | BPP840 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.FUBULOIL.HVWRKSHP.BPP840
BR4_Tags | BPP841PS01_A | HV WrkShp Tellus 100 Pump | Filter Blocked | BPP841PS01_A | CAT_P3 | HVWORKSHOP1 | PRIV_ALARMACK | A_P1_FUEL | Filter High Pressure | BPP841PS01_A | C_LOPRI | BPP841 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.FUBULOIL.HVWRKSHP.BPP841
BR4_Tags | BPP842PS01_A | HV WrkShp Rimula Oil Pump | Filter Blocked | BPP842PS01_A | CAT_P3 | HVWORKSHOP1 | PRIV_ALARMACK | A_P1_FUEL | Filter High Pressure | BPP842PS01_A | C_LOPRI | BPP842 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.FUBULOIL.HVWRKSHP.BPP842
BR4_Tags | BPP926PS01_A | HV WrkShp Donax TC30 Pump | Filter Blocked | BPP926PS01_A | CAT_P3 | HVWORKSHOP2 | PRIV_ALARMACK | A_P1_FUEL | Filter High Pressure | BPP926PS01_A | C_LOPRI | BPP926 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.FUBULOIL.HVWRKSHP2.BPP926
BR4_Tags | BPP927PS01_A | HV WrkShp Corena Pump | Filter Blocked | BPP927PS01_A | CAT_P3 | HVWORKSHOP2 | PRIV_ALARMACK | A_P1_FUEL | Filter High Pressure | BPP927PS01_A | C_LOPRI | BPP927 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.FUBULOIL.HVWRKSHP2.BPP927
BR4_Tags | BPP928PS01_A | HV WrkShp Spirax Pump | Filter Blocked | BPP928PS01_A | CAT_P3 | HVWORKSHOP2 | PRIV_ALARMACK | A_P1_FUEL | Filter High Pressure | BPP928PS01_A | C_LOPRI | BPP928 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.FUBULOIL.HVWRKSHP2.BPP928
BR4_Tags | BPP930PS01_A | HV WrkShp Hyperia 680 Pump | Filter Blocked | BPP930PS01_A | CAT_P3 | HVWORKSHOP3 | PRIV_ALARMACK | A_P1_FUEL | Filter High Pressure | BPP930PS01_A | C_LOPRI | BPP930 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.FUBULOIL.HVWRKSHP3.BPP930
BR4_Tags | BPP931PS01_A | HV WrkShp Donax TC10 Pump | Filter Blocked | BPP931PS01_A | CAT_P3 | HVWORKSHOP3 | PRIV_ALARMACK | A_P1_FUEL | Filter High Pressure | BPP931PS01_A | C_LOPRI | BPP931 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.FUBULOIL.HVWRKSHP3.BPP931
BR4_Tags | BTK820FQ01_Flw_A | HV WrkShp Dirty Waste Oil Tk | Loading Wrong Flow Trip | BTK820FQ01_Flw_A | CAT_P3 | HVWORKSHOP1 | PRIV_ALARMACK | A_P1_FUEL | Loading Wrong Flow | BTK820FQ01_Flw_A | C_LOPRI | BTK820FQ01 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.FUBULOIL.HVWRKSHP.BTK820.FQ01
BR4_Tags | BTK820LT01_Hi_A | HV WrkShp Dirty Waste Oil Tk | Level High Trip | BTK820LT01_Hi_A | CAT_P3 | HVWORKSHOP1 | PRIV_ALARMACK | A_P1_FUEL | Level High | BTK820LT01_Hi_A | C_LOPRI | BTK820 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.FUBULOIL.HVWRKSHP.BTK820.LT01
BR4_Tags | BTK820LT01_HiHi_A | HV WrkShp Dirty Waste Oil Tk | Level High High Trip | BTK820LT01_HiHi_A | CAT_P3 | HVWORKSHOP1 | PRIV_ALARMACK | A_P1_FUEL | Level High High | BTK820LT01_HiHi_A | C_LOPRI | BTK820 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.FUBULOIL.HVWRKSHP.BTK820.LT01
BR4_Tags | BTK820LT01_Lo_A | HV WrkShp Dirty Waste Oil Tk | Level Low | BTK820LT01_Lo_A | CAT_P3 | HVWORKSHOP1 | PRIV_ALARMACK | A_P1_FUEL | Level Low | BTK820LT01_Lo_A | C_LOPRI | BTK820 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.FUBULOIL.HVWRKSHP.BTK820.LT01
BR4_Tags | BTK820LT01_OK_A | Vehicle Workshop PLC | Rack 0 Slot 1 Channel 2 Error | BTK820LT01_OK_A | CAT_P3 | BPL832 | PRIV_ALARMACK | A_P1_FUEL | Rack 0 Slot 1 Channel 2 Error | BTK820LT01_OK_A | C_LOPRI | BPL832 | Class_Equipment | BR4_Cluster1 | BR4.UTILITIES.FUBULOIL.HVWRKSHP.BTK820.LT01
BR4_Tags | BTK821FQ01_Flw_A | HV WrkShp Clean Waste Oil Tk | Loading Wrong Flow Trip | BTK821FQ01_Flw_A | CAT_P3 | HVWORKSHOP1 | PRIV_ALARMACK | A_P1_FUEL | Loading Wrong Flow | BTK821FQ01_Flw_A | C_LOPRI | BTK821FQ01 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.FUBULOIL.HVWRKSHP.BTK821.FQ01
BR4_Tags | BTK821LT01_Hi_A | HV WrkShp Clean Waste Oil Tk | Level High Trip | BTK821LT01_Hi_A | CAT_P3 | HVWORKSHOP1 | PRIV_ALARMACK | A_P1_FUEL | Level High | BTK821LT01_Hi_A | C_LOPRI | BTK821 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.FUBULOIL.HVWRKSHP.BTK821.LT01
BR4_Tags | BTK821LT01_HiHi_A | HV WrkShp Clean Waste Oil Tk | Level High High Trip | BTK821LT01_HiHi_A | CAT_P3 | HVWORKSHOP1 | PRIV_ALARMACK | A_P1_FUEL | Level High High | BTK821LT01_HiHi_A | C_LOPRI | BTK821 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.FUBULOIL.HVWRKSHP.BTK821.LT01
BR4_Tags | BTK821LT01_Lo_A | HV WrkShp Clean Waste Oil Tk | Level Low | BTK821LT01_Lo_A | CAT_P3 | HVWORKSHOP1 | PRIV_ALARMACK | A_P1_FUEL | Level Low | BTK821LT01_Lo_A | C_LOPRI | BTK821 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.FUBULOIL.HVWRKSHP.BTK821.LT01
BR4_Tags | BTK821LT01_OK_A | Vehicle Workshop PLC | Rack 0 Slot 1 Channel 3 Error | BTK821LT01_OK_A | CAT_P3 | BPL832 | PRIV_ALARMACK | A_P1_FUEL | Rack 0 Slot 1 Channel 3 Error | BTK821LT01_OK_A | C_LOPRI | BPL832 | Class_Equipment | BR4_Cluster1 | BR4.UTILITIES.FUBULOIL.HVWRKSHP.BTK821.LT01
BR4_Tags | BTK822FQ01_Flw_A | HV WrkShp Rimula Oil Bulk Tk | Unloading Wrong Flow Trip | BTK822FQ01_Flw_A | CAT_P3 | HVWORKSHOP1 | PRIV_ALARMACK | A_P1_FUEL | Unloading Wrong Flow | BTK822FQ01_Flw_A | C_LOPRI | BTK822FQ01 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.FUBULOIL.HVWRKSHP.BTK822.FQ01
BR4_Tags | BTK822LT01_Hi_A | HV WrkShp Rimula Oil Bulk Tk | Level High Trip | BTK822LT01_Hi_A | CAT_P3 | HVWORKSHOP1 | PRIV_ALARMACK | A_P1_FUEL | Level High | BTK822LT01_Hi_A | C_LOPRI | BTK822 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.FUBULOIL.HVWRKSHP.BTK822.LT01
BR4_Tags | BTK822LT01_HiHi_A | HV WrkShp Rimula Oil Bulk Tk | Level High High Trip | BTK822LT01_HiHi_A | CAT_P3 | HVWORKSHOP1 | PRIV_ALARMACK | A_P1_FUEL | Level High High | BTK822LT01_HiHi_A | C_LOPRI | BTK822 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.FUBULOIL.HVWRKSHP.BTK822.LT01
BR4_Tags | BTK822LT01_Lo_A | HV WrkShp Rimula Oil Bulk Tk | Level Low Trip | BTK822LT01_Lo_A | CAT_P3 | HVWORKSHOP1 | PRIV_ALARMACK | A_P1_FUEL | Level Low | BTK822LT01_Lo_A | C_LOPRI | BTK822 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.FUBULOIL.HVWRKSHP.BTK822.LT01
BR4_Tags | BTK822LT01_OK_A | Vehicle Workshop PLC | Rack 0 Slot 2 Channel 0 Error | BTK822LT01_OK_A | CAT_P3 | BPL832 | PRIV_ALARMACK | A_P1_FUEL | Rack 0 Slot 2 Channel 0 Error | BTK822LT01_OK_A | C_LOPRI | BPL832 | Class_Equipment | BR4_Cluster1 | BR4.UTILITIES.FUBULOIL.HVWRKSHP.BTK822.LT01
BR4_Tags | BTK823FQ01_Flw_A | HV WrkShp Donax TC50 Bulk Tk | Unloading Wrong Flow Trip | BTK823FQ01_Flw_A | CAT_P3 | HVWORKSHOP1 | PRIV_ALARMACK | A_P1_FUEL | Unloading Wrong Flow | BTK823FQ01_Flw_A | C_LOPRI | BTK823FQ01 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.FUBULOIL.HVWRKSHP.BTK823.FQ01
BR4_Tags | BTK823LT01_Hi_A | HV WrkShp Donax TC50 Bulk Tk | Level High Trip | BTK823LT01_Hi_A | CAT_P3 | HVWORKSHOP1 | PRIV_ALARMACK | A_P1_FUEL | Level High | BTK823LT01_Hi_A | C_LOPRI | BTK823 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.FUBULOIL.HVWRKSHP.BTK823.LT01
BR4_Tags | BTK823LT01_HiHi_A | HV WrkShp Donax TC50 Bulk Tk | Level High High Trip | BTK823LT01_HiHi_A | CAT_P3 | HVWORKSHOP1 | PRIV_ALARMACK | A_P1_FUEL | Level High High | BTK823LT01_HiHi_A | C_LOPRI | BTK823 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.FUBULOIL.HVWRKSHP.BTK823.LT01
BR4_Tags | BTK823LT01_Lo_A | HV WrkShp Donax TC50 Bulk Tk | Level Low Trip | BTK823LT01_Lo_A | CAT_P3 | HVWORKSHOP1 | PRIV_ALARMACK | A_P1_FUEL | Level Low | BTK823LT01_Lo_A | C_LOPRI | BTK823 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.FUBULOIL.HVWRKSHP.BTK823.LT01
BR4_Tags | BTK823LT01_OK_A | Vehicle Workshop PLC | Rack 0 Slot 2 Channel 1 Error | BTK823LT01_OK_A | CAT_P3 | BPL832 | PRIV_ALARMACK | A_P1_FUEL | Rack 0 Slot 2 Channel 1 Error | BTK823LT01_OK_A | C_LOPRI | BPL832 | Class_Equipment | BR4_Cluster1 | BR4.UTILITIES.FUBULOIL.HVWRKSHP.BTK823.LT01
BR4_Tags | BTK824FQ01_Flw_A | HV WrkShp Tellus 100 Bulk Tk | Unloading Wrong Flow Trip | BTK824FQ01_Flw_A | CAT_P3 | HVWORKSHOP1 | PRIV_ALARMACK | A_P1_FUEL | Unloading Wrong Flow | BTK824FQ01_Flw_A | C_LOPRI | BTK824FQ01 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.FUBULOIL.HVWRKSHP.BTK824.FQ01
BR4_Tags | BTK824LT01_Hi_A | HV WrkShp Tellus 100 Bulk Tk | Level High Trip | BTK824LT01_Hi_A | CAT_P3 | HVWORKSHOP1 | PRIV_ALARMACK | A_P1_FUEL | Level High | BTK824LT01_Hi_A | C_LOPRI | BTK824 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.FUBULOIL.HVWRKSHP.BTK824.LT01
BR4_Tags | BTK824LT01_HiHi_A | HV WrkShp Tellus 100 Bulk Tk | Level High High Trip | BTK824LT01_HiHi_A | CAT_P3 | HVWORKSHOP1 | PRIV_ALARMACK | A_P1_FUEL | Level High High | BTK824LT01_HiHi_A | C_LOPRI | BTK824 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.FUBULOIL.HVWRKSHP.BTK824.LT01
BR4_Tags | BTK824LT01_Lo_A | HV WrkShp Tellus 100 Bulk Tk | Level Low Trip | BTK824LT01_Lo_A | CAT_P3 | HVWORKSHOP1 | PRIV_ALARMACK | A_P1_FUEL | Level Low | BTK824LT01_Lo_A | C_LOPRI | BTK824 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.FUBULOIL.HVWRKSHP.BTK824.LT01
BR4_Tags | BTK824LT01_OK_A | Vehicle Workshop PLC | Rack 0 Slot 2 Channel 2 Error | BTK824LT01_OK_A | CAT_P3 | BPL832 | PRIV_ALARMACK | A_P1_FUEL | Rack 0 Slot 2 Channel 2 Error | BTK824LT01_OK_A | C_LOPRI | BPL832 | Class_Equipment | BR4_Cluster1 | BR4.UTILITIES.FUBULOIL.HVWRKSHP.BTK824.LT01
BR4_Tags | BTK825LT01_Hi_A | HV WrkShp Rimula Oil Day Tk | Level High Trip | BTK825LT01_Hi_A | CAT_P3 | HVWORKSHOP1 | PRIV_ALARMACK | A_P1_FUEL | Level High | BTK825LT01_Hi_A | C_LOPRI | BTK825 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.FUBULOIL.HVWRKSHP.BTK825.LT01
BR4_Tags | BTK825LT01_HiHi_A | HV WrkShp Rimula Oil Day Tk | Level High High Trip | BTK825LT01_HiHi_A | CAT_P3 | HVWORKSHOP1 | PRIV_ALARMACK | A_P1_FUEL | Level High High | BTK825LT01_HiHi_A | C_LOPRI | BTK825 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.FUBULOIL.HVWRKSHP.BTK825.LT01
BR4_Tags | BTK825LT01_Lo_A | HV WrkShp Rimula Oil Day Tk | Level Low Trip | BTK825LT01_Lo_A | CAT_P3 | HVWORKSHOP1 | PRIV_ALARMACK | A_P1_FUEL | Level Low | BTK825LT01_Lo_A | C_LOPRI | BTK825 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.FUBULOIL.HVWRKSHP.BTK825.LT01
BR4_Tags | BTK825LT01_OK_A | Vehicle Workshop PLC | Rack 0 Slot 2 Channel 3 Error | BTK825LT01_OK_A | CAT_P3 | BPL832 | PRIV_ALARMACK | A_P1_FUEL | Rack 0 Slot 2 Channel 3 Error | BTK825LT01_OK_A | C_LOPRI | BPL832 | Class_Equipment | BR4_Cluster1 | BR4.UTILITIES.FUBULOIL.HVWRKSHP.BTK825.LT01
BR4_Tags | BTK826LT01_Hi_A | HV WrkShp Tellus 100 Day Tk | Level High Trip | BTK826LT01_Hi_A | CAT_P3 | HVWORKSHOP1 | PRIV_ALARMACK | A_P1_FUEL | Level High | BTK826LT01_Hi_A | C_LOPRI | BTK826 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.FUBULOIL.HVWRKSHP.BTK826.LT01
BR4_Tags | BTK826LT01_HiHi_A | HV WrkShp Tellus 100 Day Tk | Level High High Trip | BTK826LT01_HiHi_A | CAT_P3 | HVWORKSHOP1 | PRIV_ALARMACK | A_P1_FUEL | Level High High | BTK826LT01_HiHi_A | C_LOPRI | BTK826 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.FUBULOIL.HVWRKSHP.BTK826.LT01
BR4_Tags | BTK826LT01_Lo_A | HV WrkShp Tellus 100 Day Tk | Level Low Trip | BTK826LT01_Lo_A | CAT_P3 | HVWORKSHOP1 | PRIV_ALARMACK | A_P1_FUEL | Level Low | BTK826LT01_Lo_A | C_LOPRI | BTK826 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.FUBULOIL.HVWRKSHP.BTK826.LT01
BR4_Tags | BTK826LT01_OK_A | Vehicle Workshop PLC | Rack 0 Slot 3 Channel 0 Error | BTK826LT01_OK_A | CAT_P3 | BPL832 | PRIV_ALARMACK | A_P1_FUEL | Rack 0 Slot 3 Channel 0 Error | BTK826LT01_OK_A | C_LOPRI | BPL832 | Class_Equipment | BR4_Cluster1 | BR4.UTILITIES.FUBULOIL.HVWRKSHP.BTK826.LT01
BR4_Tags | BTK827LT01_Hi_A | HV WrkShp Donax TC50 Day Tk | Level High Trip | BTK827LT01_Hi_A | CAT_P3 | HVWORKSHOP1 | PRIV_ALARMACK | A_P1_FUEL | Level High | BTK827LT01_Hi_A | C_LOPRI | BTK827 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.FUBULOIL.HVWRKSHP.BTK827.LT01
BR4_Tags | BTK827LT01_HiHi_A | HV WrkShp Donax TC50 Day Tk | Level High High Trip | BTK827LT01_HiHi_A | CAT_P3 | HVWORKSHOP1 | PRIV_ALARMACK | A_P1_FUEL | Level High High | BTK827LT01_HiHi_A | C_LOPRI | BTK827 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.FUBULOIL.HVWRKSHP.BTK827.LT01
BR4_Tags | BTK827LT01_Lo_A | HV WrkShp Donax TC50 Day Tk | Level Low Trip | BTK827LT01_Lo_A | CAT_P3 | HVWORKSHOP1 | PRIV_ALARMACK | A_P1_FUEL | Level Low | BTK827LT01_Lo_A | C_LOPRI | BTK827 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.FUBULOIL.HVWRKSHP.BTK827.LT01
BR4_Tags | BTK827LT01_OK_A | Vehicle Workshop PLC | Rack 0 Slot 3 Channel 1 Error | BTK827LT01_OK_A | CAT_P3 | BPL832 | PRIV_ALARMACK | A_P1_FUEL | Rack 0 Slot 3 Channel 1 Error | BTK827LT01_OK_A | C_LOPRI | BPL832 | Class_Equipment | BR4_Cluster1 | BR4.UTILITIES.FUBULOIL.HVWRKSHP.BTK827.LT01
BR4_Tags | BTK827TT01_Lo_A | HV WrkShp Donax TC50 Day Tk | Temperature Low | BTK827TT01_Lo_A | CAT_P3 | HVWORKSHOP1 | PRIV_ALARMACK | A_P1_FUEL | Temperature Low | BTK827TT01_Lo_A | C_LOPRI | BTK827 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.FUBULOIL.HVWRKSHP.BTK827.TT01
BR4_Tags | BTK827TT01_OK_A | Vehicle Workshop PLC | Rack 0 Slot 1 Channel 1 Error | BTK827TT01_OK_A | CAT_P3 | BPL832 | PRIV_ALARMACK | A_P1_FUEL | Rack 0 Slot 1 Channel 1 Error | BTK827TT01_OK_A | C_LOPRI | BPL832 | Class_Equipment | BR4_Cluster1 | BR4.UTILITIES.FUBULOIL.HVWRKSHP.BTK827.TT01
BR4_Tags | BTK827ZS01_A | HV WrkShp Donax TC50 Pump | Recirc Valve Failed to Open or Close Trip | BTK827ZS01_A | CAT_P3 | HVWORKSHOP1 | PRIV_ALARMACK | A_P1_FUEL | Recirc Valve Limit Switch Fault | BTK827ZS01_A | C_LOPRI | BPP840 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.FUBULOIL.HVWRKSHP.BTK827
BR4_Tags | BTK830FQ01_Flw_A | HV WrkShp Tellus 46 Tank | Unloading Wrong Flow Trip | BTK830FQ01_Flw_A | CAT_P3 | HVWORKSHOP1 | PRIV_ALARMACK | A_P1_FUEL | Unloading Wrong Flow | BTK830FQ01_Flw_A | C_LOPRI | BTK830FQ01 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.FUBULOIL.HVWRKSHP.BTK830.FQ01
BR4_Tags | BTK830FQ02_Flw_A | HV WrkShp Waste Coolant Tank | Loading Wrong Flow Trip | BTK830FQ02_Flw_A | CAT_P3 | HVWORKSHOP1 | PRIV_ALARMACK | A_P1_FUEL | Loading Wrong Flow | BTK830FQ02_Flw_A | C_LOPRI | BTK830FQ02 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.FUBULOIL.HVWRKSHP.BTK830.FQ02
BR4_Tags | BTK830LT01_Hi_A | HV WrkShpTellus 46 Tank | Level High Trip | BTK830LT01_Hi_A | CAT_P3 | HVWORKSHOP1 | PRIV_ALARMACK | A_P1_FUEL | Level High | BTK830LT01_Hi_A | C_LOPRI | BTK830 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.FUBULOIL.HVWRKSHP.BTK830.LT01
BR4_Tags | BTK830LT01_HiHi_A | HV WrkShpTellus 46 Tank | Level High High Trip | BTK830LT01_HiHi_A | CAT_P3 | HVWORKSHOP1 | PRIV_ALARMACK | A_P1_FUEL | Level High High | BTK830LT01_HiHi_A | C_LOPRI | BTK830 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.FUBULOIL.HVWRKSHP.BTK830.LT01
BR4_Tags | BTK830LT01_Lo_A | HV WrkShpTellus 46 Tank | Level Low Trip | BTK830LT01_Lo_A | CAT_P3 | HVWORKSHOP1 | PRIV_ALARMACK | A_P1_FUEL | Level Low | BTK830LT01_Lo_A | C_LOPRI | BTK830 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.FUBULOIL.HVWRKSHP.BTK830.LT01
BR4_Tags | BTK830LT01_OK_A | Vehicle Workshop PLC | Rack 0 Slot 3 Channel 2 Error | BTK830LT01_OK_A | CAT_P3 | BPL832 | PRIV_ALARMACK | A_P1_FUEL | Rack 0 Slot 3 Channel 2 Error | BTK830LT01_OK_A | C_LOPRI | BPL832 | Class_Equipment | BR4_Cluster1 | BR4.UTILITIES.FUBULOIL.HVWRKSHP.BTK830.LT01
BR4_Tags | BTK830LT02_Hi_A | HV WrkShp Waste Coolant Tank | Level High Trip | BTK830LT02_Hi_A | CAT_P3 | HVWORKSHOP1 | PRIV_ALARMACK | A_P1_FUEL | Level High | BTK830LT02_Hi_A | C_LOPRI | BTK830 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.FUBULOIL.HVWRKSHP.BTK830.LT02
BR4_Tags | BTK830LT02_HiHi_A | HV WrkShp Waste Coolant Tank | Level High High Trip | BTK830LT02_HiHi_A | CAT_P3 | HVWORKSHOP1 | PRIV_ALARMACK | A_P1_FUEL | Level High High | BTK830LT02_HiHi_A | C_LOPRI | BTK830 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.FUBULOIL.HVWRKSHP.BTK830.LT02
BR4_Tags | BTK830LT02_Lo_A | HV WrkShp Waste Coolant Tank | Level Low Trip | BTK830LT02_Lo_A | CAT_P3 | HVWORKSHOP1 | PRIV_ALARMACK | A_P1_FUEL | Level Low | BTK830LT02_Lo_A | C_LOPRI | BTK830 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.FUBULOIL.HVWRKSHP.BTK830.LT02
BR4_Tags | BTK830LT02_OK_A | Vehicle Workshop PLC | Rack 0 Slot 3 Channel 3 Error | BTK830LT02_OK_A | CAT_P3 | BPL832 | PRIV_ALARMACK | A_P1_FUEL | Rack 0 Slot 3 Channel 3 Error | BTK830LT02_OK_A | C_LOPRI | BPL832 | Class_Equipment | BR4_Cluster1 | BR4.UTILITIES.FUBULOIL.HVWRKSHP.BTK830.LT02
BR4_Tags | BPP812PS01_A | HV WrkShp Tellus 46 Pump | High Pressure Trip | BPP812PS01_A | CAT_P3 | HVWORKSHOP1 | PRIV_ALARMACK | A_P1_FUEL | High Pressure | BPP812PS01_A | C_LOPRI | BPP812 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.FUBULOIL.HVWRKSHP.BPP812
BR4_Tags | BLB802FQ01_Flw_A | HV WrkShp Lube Station 1 | Hyperia 680 Wrong Flow Trip | BLB802FQ01_Flw_A | CAT_P3 | HVWORKSHOP3 | PRIV_ALARMACK | A_P1_FUEL | Hyperia 680 Wrong Flow | BLB802FQ01_Flw_A | C_LOPRI | BLB802 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.FUBULOIL.HVWRKSHP3.BLB802
BR4_Tags | BLB802FQ02_Flw_A | HV WrkShp Lube Station 1 | Donax TC30 Wrong Flow Trip | BLB802FQ02_Flw_A | CAT_P3 | HVWORKSHOP3 | PRIV_ALARMACK | A_P1_FUEL | Donax TC30 Wrong Flow | BLB802FQ02_Flw_A | C_LOPRI | BLB802 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.FUBULOIL.HVWRKSHP3.BLB802
BR4_Tags | BLB802FQ03_Flw_A | HV WrkShp Lube Station 1 | Donax TC50 Wrong Flow Trip | BLB802FQ03_Flw_A | CAT_P3 | HVWORKSHOP3 | PRIV_ALARMACK | A_P1_FUEL | Donax TC50 Wrong Flow | BLB802FQ03_Flw_A | C_LOPRI | BLB802 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.FUBULOIL.HVWRKSHP3.BLB802
BR4_Tags | BLB802FQ04_Flw_A | HV WrkShp Lube Station 1 | Tellus 100 Wrong Flow Trip | BLB802FQ04_Flw_A | CAT_P3 | HVWORKSHOP3 | PRIV_ALARMACK | A_P1_FUEL | Tellus 100 Wrong Flow | BLB802FQ04_Flw_A | C_LOPRI | BLB802 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.FUBULOIL.HVWRKSHP3.BLB802
BR4_Tags | BLB802FQ05_Flw_A | HV WrkShp Lube Station 1 | Rimula 15W40 Wrong Flow Trip | BLB802FQ05_Flw_A | CAT_P3 | HVWORKSHOP3 | PRIV_ALARMACK | A_P1_FUEL | Rimula 15W40 Wrong Flow | BLB802FQ05_Flw_A | C_LOPRI | BLB802 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.FUBULOIL.HVWRKSHP3.BLB802
BR4_Tags | BLB802FQ06_Flw_A | HV WrkShp Lube Station 1 | Tellus 46 Wrong Flow Trip | BLB802FQ06_Flw_A | CAT_P3 | HVWORKSHOP3 | PRIV_ALARMACK | A_P1_FUEL | Tellus 46 Wrong Flow | BLB802FQ06_Flw_A | C_LOPRI | BLB802 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.FUBULOIL.HVWRKSHP3.BLB802
BR4_Tags | BLB802FQ07_Flw_A | HV WrkShp Lube Station 1 | Donax TC10 Wrong Flow Trip | BLB802FQ07_Flw_A | CAT_P3 | HVWORKSHOP3 | PRIV_ALARMACK | A_P1_FUEL | Donax TC10 Wrong Flow | BLB802FQ07_Flw_A | C_LOPRI | BLB802 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.FUBULOIL.HVWRKSHP3.BLB802
BR4_Tags | BLB803FQ01_Flw_A | HV WrkShp Lube Station 2 | Hyperia 680 Wrong Flow Trip | BLB803FQ01_Flw_A | CAT_P3 | HVWORKSHOP3 | PRIV_ALARMACK | A_P1_FUEL | Hyperia 680 Wrong Flow | BLB803FQ01_Flw_A | C_LOPRI | BLB803 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.FUBULOIL.HVWRKSHP3.BLB803
BR4_Tags | BLB803FQ02_Flw_A | HV WrkShp Lube Station 2 | Donax TC30 Wrong Flow Trip | BLB803FQ02_Flw_A | CAT_P3 | HVWORKSHOP3 | PRIV_ALARMACK | A_P1_FUEL | Donax TC30 Wrong Flow | BLB803FQ02_Flw_A | C_LOPRI | BLB803 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.FUBULOIL.HVWRKSHP3.BLB803
BR4_Tags | BLB803FQ03_Flw_A | HV WrkShp Lube Station 2 | Donax TC50 Wrong Flow Trip | BLB803FQ03_Flw_A | CAT_P3 | HVWORKSHOP3 | PRIV_ALARMACK | A_P1_FUEL | Donax TC50 Wrong Flow | BLB803FQ03_Flw_A | C_LOPRI | BLB803 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.FUBULOIL.HVWRKSHP3.BLB803
BR4_Tags | BLB803FQ04_Flw_A | HV WrkShp Lube Station 2 | Tellus 100 Wrong Flow Trip | BLB803FQ04_Flw_A | CAT_P3 | HVWORKSHOP3 | PRIV_ALARMACK | A_P1_FUEL | Tellus 100 Wrong Flow | BLB803FQ04_Flw_A | C_LOPRI | BLB803 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.FUBULOIL.HVWRKSHP3.BLB803
BR4_Tags | BLB803FQ05_Flw_A | HV WrkShp Lube Station 2 | Rimula 15W40 Wrong Flow Trip | BLB803FQ05_Flw_A | CAT_P3 | HVWORKSHOP3 | PRIV_ALARMACK | A_P1_FUEL | Rimula 15W40 Wrong Flow | BLB803FQ05_Flw_A | C_LOPRI | BLB803 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.FUBULOIL.HVWRKSHP3.BLB803
BR4_Tags | BLB803FQ06_Flw_A | HV WrkShp Lube Station 2 | Tellus 46 Wrong Flow Trip | BLB803FQ06_Flw_A | CAT_P3 | HVWORKSHOP3 | PRIV_ALARMACK | A_P1_FUEL | Tellus 46 Wrong Flow | BLB803FQ06_Flw_A | C_LOPRI | BLB803 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.FUBULOIL.HVWRKSHP3.BLB803
BR4_Tags | BLB803FQ07_Flw_A | HV WrkShp Lube Station 2 | Donax TC10 Wrong Flow Trip | BLB803FQ07_Flw_A | CAT_P3 | HVWORKSHOP3 | PRIV_ALARMACK | A_P1_FUEL | Donax TC10 Wrong Flow | BLB803FQ07_Flw_A | C_LOPRI | BLB803 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.FUBULOIL.HVWRKSHP3.BLB803
BR4_Tags | BLB804FQ01_Flw_A | HV WrkShp Lube Station 3 | Hyperia 680 Wrong Flow Trip | BLB804FQ01_Flw_A | CAT_P3 | HVWORKSHOP3 | PRIV_ALARMACK | A_P1_FUEL | Hyperia 680 Wrong Flow | BLB804FQ01_Flw_A | C_LOPRI | BLB804 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.FUBULOIL.HVWRKSHP3.BLB804
BR4_Tags | BLB804FQ02_Flw_A | HV WrkShp Lube Station 3 | Donax TC30 Wrong Flow Trip | BLB804FQ02_Flw_A | CAT_P3 | HVWORKSHOP3 | PRIV_ALARMACK | A_P1_FUEL | Donax TC30 Wrong Flow | BLB804FQ02_Flw_A | C_LOPRI | BLB804 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.FUBULOIL.HVWRKSHP3.BLB804
BR4_Tags | BLB804FQ03_Flw_A | HV WrkShp Lube Station 3 | Donax TC50 Wrong Flow Trip | BLB804FQ03_Flw_A | CAT_P3 | HVWORKSHOP3 | PRIV_ALARMACK | A_P1_FUEL | Donax TC50 Wrong Flow | BLB804FQ03_Flw_A | C_LOPRI | BLB804 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.FUBULOIL.HVWRKSHP3.BLB804
BR4_Tags | BLB804FQ04_Flw_A | HV WrkShp Lube Station 3 | Tellus 100 Wrong Flow Trip | BLB804FQ04_Flw_A | CAT_P3 | HVWORKSHOP3 | PRIV_ALARMACK | A_P1_FUEL | Tellus 100 Wrong Flow | BLB804FQ04_Flw_A | C_LOPRI | BLB804 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.FUBULOIL.HVWRKSHP3.BLB804
BR4_Tags | BLB804FQ05_Flw_A | HV WrkShp Lube Station 3 | Rimula 15W40 Wrong Flow Trip | BLB804FQ05_Flw_A | CAT_P3 | HVWORKSHOP3 | PRIV_ALARMACK | A_P1_FUEL | Rimula 15W40 Wrong Flow | BLB804FQ05_Flw_A | C_LOPRI | BLB804 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.FUBULOIL.HVWRKSHP3.BLB804
BR4_Tags | BLB804FQ06_Flw_A | HV WrkShp Lube Station 3 | Tellus 46 Wrong Flow Trip | BLB804FQ06_Flw_A | CAT_P3 | HVWORKSHOP3 | PRIV_ALARMACK | A_P1_FUEL | Tellus 46 Wrong Flow | BLB804FQ06_Flw_A | C_LOPRI | BLB804 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.FUBULOIL.HVWRKSHP3.BLB804
BR4_Tags | BLB804FQ07_Flw_A | HV WrkShp Lube Station 3 | Donax TC10 Wrong Flow Trip | BLB804FQ07_Flw_A | CAT_P3 | HVWORKSHOP3 | PRIV_ALARMACK | A_P1_FUEL | Donax TC10 Wrong Flow | BLB804FQ07_Flw_A | C_LOPRI | BLB804 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.FUBULOIL.HVWRKSHP3.BLB804
BR4_Tags | BLB805FQ01_Flw_A | LV WrkShp Lube Station 1 | Gear Oil (140) Wrong Flow Trip | BLB805FQ01_Flw_A | CAT_P3 | LVWORKSHOP | PRIV_ALARMACK | A_P1_FUEL | Gear Oil (140) Wrong Flow | BLB805FQ01_Flw_A | C_LOPRI | BLB805 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.FUBULOIL.LVWRKSHP.BLB805
BR4_Tags | BLB805FQ02_Flw_A | LV WrkShp Lube Station 1 | Gear Oil (90) Wrong Flow Trip | BLB805FQ02_Flw_A | CAT_P3 | LVWORKSHOP | PRIV_ALARMACK | A_P1_FUEL | Gear Oil (90) Wrong Flow | BLB805FQ02_Flw_A | C_LOPRI | BLB805 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.FUBULOIL.LVWRKSHP.BLB805
BR4_Tags | BLB805FQ03_Flw_A | LV WrkShp Lube Station 1 | Engine Oil Wrong Flow Trip | BLB805FQ03_Flw_A | CAT_P3 | LVWORKSHOP | PRIV_ALARMACK | A_P1_FUEL | Engine Oil Wrong Flow | BLB805FQ03_Flw_A | C_LOPRI | BLB805 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.FUBULOIL.LVWRKSHP.BLB805
BR4_Tags | BPP935PS01_A | HV WrkShp 15W40 Oil Pump | Filter Blocked | BPP935PS01_A | CAT_P3 | LVWORKSHOP | PRIV_ALARMACK | A_P1_FUEL | Filter High Pressure | BPP935PS01_A | C_LOPRI | BPP935 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.FUBULOIL.LVWRKSHP.BPP935
BR4_Tags | BPP936PS01_A | LV WrkShp Gear Oil 90 Pump | Filter Blocked | BPP936PS01_A | CAT_P3 | LVWORKSHOP | PRIV_ALARMACK | A_P1_FUEL | Filter High Pressure | BPP936PS01_A | C_LOPRI | BPP936 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.FUBULOIL.LVWRKSHP.BPP936
BR4_Tags | BPP937PS01_A | LV WrkShp Gear Oil 140 Pump | Filter Blocked | BPP937PS01_A | CAT_P3 | LVWORKSHOP | PRIV_ALARMACK | A_P1_FUEL | Filter High Pressure | BPP937PS01_A | C_LOPRI | BPP937 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.FUBULOIL.LVWRKSHP.BPP937
BR4_Tags | BPP934PS01_A | LV WrkShp LV Coolant Pump | Filter Blocked | BPP934PS01_A | CAT_P3 | LVWORKSHOP | PRIV_ALARMACK | A_P1_FUEL | Filter High Pressure | BPP934PS01_A | C_LOPRI | BPP934 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.FUBULOIL.LVWRKSHP.BPP934
BR4_Tags | BLB806FQ01_Flw_A | LV WrkShp Lube Station 2 | Gear Oil (140) Wrong Flow Trip | BLB806FQ01_Flw_A | CAT_P3 | LVWORKSHOP | PRIV_ALARMACK | A_P1_FUEL | Gear Oil (140) Wrong Flow | BLB806FQ01_Flw_A | C_LOPRI | BLB806 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.FUBULOIL.LVWRKSHP.BLB806
BR4_Tags | BLB806FQ02_Flw_A | LV WrkShp Lube Station 2 | Gear Oil (90) Wrong Flow Trip | BLB806FQ02_Flw_A | CAT_P3 | LVWORKSHOP | PRIV_ALARMACK | A_P1_FUEL | Gear Oil (90) Wrong Flow | BLB806FQ02_Flw_A | C_LOPRI | BLB806 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.FUBULOIL.LVWRKSHP.BLB806
BR4_Tags | BLB806FQ03_Flw_A | LV WrkShp Lube Station 2 | Engine Oil Wrong Flow Trip | BLB806FQ03_Flw_A | CAT_P3 | LVWORKSHOP | PRIV_ALARMACK | A_P1_FUEL | Engine Oil Wrong Flow | BLB806FQ03_Flw_A | C_LOPRI | BLB806 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.FUBULOIL.LVWRKSHP.BLB806
BR4_Tags | BPP930_NoFlw_A | HV WrkShp Hyperia 680 Pump | No Flow Trip | BPP930_NoFlw_A | CAT_P3 | HVWORKSHOP3 | PRIV_ALARMACK | A_P1_FUEL | No Flow | BPP930_NoFlw_A | C_LOPRI | BPP930 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.FUBULOIL.HVWRKSHP3.BPP930
BR4_Tags | BPP926_NoFlw_A | HV WrkShp Donax TC30 Pump | No Flow Trip | BPP926_NoFlw_A | CAT_P3 | HVWORKSHOP2 | PRIV_ALARMACK | A_P1_FUEL | No Flow | BPP926_NoFlw_A | C_LOPRI | BPP926 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.FUBULOIL.HVWRKSHP2.BPP926
BR4_Tags | BPP840_NoFlw_A | HV WrkShp Donax TC50 Pump | No Flow Trip | BPP840_NoFlw_A | CAT_P3 | HVWORKSHOP1 | PRIV_ALARMACK | A_P1_FUEL | No Flow | BPP840_NoFlw_A | C_LOPRI | BPP840 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.FUBULOIL.HVWRKSHP.BPP840
BR4_Tags | BPP841_NoFlw_A | HV WrkShp Tellus 100 Pump | No Flow Trip | BPP841_NoFlw_A | CAT_P3 | HVWORKSHOP1 | PRIV_ALARMACK | A_P1_FUEL | No Flow | BPP841_NoFlw_A | C_LOPRI | BPP841 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.FUBULOIL.HVWRKSHP.BPP841
BR4_Tags | BPP842_NoFlw_A | HV WrkShp Rimula Oil Pump | No Flow Trip | BPP842_NoFlw_A | CAT_P3 | HVWORKSHOP1 | PRIV_ALARMACK | A_P1_FUEL | No Flow | BPP842_NoFlw_A | C_LOPRI | BPP842 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.FUBULOIL.HVWRKSHP.BPP842
BR4_Tags | BPP812_NoFlw_A | HV WrkShp Tellus 46 Pump | No Flow Trip | BPP812_NoFlw_A | CAT_P3 | HVWORKSHOP1 | PRIV_ALARMACK | A_P1_FUEL | No Flow | BPP812_NoFlw_A | C_LOPRI | BPP812 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.FUBULOIL.HVWRKSHP.BPP812
BR4_Tags | BPP931_NoFlw_A | HV WrkShp Donax TC10 Pump | No Flow Trip | BPP931_NoFlw_A | CAT_P3 | HVWORKSHOP3 | PRIV_ALARMACK | A_P1_FUEL | No Flow | BPP931_NoFlw_A | C_LOPRI | BPP931 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.FUBULOIL.HVWRKSHP3.BPP931
BR4_Tags | BPP937_NoFlw_A | LV WrkShp Gear Oil 140 Pump | No Flow Trip | BPP937_NoFlw_A | CAT_P3 | LVWORKSHOP | PRIV_ALARMACK | A_P1_FUEL | No Flow | BPP937_NoFlw_A | C_LOPRI | BPP937 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.FUBULOIL.LVWRKSHP.BPP937
BR4_Tags | BPP936_NoFlw_A | LV WrkShp Gear Oil 90 Pump | No Flow Trip | BPP936_NoFlw_A | CAT_P3 | LVWORKSHOP | PRIV_ALARMACK | A_P1_FUEL | No Flow | BPP936_NoFlw_A | C_LOPRI | BPP936 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.FUBULOIL.LVWRKSHP.BPP936
BR4_Tags | BPP935_NoFlw_A | HV WrkShp 15W40 Oil Pump | No Flow Trip | BPP935_NoFlw_A | CAT_P3 | LVWORKSHOP | PRIV_ALARMACK | A_P1_FUEL | No Flow | BPP935_NoFlw_A | C_LOPRI | BPP935 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.FUBULOIL.LVWRKSHP.BPP935
BR4_Tags | BPL832PN01LOS01_A | Vehicle Workshop PLC | Lock Off Stop Trip | BPL832PN01LOS01_A | CAT_P1 | BPL832 | PRIV_ALARMACK | A_P1_FUEL | Lock Off Stop Pressed | BPL832PN01LOS01_A | C_LOPRI | BPL832 | Class_Process | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL832
BR4_Tags | B0832LTPN01LOS07_A | HV WrkShp Lube Truck Station | Lock Off Stop Trip | B0832LTPN01LOS07_A | CAT_P1 | HVWORKSHOP2 | PRIV_ALARMACK | A_P1_FUEL | Lock Off Stop Pressed | B0832LTPN01LOS07_A | C_LOPRI | BLB801 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.FUBULOIL
BR4_Tags | B0832HVPN01LOS02_A | HV WrkShp Lube Station 1 | Lock Off Stop Trip | B0832HVPN01LOS02_A | CAT_P1 | HVWORKSHOP3 | PRIV_ALARMACK | A_P1_FUEL | Lock Off Stop Pressed | B0832HVPN01LOS02_A | C_LOPRI | BLB802 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.FUBULOIL
BR4_Tags | B0832HVPN02LOS03_A | HV WrkShp Lube Station 2 | Lock Off Stop Trip | B0832HVPN02LOS03_A | CAT_P1 | HVWORKSHOP3 | PRIV_ALARMACK | A_P1_FUEL | Lock Off Stop Pressed | B0832HVPN02LOS03_A | C_LOPRI | BLB803 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.FUBULOIL
BR4_Tags | B0832HVPN03LOS04_A | HV WrkShp Lube Station 3 | Lock Off Stop Trip | B0832HVPN03LOS04_A | CAT_P1 | HVWORKSHOP3 | PRIV_ALARMACK | A_P1_FUEL | Lock Off Stop Pressed | B0832HVPN03LOS04_A | C_LOPRI | BLB804 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.FUBULOIL
BR4_Tags | B0832LVPN01LOS05_A | LV WrkShp Lube Station 1 | Lock Off Stop Trip | B0832LVPN01LOS05_A | CAT_P1 | LVWORKSHOP | PRIV_ALARMACK | A_P1_FUEL | Lock Off Stop Pressed | B0832LVPN01LOS05_A | C_LOPRI | BLB805 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.FUBULOIL
BR4_Tags | B0832LVPN02LOS06_A | LV WrkShp Lube Station 2 | Lock Off Stop Trip | B0832LVPN02LOS06_A | CAT_P1 | LVWORKSHOP | PRIV_ALARMACK | A_P1_FUEL | Lock Off Stop Pressed | B0832LVPN02LOS06_A | C_LOPRI | BLB806 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.FUBULOIL
BR4_Tags | BPL851_CPUEthModLinkOK_A | Loco Refuelling PLC | CPU Module Ethernet Link Fault | BPL851_CPUEthModLinkOK_A | CAT_P2 | BPL851 | PRIV_ALARMACK | A_P1_FUEL | CPU Module Ethernet Link Fault | BPL851_CPUEthModLinkOK_A | C_HIPRI | BPL851 | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL851
BR4_Tags | BPL851_CPUEthModRnng_A | Loco Refuelling PLC | CPU Module Ethernet Port Not Running Fault | BPL851_CPUEthModRnng_A | CAT_P2 | BPL851 | PRIV_ALARMACK | A_P1_FUEL | CPU Module Ethernet Port Not Running Fault | BPL851_CPUEthModRnng_A | C_HIPRI | BPL851 | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL851
BR4_Tags | BPL851_NOE1LinkOK_A | Loco Refuelling PLC | NOE1 Ethernet Link Status Fault | BPL851_NOE1LinkOK_A | CAT_P2 | BPL851 | PRIV_ALARMACK | A_P1_FUEL | NOE1 Ethernet Link Status Fault | BPL851_NOE1LinkOK_A | C_HIPRI | BPL851 | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL851
BR4_Tags | BPL851_NOE1Rnng_A | Loco Refuelling PLC | NOE1 Ethernet Module Not Running | BPL851_NOE1Rnng_A | CAT_P2 | BPL851 | PRIV_ALARMACK | A_P1_FUEL | NOE1 Ethernet Module Not Running | BPL851_NOE1Rnng_A | C_HIPRI | BPL851 | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL851 | Slot1_A
BR4_Tags | BPL851_R0S2OK_A | Loco Refuelling PLC | Rack 0 Slot 2 Module Fault | BPL851_R0S2OK_A | CAT_P3 | BPL851 | PRIV_ALARMACK | A_P1_FUEL | Rack 0 Slot 2 Module Fault | BPL851_R0S2OK_A | C_LOPRI | BPL851 | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL851 | Slot2_A
BR4_Tags | BPL851_R0S3OK_A | Loco Refuelling PLC | Rack 0 Slot 3 Module Fault | BPL851_R0S3OK_A | CAT_P3 | BPL851 | PRIV_ALARMACK | A_P1_FUEL | Rack 0 Slot 3 Module Fault | BPL851_R0S3OK_A | C_LOPRI | BPL851 | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL851 | Slot3_A
BR4_Tags | BPL851_R0S4OK_A | Loco Refuelling PLC | Rack 0 Slot 4 Module Fault | BPL851_R0S4OK_A | CAT_P3 | BPL851 | PRIV_ALARMACK | A_P1_FUEL | Rack 0 Slot 4 Module Fault | BPL851_R0S4OK_A | C_LOPRI | BPL851 | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL851 | Slot4_A
BR4_Tags | BPL851_R0S5OK_A | Loco Refuelling PLC | Rack 0 Slot 5 Module Fault | BPL851_R0S5OK_A | CAT_P3 | BPL851 | PRIV_ALARMACK | A_P1_FUEL | Rack 0 Slot 5 Module Fault | BPL851_R0S5OK_A | C_LOPRI | BPL851 | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL851 | Slot5_A
BR4_Tags | BPL851_R0S6OK_A | Loco Refuelling PLC | Rack 0 Slot 6 Module Fault | BPL851_R0S6OK_A | CAT_P3 | BPL851 | PRIV_ALARMACK | A_P1_FUEL | Rack 0 Slot 6 Module Fault | BPL851_R0S6OK_A | C_LOPRI | BPL851 | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL851 | Slot6_A
BR4_Tags | BPL851_R0S7OK_A | Loco Refuelling PLC | Rack 0 Slot 7 Module Fault | BPL851_R0S7OK_A | CAT_P3 | BPL851 | PRIV_ALARMACK | A_P1_FUEL | Rack 0 Slot 7 Module Fault | BPL851_R0S7OK_A | C_LOPRI | BPL851 | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL851 | Slot7_A
BR4_Tags | BPL851_R1S0OK_A | Loco Refuelling PLC | Rack 1 Slot 0 Module Fault | BPL851_R1S0OK_A | CAT_P3 | BPL851 | PRIV_ALARMACK | A_P1_FUEL | Rack 1 Slot 0 Module Fault | BPL851_R1S0OK_A | C_LOPRI | BPL851 | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL851.Rack1 | Slot0_A
BR4_Tags | BPL851_R1S1OK_A | Loco Refuelling PLC | Rack 1 Slot 1 Module Fault | BPL851_R1S1OK_A | CAT_P3 | BPL851 | PRIV_ALARMACK | A_P1_FUEL | Rack 1 Slot 1 Module Fault | BPL851_R1S1OK_A | C_LOPRI | BPL851 | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL851.Rack1 | Slot1_A
BR4_Tags | BPL851_R1S2OK_A | Loco Refuelling PLC | Rack 1 Slot 2 Module Fault | BPL851_R1S2OK_A | CAT_P3 | BPL851 | PRIV_ALARMACK | A_P1_FUEL | Rack 1 Slot 2 Module Fault | BPL851_R1S2OK_A | C_LOPRI | BPL851 | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL851.Rack1 | Slot2_A
BR4_Tags | BPL851_R1S3OK_A | Loco Refuelling PLC | Rack 1 Slot 3 Module Fault | BPL851_R1S3OK_A | CAT_P3 | BPL851 | PRIV_ALARMACK | A_P1_FUEL | Rack 1 Slot 3 Module Fault | BPL851_R1S3OK_A | C_LOPRI | BPL851 | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL851.Rack1 | Slot3_A
BR4_Tags | BPL851_R1S4OK_A | Loco Refuelling PLC | Rack 1 Slot 4 Module Fault | BPL851_R1S4OK_A | CAT_P3 | BPL851 | PRIV_ALARMACK | A_P1_FUEL | Rack 1 Slot 4 Module Fault | BPL851_R1S4OK_A | C_LOPRI | BPL851 | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL851.Rack1 | Slot4_A
BR4_Tags | BPL851_R1S5OK_A | Loco Refuelling PLC | Rack 1 Slot 5 Module Fault | BPL851_R1S5OK_A | CAT_P3 | BPL851 | PRIV_ALARMACK | A_P1_FUEL | Rack 1 Slot 5 Module Fault | BPL851_R1S5OK_A | C_LOPRI | BPL851 | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL851.Rack1 | Slot5_A
BR4_Tags | BPL851_R1S6OK_A | Loco Refuelling PLC | Rack 1 Slot 6 Module Fault | BPL851_R1S6OK_A | CAT_P3 | BPL851 | PRIV_ALARMACK | A_P1_FUEL | Rack 1 Slot 6 Module Fault | BPL851_R1S6OK_A | C_LOPRI | BPL851 | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL851.Rack1 | Slot6_A
BR4_Tags | BPL851_R1S7OK_A | Loco Refuelling PLC | Rack 1 Slot 7 Module Fault | BPL851_R1S7OK_A | CAT_P3 | BPL851 | PRIV_ALARMACK | A_P1_FUEL | Rack 1 Slot 7 Module Fault | BPL851_R1S7OK_A | C_LOPRI | BPL851 | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL851.Rack1 | Slot7_A
BR4_Tags | BPL851_R1S2Ch0OK_A | Loco Refuelling PLC | Rack 1 Slot 2 Channel 0 Fault | BPL851_R1S2Ch0OK_A | CAT_P3 | BPL851 | PRIV_ALARMACK | A_P1_FUEL | Rack 1 Slot 2 Channel 0 Fault | BPL851_R1S2Ch0OK_A | C_LOPRI | BPL851 | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL851.Rack1
BR4_Tags | BPL851_R1S2Ch0ROVF_E | Loco Refuelling PLC | Rack 1 Slot 2 Channel 0 Overflow Error | BPL851_R1S2Ch0ROVF_E | CAT_P4 | BPL851 | PRIV_ALARMACK | A_P1_FUEL | Rack 1 Slot 2 Channel 0 Overflow Error | BPL851_R1S2Ch0ROVF_E | C_EVENT | BPL851 | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL851.Rack1
BR4_Tags | BPL851_R1S2Ch0RUNF_E | Loco Refuelling PLC | Rack 1 Slot 2 Channel 0 Underflow Error | BPL851_R1S2Ch0RUNF_E | CAT_P4 | BPL851 | PRIV_ALARMACK | A_P1_FUEL | Rack 1 Slot 2 Channel 0 Underflow Error | BPL851_R1S2Ch0RUNF_E | C_EVENT | BPL851 | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL851.Rack1
BR4_Tags | BPL851_R1S2Ch1OK_A | Loco Refuelling PLC | Rack 1 Slot 2 Channel 1 Fault | BPL851_R1S2Ch1OK_A | CAT_P3 | BPL851 | PRIV_ALARMACK | A_P1_FUEL | Rack 1 Slot 2 Channel 1 Fault | BPL851_R1S2Ch1OK_A | C_LOPRI | BPL851 | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL851.Rack1
BR4_Tags | BPL851_R1S2Ch1ROVF_E | Loco Refuelling PLC | Rack 1 Slot 2 Channel 1 Overflow Error | BPL851_R1S2Ch1ROVF_E | CAT_P4 | BPL851 | PRIV_ALARMACK | A_P1_FUEL | Rack 1 Slot 2 Channel 1 Overflow Error | BPL851_R1S2Ch1ROVF_E | C_EVENT | BPL851 | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL851.Rack1
BR4_Tags | BPL851_R1S2Ch1RUNF_E | Loco Refuelling PLC | Rack 1 Slot 2 Channel 1 Underflow Error | BPL851_R1S2Ch1RUNF_E | CAT_P4 | BPL851 | PRIV_ALARMACK | A_P1_FUEL | Rack 1 Slot 2 Channel 1 Underflow Error | BPL851_R1S2Ch1RUNF_E | C_EVENT | BPL851 | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL851.Rack1
BR4_Tags | BPL851_R1S2Ch2OK_A | Loco Refuelling PLC | Rack 1 Slot 2 Channel 2 Fault | BPL851_R1S2Ch2OK_A | CAT_P3 | BPL851 | PRIV_ALARMACK | A_P1_FUEL | Rack 1 Slot 2 Channel 2 Fault | BPL851_R1S2Ch2OK_A | C_LOPRI | BPL851 | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL851.Rack1
BR4_Tags | BPL851_R1S2Ch2ROVF_E | Loco Refuelling PLC | Rack 1 Slot 2 Channel 2 Overflow Error | BPL851_R1S2Ch2ROVF_E | CAT_P4 | BPL851 | PRIV_ALARMACK | A_P1_FUEL | Rack 1 Slot 2 Channel 2 Overflow Error | BPL851_R1S2Ch2ROVF_E | C_EVENT | BPL851 | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL851.Rack1
BR4_Tags | BPL851_R1S2Ch2RUNF_E | Loco Refuelling PLC | Rack 1 Slot 2 Channel 2 Underflow Error | BPL851_R1S2Ch2RUNF_E | CAT_P4 | BPL851 | PRIV_ALARMACK | A_P1_FUEL | Rack 1 Slot 2 Channel 2 Underflow Error | BPL851_R1S2Ch2RUNF_E | C_EVENT | BPL851 | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL851.Rack1
BR4_Tags | BPL851_R1S2Ch3OK_A | Loco Refuelling PLC | Rack 1 Slot 2 Channel 3 Fault | BPL851_R1S2Ch3OK_A | CAT_P3 | BPL851 | PRIV_ALARMACK | A_P1_FUEL | Rack 1 Slot 2 Channel 3 Fault | BPL851_R1S2Ch3OK_A | C_LOPRI | BPL851 | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL851.Rack1
BR4_Tags | BPL851_R1S2Ch3ROVF_E | Loco Refuelling PLC | Rack 1 Slot 2 Channel 3 Overflow Error | BPL851_R1S2Ch3ROVF_E | CAT_P4 | BPL851 | PRIV_ALARMACK | A_P1_FUEL | Rack 1 Slot 2 Channel 3 Overflow Error | BPL851_R1S2Ch3ROVF_E | C_EVENT | BPL851 | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL851.Rack1
BR4_Tags | BPL851_R1S2Ch3RUNF_E | Loco Refuelling PLC | Rack 1 Slot 2 Channel 3 Underflow Error | BPL851_R1S2Ch3RUNF_E | CAT_P4 | BPL851 | PRIV_ALARMACK | A_P1_FUEL | Rack 1 Slot 2 Channel 3 Underflow Error | BPL851_R1S2Ch3RUNF_E | C_EVENT | BPL851 | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL851.Rack1
BR4_Tags | BPL851_R1S3Ch0OK_A | Loco Refuelling PLC | Rack 1 Slot 3 Channel 0 Fault | BPL851_R1S3Ch0OK_A | CAT_P3 | BPL851 | PRIV_ALARMACK | A_P1_FUEL | Rack 1 Slot 3 Channel 0 Fault | BPL851_R1S3Ch0OK_A | C_LOPRI | BPL851 | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL851.Rack1
BR4_Tags | BPL851_R1S3Ch0ROVF_E | Loco Refuelling PLC | Rack 1 Slot 3 Channel 0 Overflow Error | BPL851_R1S3Ch0ROVF_E | CAT_P4 | BPL851 | PRIV_ALARMACK | A_P1_FUEL | Rack 1 Slot 3 Channel 0 Overflow Error | BPL851_R1S3Ch0ROVF_E | C_EVENT | BPL851 | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL851.Rack1
BR4_Tags | BPL851_R1S3Ch0RUNF_E | Loco Refuelling PLC | Rack 1 Slot 3 Channel 0 Underflow Error | BPL851_R1S3Ch0RUNF_E | CAT_P4 | BPL851 | PRIV_ALARMACK | A_P1_FUEL | Rack 1 Slot 3 Channel 0 Underflow Error | BPL851_R1S3Ch0RUNF_E | C_EVENT | BPL851 | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL851.Rack1
BR4_Tags | BPL851_R1S3Ch1OK_A | Loco Refuelling PLC | Rack 1 Slot 3 Channel 1 Fault | BPL851_R1S3Ch1OK_A | CAT_P3 | BPL851 | PRIV_ALARMACK | A_P1_FUEL | Rack 1 Slot 3 Channel 1 Fault | BPL851_R1S3Ch1OK_A | C_LOPRI | BPL851 | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL851.Rack1
BR4_Tags | BPL851_R1S3Ch1ROVF_E | Loco Refuelling PLC | Rack 1 Slot 3 Channel 1 Overflow Error | BPL851_R1S3Ch1ROVF_E | CAT_P4 | BPL851 | PRIV_ALARMACK | A_P1_FUEL | Rack 1 Slot 3 Channel 1 Overflow Error | BPL851_R1S3Ch1ROVF_E | C_EVENT | BPL851 | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL851.Rack1
BR4_Tags | BPL851_R1S3Ch1RUNF_E | Loco Refuelling PLC | Rack 1 Slot 3 Channel 1 Underflow Error | BPL851_R1S3Ch1RUNF_E | CAT_P4 | BPL851 | PRIV_ALARMACK | A_P1_FUEL | Rack 1 Slot 3 Channel 1 Underflow Error | BPL851_R1S3Ch1RUNF_E | C_EVENT | BPL851 | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL851.Rack1
BR4_Tags | BPL851_R1S3Ch2OK_A | Loco Refuelling PLC | Rack 1 Slot 3 Channel 2 Fault | BPL851_R1S3Ch2OK_A | CAT_P3 | BPL851 | PRIV_ALARMACK | A_P1_FUEL | Rack 1 Slot 3 Channel 2 Fault | BPL851_R1S3Ch2OK_A | C_LOPRI | BPL851 | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL851.Rack1
BR4_Tags | BPL851_R1S3Ch2ROVF_E | Loco Refuelling PLC | Rack 1 Slot 3 Channel 2 Overflow Error | BPL851_R1S3Ch2ROVF_E | CAT_P4 | BPL851 | PRIV_ALARMACK | A_P1_FUEL | Rack 1 Slot 3 Channel 2 Overflow Error | BPL851_R1S3Ch2ROVF_E | C_EVENT | BPL851 | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL851.Rack1
BR4_Tags | BPL851_R1S3Ch2RUNF_E | Loco Refuelling PLC | Rack 1 Slot 3 Channel 2 Underflow Error | BPL851_R1S3Ch2RUNF_E | CAT_P4 | BPL851 | PRIV_ALARMACK | A_P1_FUEL | Rack 1 Slot 3 Channel 2 Underflow Error | BPL851_R1S3Ch2RUNF_E | C_EVENT | BPL851 | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL851.Rack1
BR4_Tags | BPL851_R1S3Ch3OK_A | Loco Refuelling PLC | Rack 1 Slot 3 Channel 3 Fault | BPL851_R1S3Ch3OK_A | CAT_P3 | BPL851 | PRIV_ALARMACK | A_P1_FUEL | Rack 1 Slot 3 Channel 3 Fault | BPL851_R1S3Ch3OK_A | C_LOPRI | BPL851 | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL851.Rack1
BR4_Tags | BPL851_R1S3Ch3ROVF_E | Loco Refuelling PLC | Rack 1 Slot 3 Channel 3 Overflow Error | BPL851_R1S3Ch3ROVF_E | CAT_P4 | BPL851 | PRIV_ALARMACK | A_P1_FUEL | Rack 1 Slot 3 Channel 3 Overflow Error | BPL851_R1S3Ch3ROVF_E | C_EVENT | BPL851 | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL851.Rack1
BR4_Tags | BPL851_R1S3Ch3RUNF_E | Loco Refuelling PLC | Rack 1 Slot 3 Channel 3 Underflow Error | BPL851_R1S3Ch3RUNF_E | CAT_P4 | BPL851 | PRIV_ALARMACK | A_P1_FUEL | Rack 1 Slot 3 Channel 3 Underflow Error | BPL851_R1S3Ch3RUNF_E | C_EVENT | BPL851 | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL851.Rack1
BR4_Tags | BPL851_R1S4Ch0OK_A | Loco Refuelling PLC | Rack 1 Slot 4 Channel 0 Fault | BPL851_R1S4Ch0OK_A | CAT_P3 | BPL851 | PRIV_ALARMACK | A_P1_FUEL | Rack 1 Slot 4 Channel 0 Fault | BPL851_R1S4Ch0OK_A | C_LOPRI | BPL851 | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL851.Rack1
BR4_Tags | BPL851_R1S4Ch0ROVF_E | Loco Refuelling PLC | Rack 1 Slot 4 Channel 0 Overflow Error | BPL851_R1S4Ch0ROVF_E | CAT_P4 | BPL851 | PRIV_ALARMACK | A_P1_FUEL | Rack 1 Slot 4 Channel 0 Overflow Error | BPL851_R1S4Ch0ROVF_E | C_EVENT | BPL851 | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL851.Rack1
BR4_Tags | BPL851_R1S4Ch0RUNF_E | Loco Refuelling PLC | Rack 1 Slot 4 Channel 0 Underflow Error | BPL851_R1S4Ch0RUNF_E | CAT_P4 | BPL851 | PRIV_ALARMACK | A_P1_FUEL | Rack 1 Slot 4 Channel 0 Underflow Error | BPL851_R1S4Ch0RUNF_E | C_EVENT | BPL851 | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL851.Rack1
BR4_Tags | BPL851_R1S4Ch1OK_A | Loco Refuelling PLC | Rack 1 Slot 4 Channel 1 Fault | BPL851_R1S4Ch1OK_A | CAT_P3 | BPL851 | PRIV_ALARMACK | A_P1_FUEL | Rack 1 Slot 4 Channel 1 Fault | BPL851_R1S4Ch1OK_A | C_LOPRI | BPL851 | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL851.Rack1
BR4_Tags | BPL851_R1S4Ch1ROVF_E | Loco Refuelling PLC | Rack 1 Slot 4 Channel 1 Overflow Error | BPL851_R1S4Ch1ROVF_E | CAT_P4 | BPL851 | PRIV_ALARMACK | A_P1_FUEL | Rack 1 Slot 4 Channel 1 Overflow Error | BPL851_R1S4Ch1ROVF_E | C_EVENT | BPL851 | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL851.Rack1
BR4_Tags | BPL851_R1S4Ch1RUNF_E | Loco Refuelling PLC | Rack 1 Slot 4 Channel 1 Underflow Error | BPL851_R1S4Ch1RUNF_E | CAT_P4 | BPL851 | PRIV_ALARMACK | A_P1_FUEL | Rack 1 Slot 4 Channel 1 Underflow Error | BPL851_R1S4Ch1RUNF_E | C_EVENT | BPL851 | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL851.Rack1
BR4_Tags | BPL851_R1S4Ch2OK_A | Loco Refuelling PLC | Rack 1 Slot 4 Channel 2 Fault | BPL851_R1S4Ch2OK_A | CAT_P3 | BPL851 | PRIV_ALARMACK | A_P1_FUEL | Rack 1 Slot 4 Channel 2 Fault | BPL851_R1S4Ch2OK_A | C_LOPRI | BPL851 | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL851.Rack1
BR4_Tags | BPL851_R1S4Ch2ROVF_E | Loco Refuelling PLC | Rack 1 Slot 4 Channel 2 Overflow Error | BPL851_R1S4Ch2ROVF_E | CAT_P4 | BPL851 | PRIV_ALARMACK | A_P1_FUEL | Rack 1 Slot 4 Channel 2 Overflow Error | BPL851_R1S4Ch2ROVF_E | C_EVENT | BPL851 | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL851.Rack1
BR4_Tags | BPL851_R1S4Ch2RUNF_E | Loco Refuelling PLC | Rack 1 Slot 4 Channel 2 Underflow Error | BPL851_R1S4Ch2RUNF_E | CAT_P4 | BPL851 | PRIV_ALARMACK | A_P1_FUEL | Rack 1 Slot 4 Channel 2 Underflow Error | BPL851_R1S4Ch2RUNF_E | C_EVENT | BPL851 | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL851.Rack1
BR4_Tags | BPL851_R1S4Ch3OK_A | Loco Refuelling PLC | Rack 1 Slot 4 Channel 3 Fault | BPL851_R1S4Ch3OK_A | CAT_P3 | BPL851 | PRIV_ALARMACK | A_P1_FUEL | Rack 1 Slot 4 Channel 3 Fault | BPL851_R1S4Ch3OK_A | C_LOPRI | BPL851 | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL851.Rack1
BR4_Tags | BPL851_R1S4Ch3ROVF_E | Loco Refuelling PLC | Rack 1 Slot 4 Channel 3 Overflow Error | BPL851_R1S4Ch3ROVF_E | CAT_P4 | BPL851 | PRIV_ALARMACK | A_P1_FUEL | Rack 1 Slot 4 Channel 3 Overflow Error | BPL851_R1S4Ch3ROVF_E | C_EVENT | BPL851 | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL851.Rack1
BR4_Tags | BPL851_R1S4Ch3RUNF_E | Loco Refuelling PLC | Rack 1 Slot 4 Channel 3 Underflow Error | BPL851_R1S4Ch3RUNF_E | CAT_P4 | BPL851 | PRIV_ALARMACK | A_P1_FUEL | Rack 1 Slot 4 Channel 3 Underflow Error | BPL851_R1S4Ch3RUNF_E | C_EVENT | BPL851 | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL851.Rack1
BR4_Tags | BPL851_R1S5Ch0OK_A | Loco Refuelling PLC | Rack 1 Slot 5 Channel 0 Fault | BPL851_R1S5Ch0OK_A | CAT_P3 | BPL851 | PRIV_ALARMACK | A_P1_FUEL | Rack 1 Slot 5 Channel 0 Fault | BPL851_R1S5Ch0OK_A | C_LOPRI | BPL851 | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL851.Rack1
BR4_Tags | BPL851_R1S5Ch0ROVF_E | Loco Refuelling PLC | Rack 1 Slot 5 Channel 0 Overflow Error | BPL851_R1S5Ch0ROVF_E | CAT_P4 | BPL851 | PRIV_ALARMACK | A_P1_FUEL | Rack 1 Slot 5 Channel 0 Overflow Error | BPL851_R1S5Ch0ROVF_E | C_EVENT | BPL851 | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL851.Rack1
BR4_Tags | BPL851_R1S5Ch0RUNF_E | Loco Refuelling PLC | Rack 1 Slot 5 Channel 0 Underflow Error | BPL851_R1S5Ch0RUNF_E | CAT_P4 | BPL851 | PRIV_ALARMACK | A_P1_FUEL | Rack 1 Slot 5 Channel 0 Underflow Error | BPL851_R1S5Ch0RUNF_E | C_EVENT | BPL851 | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL851.Rack1
BR4_Tags | BPL851_R1S5Ch1OK_A | Loco Refuelling PLC | Rack 1 Slot 5 Channel 1 Fault | BPL851_R1S5Ch1OK_A | CAT_P3 | BPL851 | PRIV_ALARMACK | A_P1_FUEL | Rack 1 Slot 5 Channel 1 Fault | BPL851_R1S5Ch1OK_A | C_LOPRI | BPL851 | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL851.Rack1
BR4_Tags | BPL851_R1S5Ch1ROVF_E | Loco Refuelling PLC | Rack 1 Slot 5 Channel 1 Overflow Error | BPL851_R1S5Ch1ROVF_E | CAT_P4 | BPL851 | PRIV_ALARMACK | A_P1_FUEL | Rack 1 Slot 5 Channel 1 Overflow Error | BPL851_R1S5Ch1ROVF_E | C_EVENT | BPL851 | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL851.Rack1
BR4_Tags | BPL851_R1S5Ch1RUNF_E | Loco Refuelling PLC | Rack 1 Slot 5 Channel 1 Underflow Error | BPL851_R1S5Ch1RUNF_E | CAT_P4 | BPL851 | PRIV_ALARMACK | A_P1_FUEL | Rack 1 Slot 5 Channel 1 Underflow Error | BPL851_R1S5Ch1RUNF_E | C_EVENT | BPL851 | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL851.Rack1
BR4_Tags | BPL851_R1S5Ch2OK_A | Loco Refuelling PLC | Rack 1 Slot 5 Channel 2 Fault | BPL851_R1S5Ch2OK_A | CAT_P3 | BPL851 | PRIV_ALARMACK | A_P1_FUEL | Rack 1 Slot 5 Channel 2 Fault | BPL851_R1S5Ch2OK_A | C_LOPRI | BPL851 | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL851.Rack1
BR4_Tags | BPL851_R1S5Ch2ROVF_E | Loco Refuelling PLC | Rack 1 Slot 5 Channel 2 Overflow Error | BPL851_R1S5Ch2ROVF_E | CAT_P4 | BPL851 | PRIV_ALARMACK | A_P1_FUEL | Rack 1 Slot 5 Channel 2 Overflow Error | BPL851_R1S5Ch2ROVF_E | C_EVENT | BPL851 | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL851.Rack1
BR4_Tags | BPL851_R1S5Ch2RUNF_E | Loco Refuelling PLC | Rack 1 Slot 5 Channel 2 Underflow Error | BPL851_R1S5Ch2RUNF_E | CAT_P4 | BPL851 | PRIV_ALARMACK | A_P1_FUEL | Rack 1 Slot 5 Channel 2 Underflow Error | BPL851_R1S5Ch2RUNF_E | C_EVENT | BPL851 | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL851.Rack1
BR4_Tags | BPL851_R1S5Ch3OK_A | Loco Refuelling PLC | Rack 1 Slot 5 Channel 3 Fault | BPL851_R1S5Ch3OK_A | CAT_P3 | BPL851 | PRIV_ALARMACK | A_P1_FUEL | Rack 1 Slot 5 Channel 3 Fault | BPL851_R1S5Ch3OK_A | C_LOPRI | BPL851 | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL851.Rack1
BR4_Tags | BPL851_R1S5Ch3ROVF_E | Loco Refuelling PLC | Rack 1 Slot 5 Channel 3 Overflow Error | BPL851_R1S5Ch3ROVF_E | CAT_P4 | BPL851 | PRIV_ALARMACK | A_P1_FUEL | Rack 1 Slot 5 Channel 3 Overflow Error | BPL851_R1S5Ch3ROVF_E | C_EVENT | BPL851 | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL851.Rack1
BR4_Tags | BPL851_R1S5Ch3RUNF_E | Loco Refuelling PLC | Rack 1 Slot 5 Channel 3 Underflow Error | BPL851_R1S5Ch3RUNF_E | CAT_P4 | BPL851 | PRIV_ALARMACK | A_P1_FUEL | Rack 1 Slot 5 Channel 3 Underflow Error | BPL851_R1S5Ch3RUNF_E | C_EVENT | BPL851 | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL851.Rack1
BR4_Tags | BPL851_BPL801CommsFlt_A | Loco Refuelling PLC | InterPLC BPL801 Communications Faulted | BPL851_BPL801CommsFlt_A | CAT_P2 | BPL851 | PRIV_ALARMACK | A_P1_FUEL | InterPLC BPL801 Communications Faulted | BPL851_BPL801CommsFlt_A | C_HIPRI | BPL851 | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL851
BR4_Tags | RLF01PLCM01OK_A | Loco Refuelling PLC | RS910 Modbus/RTU Server Fault | RLF01PLCM01OK_A | CAT_P3 | BPL851 | PRIV_ALARMACK | A_P1_FUEL | RS910 Modbus/RTU Server Fault | RLF01PLCM01OK_A | C_LOPRI | BPL851 | Class_Equipment | BR4_Cluster1 | BR4.SRV.CTRLSYS.PLC.BPL851
BR4_Tags | BMC850ESD01_A | Loco Refuelling | Unloading Area EStop 1 Activated | BMC850ESD01_A | CAT_P3 | LOCOREFUEL1 | PRIV_ALARMACK | A_P1_FUEL | Unloading Area EStop 1 Activated | BMC850ESD01_A | C_LOPRI | BMC850 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.FUBULOIL.LOCOREFUEL.BMC850
BR4_Tags | BMC850ESD02_A | Loco Refuelling | Unloading Area EStop 2 Activated | BMC850ESD02_A | CAT_P3 | LOCOREFUEL1 | PRIV_ALARMACK | A_P1_FUEL | Unloading Area EStop 2 Activated | BMC850ESD02_A | C_LOPRI | BMC850 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.FUBULOIL.LOCOREFUEL.BMC850
BR4_Tags | BMC850ESD03_A | Loco Refuelling | Unloading Area EStop 3 Activated | BMC850ESD03_A | CAT_P3 | LOCOREFUEL1 | PRIV_ALARMACK | A_P1_FUEL | Unloading Area EStop 3 Activated | BMC850ESD03_A | C_LOPRI | BMC850 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.FUBULOIL.LOCOREFUEL.BMC850
BR4_Tags | BMC850ESD04_A | Loco Refuelling | EStop 4 Activated | BMC850ESD04_A | CAT_P3 | LOCOREFUEL1 | PRIV_ALARMACK | A_P1_FUEL | Refuelling Area EStop 4 Activated | BMC850ESD04_A | C_LOPRI | BMC850 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.FUBULOIL.LOCOREFUEL.BMC850
BR4_Tags | BMC850ESD05_A | Loco Refuelling | EStop 5 Activated | BMC850ESD05_A | CAT_P3 | LOCOREFUEL1 | PRIV_ALARMACK | A_P1_FUEL | Refuelling Area EStop 5 Activated | BMC850ESD05_A | C_LOPRI | BMC850 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.FUBULOIL.LOCOREFUEL.BMC850
BR4_Tags | BMC850ESDOK_A | Loco Refuelling | EStop Safety Relay Activted / Loss of 24V DC | BMC850ESDOK_A | CAT_P3 | LOCOREFUEL1 | PRIV_ALARMACK | A_P1_FUEL | EStop Safety Relay Activted / Loss of 24V DC | BMC850ESDOK_A | C_LOPRI | BMC850 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.FUBULOIL.LOCOREFUEL.BMC850
BR4_Tags | BPP850DCOK_A | Loco RF Diesel Pump | 24VDC Power Supply Trip | BPP850DCOK_A | CAT_P3 | LOCOREFUEL1 | PRIV_ALARMACK | A_P1_FUEL | Loss of 24 V DC supply | BPP850DCOK_A | C_LOPRI | BPP850 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.FUBULOIL.LOCOREFUEL.BPP850
BR4_Tags | BPP850_TesysTCommsOK_A | Loco RF Diesel Pump | Motor Management Controller Comms Fault | BPP850_TesysTCommsOK_A | CAT_P3 | LOCOREFUEL1 | PRIV_ALARMACK | A_P1_FUEL | Motor Management Controller Comms Fault | BPP850_TesysTCommsOK_A | C_LOPRI | BPP850 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.FUBULOIL.LOCOREFUEL.BPP850.TesysT
BR4_Tags | BPP850_TesysTSysFlt_A | Loco RF Diesel Pump | Motor Management Controller Tripped | BPP850_TesysTSysFlt_A | CAT_P3 | LOCOREFUEL1 | PRIV_ALARMACK | A_P1_FUEL | Motor Management Controller Fault | BPP850_TesysTSysFlt_A | C_LOPRI | BPP850 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.FUBULOIL.LOCOREFUEL.BPP850.TesysT
BR4_Tags | BPP850ACOK_A | Loco RF Diesel Pump | 240VAC Power Supply Trip | BPP850ACOK_A | CAT_P3 | LOCOREFUEL1 | PRIV_ALARMACK | A_P1_FUEL | Loss of 240 V AC supply | BPP850ACOK_A | C_LOPRI | BPP850 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.FUBULOIL.LOCOREFUEL.BPP850
BR4_Tags | BPP850IS01_A | Loco RF Diesel Pump | Isolator Open Trip | BPP850IS01_A | CAT_P3 | LOCOREFUEL1 | PRIV_ALARMACK | A_P1_FUEL | Isolator Not Closed | BPP850IS01_A | C_LOPRI | BPP850 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.FUBULOIL.LOCOREFUEL.BPP850.IS01
BR4_Tags | BPP850LOS01_A | Loco RF Diesel Pump | Lock Off Stop Trip | BPP850LOS01_A | CAT_P1 | LOCOREFUEL1 | PRIV_ALARMACK | A_P1_FUEL | Lock Off Stop Trip | BPP850LOS01_A | C_LOPRI | BPP850 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.FUBULOIL.LOCOREFUEL.BPP850.LOS01
BR4_Tags | BPP850MC01_A | Loco RF Diesel Pump | Main Contactor Faulted Trip | BPP850MC01_A | CAT_P3 | LOCOREFUEL1 | PRIV_ALARMACK | A_P1_FUEL | Main Contactor Failure | BPP850MC01_A | C_LOPRI | BPP850 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.FUBULOIL.LOCOREFUEL.BPP850.MC01
BR4_Tags | BPP850PT01_Hi_A | Loco RF Diesel Pump | Filter Differential Pressure High | BPP850PT01_Hi_A | CAT_P3 | LOCOREFUEL1 | PRIV_ALARMACK | A_P1_FUEL | Filter Differential Pressure High | BPP850PT01_Hi_A | C_LOPRI | BPP850 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.FUBULOIL.LOCOREFUEL.BPP850.PT01
BR4_Tags | BPP850FQ01_A | Loco RF Diesel Pump | No Flow Trip | BPP850FQ01_A | CAT_P3 | LOCOREFUEL1 | PRIV_ALARMACK | A_P1_FUEL | Running But No Flow | BPP850FQ01_A | C_LOPRI | BPP850 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.FUBULOIL.LOCOREFUEL.BPP850
BR4_Tags | BPP851DCOK_A | Loco RF Coolant Pump | 24VDC Power Supply Trip | BPP851DCOK_A | CAT_P3 | LOCOREFUEL1 | PRIV_ALARMACK | A_P1_FUEL | Loss of 24 V DC supply | BPP851DCOK_A | C_LOPRI | BPP851 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.FUBULOIL.LOCOREFUEL.BPP851
BR4_Tags | BPP851_TesysTCommsOK_A | Loco RF Coolant Pump | Motor Management Controller Comms Fault | BPP851_TesysTCommsOK_A | CAT_P3 | LOCOREFUEL1 | PRIV_ALARMACK | A_P1_FUEL | Motor Management Controller Comms Fault | BPP851_TesysTCommsOK_A | C_LOPRI | BPP851 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.FUBULOIL.LOCOREFUEL.BPP851.TesysT
BR4_Tags | BPP851_TesysTSysFlt_A | Loco RF Coolant Pump | Motor Management Controller Tripped | BPP851_TesysTSysFlt_A | CAT_P3 | LOCOREFUEL1 | PRIV_ALARMACK | A_P1_FUEL | Motor Management Controller Fault | BPP851_TesysTSysFlt_A | C_LOPRI | BPP851 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.FUBULOIL.LOCOREFUEL.BPP851.TesysT
BR4_Tags | BPP851ACOK_A | Loco RF Coolant Pump | 240VAC Power Supply Trip | BPP851ACOK_A | CAT_P3 | LOCOREFUEL1 | PRIV_ALARMACK | A_P1_FUEL | Loss of 240 V AC supply | BPP851ACOK_A | C_LOPRI | BPP851 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.FUBULOIL.LOCOREFUEL.BPP851
BR4_Tags | BPP851IS01_A | Loco RF Coolant Pump | Isolator Open Trip | BPP851IS01_A | CAT_P3 | LOCOREFUEL1 | PRIV_ALARMACK | A_P1_FUEL | Isolator Not Closed | BPP851IS01_A | C_LOPRI | BPP851 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.FUBULOIL.LOCOREFUEL.BPP851.IS01
BR4_Tags | BPP851LOS01_A | Loco RF Coolant Pump | Lock Off Stop Trip | BPP851LOS01_A | CAT_P1 | LOCOREFUEL1 | PRIV_ALARMACK | A_P1_FUEL | Lock Off Stop Trip | BPP851LOS01_A | C_LOPRI | BPP851 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.FUBULOIL.LOCOREFUEL.BPP851.LOS01
BR4_Tags | BPP851MC01_A | Loco RF Coolant Pump | Main Contactor Faulted Trip | BPP851MC01_A | CAT_P3 | LOCOREFUEL1 | PRIV_ALARMACK | A_P1_FUEL | Main Contactor Failure | BPP851MC01_A | C_LOPRI | BPP851 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.FUBULOIL.LOCOREFUEL.BPP851.MC01
BR4_Tags | BACC801PT01_Lo_A | Loco RF Coolant Pump | Running But No Pressure | BACC801PT01_Lo_A | CAT_P3 | LOCOREFUEL1 | PRIV_ALARMACK | A_P1_FUEL | Running But No Pressure | BACC801PT01_Lo_A | C_LOPRI | BACC801 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.FUBULOIL.LOCOREFUEL.BACC801.PT01
BR4_Tags | BPP852DCOK_A | Loco RF Lube Oil Pump | 24VDC Power Supply Trip | BPP852DCOK_A | CAT_P3 | LOCOREFUEL1 | PRIV_ALARMACK | A_P1_FUEL | Loss of 24 V DC supply | BPP852DCOK_A | C_LOPRI | BPP852 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.FUBULOIL.LOCOREFUEL.BPP852
BR4_Tags | BPP852_TesysTCommsOK_A | Loco RF Lube Oil Pump | Motor Management Controller Comms Fault | BPP852_TesysTCommsOK_A | CAT_P3 | LOCOREFUEL1 | PRIV_ALARMACK | A_P1_FUEL | Motor Management Controller Comms Fault | BPP852_TesysTCommsOK_A | C_LOPRI | BPP852 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.FUBULOIL.LOCOREFUEL.BPP852.TesysT
BR4_Tags | BPP852_TesysTSysFlt_A | Loco RF Lube Oil Pump | Motor Management Controller Tripped | BPP852_TesysTSysFlt_A | CAT_P3 | LOCOREFUEL1 | PRIV_ALARMACK | A_P1_FUEL | Motor Management Controller Fault | BPP852_TesysTSysFlt_A | C_LOPRI | BPP852 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.FUBULOIL.LOCOREFUEL.BPP852.TesysT
BR4_Tags | BPP852ACOK_A | Loco RF Lube Oil Pump | 240VAC Power Supply Trip | BPP852ACOK_A | CAT_P3 | LOCOREFUEL1 | PRIV_ALARMACK | A_P1_FUEL | Loss of 240 V AC supply | BPP852ACOK_A | C_LOPRI | BPP852 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.FUBULOIL.LOCOREFUEL.BPP852
BR4_Tags | BPP852IS01_A | Loco RF Lube Oil Pump | Isolator Open Trip | BPP852IS01_A | CAT_P3 | LOCOREFUEL1 | PRIV_ALARMACK | A_P1_FUEL | Isolator Not Closed | BPP852IS01_A | C_LOPRI | BPP852 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.FUBULOIL.LOCOREFUEL.BPP852.IS01
BR4_Tags | BPP852LOS01_A | Loco RF Lube Oil Pump | Lock Off Stop Trip | BPP852LOS01_A | CAT_P1 | LOCOREFUEL1 | PRIV_ALARMACK | A_P1_FUEL | Lock Off Stop Trip | BPP852LOS01_A | C_LOPRI | BPP852 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.FUBULOIL.LOCOREFUEL.BPP852.LOS01
BR4_Tags | BPP852MC01_A | Loco RF Lube Oil Pump | Main Contactor Faulted Trip | BPP852MC01_A | CAT_P3 | LOCOREFUEL1 | PRIV_ALARMACK | A_P1_FUEL | Main Contactor Failure | BPP852MC01_A | C_LOPRI | BPP852 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.FUBULOIL.LOCOREFUEL.BPP852.MC01
BR4_Tags | BPP852PS01_A | Loco RF Lube Oil Pump | Filter Blocked | BPP852PS01_A | CAT_P3 | LOCOREFUEL1 | PRIV_ALARMACK | A_P1_FUEL | Blocked Filter | BPP852PS01_A | C_LOPRI | BPP852 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.FUBULOIL.LOCOREFUEL.BPP852
BR4_Tags | BPP852FQ01_A | Loco RF Lube Oil Pump | No Flow Trip | BPP852FQ01_A | CAT_P3 | LOCOREFUEL1 | PRIV_ALARMACK | A_P1_FUEL | Running But No Flow | BPP852FQ01_A | C_LOPRI | BPP852 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.FUBULOIL.LOCOREFUEL.BPP852
BR4_Tags | BACC802PT01_Lo_A | Loco RF Lube Oil Accumulator | Running But No Pressure | BACC802PT01_Lo_A | CAT_P3 | LOCOREFUEL1 | PRIV_ALARMACK | A_P1_FUEL | Running But No Pressure | BACC802PT01_Lo_A | C_LOPRI | BACC802 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.FUBULOIL.LOCOREFUEL.BACC802.PT01
BR4_Tags | BPP853DCOK_A | Loco RF Retention Drain Pump | 24VDC Power Supply Trip | BPP853DCOK_A | CAT_P3 | LOCOREFUEL1 | PRIV_ALARMACK | A_P1_FUEL | Loss of 24 V DC supply | BPP853DCOK_A | C_LOPRI | BPP853 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.FUBULOIL.LOCOREFUEL.BPP853
BR4_Tags | BPP853LOS01_A | Loco RF Retention Drain Pump | Lock Off Stop Trip | BPP853LOS01_A | CAT_P1 | LOCOREFUEL1 | PRIV_ALARMACK | A_P1_FUEL | Lock Off Stop Trip | BPP853LOS01_A | C_LOPRI | BPP853 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.FUBULOIL.LOCOREFUEL.BPP853.LOS01
BR4_Tags | BPP854DCOK_A | Loco RF Unloading Pump | 24VDC Power Supply Trip | BPP854DCOK_A | CAT_P3 | LOCOREFUEL1 | PRIV_ALARMACK | A_P1_FUEL | Loss of 24 V DC supply | BPP854DCOK_A | C_LOPRI | BPP854 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.FUBULOIL.LOCOREFUEL.BPP854
BR4_Tags | BPP854_TesysTCommsOK_A | Loco RF Unloading Pump | Motor Management Controller Comms Fault | BPP854_TesysTCommsOK_A | CAT_P3 | LOCOREFUEL1 | PRIV_ALARMACK | A_P1_FUEL | Motor Management Controller Comms Fault | BPP854_TesysTCommsOK_A | C_LOPRI | BPP854 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.FUBULOIL.LOCOREFUEL.BPP854.TesysT
BR4_Tags | BPP854_TesysTSysFlt_A | Loco RF Unloading Pump | Motor Management Controller Tripped | BPP854_TesysTSysFlt_A | CAT_P3 | LOCOREFUEL1 | PRIV_ALARMACK | A_P1_FUEL | Motor Management Controller Fault | BPP854_TesysTSysFlt_A | C_LOPRI | BPP854 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.FUBULOIL.LOCOREFUEL.BPP854.TesysT
BR4_Tags | BPP854ACOK_A | Loco RF Unloading Pump | 240VAC Power Supply Trip | BPP854ACOK_A | CAT_P3 | LOCOREFUEL1 | PRIV_ALARMACK | A_P1_FUEL | Loss of 240 V AC supply | BPP854ACOK_A | C_LOPRI | BPP854 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.FUBULOIL.LOCOREFUEL.BPP854
BR4_Tags | BPP854IS01_A | Loco RF Unloading Pump | Isolator Open Trip | BPP854IS01_A | CAT_P3 | LOCOREFUEL1 | PRIV_ALARMACK | A_P1_FUEL | Isolator Not Closed | BPP854IS01_A | C_LOPRI | BPP854 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.FUBULOIL.LOCOREFUEL.BPP854.IS01
BR4_Tags | BPP854LOS01_A | Loco RF Unloading Pump | Lock Off Stop Trip | BPP854LOS01_A | CAT_P1 | LOCOREFUEL1 | PRIV_ALARMACK | A_P1_FUEL | Lock Off Stop Trip | BPP854LOS01_A | C_LOPRI | BPP854 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.FUBULOIL.LOCOREFUEL.BPP854.LOS01
BR4_Tags | BPP854MC01_A | Loco RF Unloading Pump | Main Contactor Faulted Trip | BPP854MC01_A | CAT_P3 | LOCOREFUEL1 | PRIV_ALARMACK | A_P1_FUEL | Main Contactor Failure | BPP854MC01_A | C_LOPRI | BPP854 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.FUBULOIL.LOCOREFUEL.BPP854.MC01
BR4_Tags | BPP854PT01_Hi_A | Loco RF Unloading Pump | Filter Differential Pressure High | BPP854PT01_Hi_A | CAT_P3 | LOCOREFUEL1 | PRIV_ALARMACK | A_P1_FUEL | Filter Differential Pressure High | BPP854PT01_Hi_A | C_LOPRI | BPP854 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.FUBULOIL.LOCOREFUEL.BPP854.PT01
BR4_Tags | BPP854FQ01_A | Loco RF Unloading Pump | No Flow Trip | BPP854FQ01_A | CAT_P3 | LOCOREFUEL1 | PRIV_ALARMACK | A_P1_FUEL | Running But No Flow | BPP854FQ01_A | C_LOPRI | BPP854 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.FUBULOIL.LOCOREFUEL.BPP854
BR4_Tags | BPP856DCOK_A | Loco RF Process Water Pump | 24VDC Power Supply Trip | BPP856DCOK_A | CAT_P3 | LOCOREFUEL2 | PRIV_ALARMACK | A_P1_FUEL | Loss of 24 V DC supply | BPP856DCOK_A | C_LOPRI | BPP856 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.FUBULOIL.LOCOREFUEL.BPP856
BR4_Tags | BPP856_TesysTCommsOK_A | Loco RF Process Water Pump | Motor Management Controller Comms Fault | BPP856_TesysTCommsOK_A | CAT_P3 | LOCOREFUEL2 | PRIV_ALARMACK | A_P1_FUEL | Motor Management Controller Comms Fault | BPP856_TesysTCommsOK_A | C_LOPRI | BPP856 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.FUBULOIL.LOCOREFUEL.BPP856.TesysT
BR4_Tags | BPP856_TesysTSysFlt_A | Loco RF Process Water Pump | Motor Management Controller Tripped | BPP856_TesysTSysFlt_A | CAT_P3 | LOCOREFUEL2 | PRIV_ALARMACK | A_P1_FUEL | Motor Management Controller Fault | BPP856_TesysTSysFlt_A | C_LOPRI | BPP856 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.FUBULOIL.LOCOREFUEL.BPP856.TesysT
BR4_Tags | BPP856ACOK_A | Loco RF Process Water Pump | 240VAC Power Supply Trip | BPP856ACOK_A | CAT_P3 | LOCOREFUEL2 | PRIV_ALARMACK | A_P1_FUEL | Loss of 240 V AC supply | BPP856ACOK_A | C_LOPRI | BPP856 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.FUBULOIL.LOCOREFUEL.BPP856
BR4_Tags | BPP856IS01_A | Loco RF Process Water Pump | Isolator Open Trip | BPP856IS01_A | CAT_P3 | LOCOREFUEL2 | PRIV_ALARMACK | A_P1_FUEL | Isolator Not Closed | BPP856IS01_A | C_LOPRI | BPP856 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.FUBULOIL.LOCOREFUEL.BPP856.IS01
BR4_Tags | BPP856LOS01_A | Loco RF Process Water Pump | Lock Off Stop Trip | BPP856LOS01_A | CAT_P1 | LOCOREFUEL2 | PRIV_ALARMACK | A_P1_FUEL | Lock Off Stop Trip | BPP856LOS01_A | C_LOPRI | BPP856 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.FUBULOIL.LOCOREFUEL.BPP856.LOS01
BR4_Tags | BPP856MC01_A | Loco RF Process Water Pump | Main Contactor Faulted Trip | BPP856MC01_A | CAT_P3 | LOCOREFUEL2 | PRIV_ALARMACK | A_P1_FUEL | Main Contactor Failure | BPP856MC01_A | C_LOPRI | BPP856 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.FUBULOIL.LOCOREFUEL.BPP856.MC01
BR4_Tags | BUV854XS01_A | Loco RF Process Water Pump | UV Filter Fault | BUV854XS01_A | CAT_P3 | LOCOREFUEL2 | PRIV_ALARMACK | A_P1_FUEL | UV Filter Fault | BUV854XS01_A | C_LOPRI | BPP856 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.FUBULOIL.LOCOREFUEL.BPP856
BR4_Tags | BWA856PT01_Lo_A | Loco RF Water Pump Accum | Pressure Low | BWA856PT01_Lo_A | CAT_P3 | LOCOREFUEL2 | PRIV_ALARMACK | A_P1_FUEL | System Pressure Low | BWA856PT01_Lo_A | C_LOPRI | BWA856 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.FUBULOIL.LOCOREFUEL.BWA856.PT01
BR4_Tags | BWA856PSH01_A | Loco RF Water Pump Accum | Pressure High High Trip | BWA856PSH01_A | CAT_P3 | LOCOREFUEL2 | PRIV_ALARMACK | A_P1_FUEL | System Pressure High High Trip | BWA856PSH01_A | C_LOPRI | BWA856 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.FUBULOIL.LOCOREFUEL.BWA856
BR4_Tags | BPP857DCOK_A | Loco RF Sump Pump | 24VDC Power Supply Trip | BPP857DCOK_A | CAT_P3 | LOCOREFUEL1 | PRIV_ALARMACK | A_P1_FUEL | Loss of 24 V DC supply | BPP857DCOK_A | C_LOPRI | BPP857 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.FUBULOIL.LOCOREFUEL.BPP857
BR4_Tags | BPP857_TesysTCommsOK_A | Loco RF Sump Pump | Motor Management Controller Comms Fault | BPP857_TesysTCommsOK_A | CAT_P3 | LOCOREFUEL1 | PRIV_ALARMACK | A_P1_FUEL | Motor Management Controller Comms Fault | BPP857_TesysTCommsOK_A | C_LOPRI | BPP857 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.FUBULOIL.LOCOREFUEL.BPP857.TesysT
BR4_Tags | BPP857_TesysTSysFlt_A | Loco RF Sump Pump | Motor Management Controller Tripped | BPP857_TesysTSysFlt_A | CAT_P3 | LOCOREFUEL1 | PRIV_ALARMACK | A_P1_FUEL | Motor Management Controller Fault | BPP857_TesysTSysFlt_A | C_LOPRI | BPP857 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.FUBULOIL.LOCOREFUEL.BPP857.TesysT
BR4_Tags | BPP857ACOK_A | Loco RF Sump Pump | 240VAC Power Supply Trip | BPP857ACOK_A | CAT_P3 | LOCOREFUEL1 | PRIV_ALARMACK | A_P1_FUEL | Loss of 240 V AC supply | BPP857ACOK_A | C_LOPRI | BPP857 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.FUBULOIL.LOCOREFUEL.BPP857
BR4_Tags | BPP857IS01_A | Loco RF Sump Pump | Isolator Open Trip | BPP857IS01_A | CAT_P3 | LOCOREFUEL1 | PRIV_ALARMACK | A_P1_FUEL | Isolator Not Closed | BPP857IS01_A | C_LOPRI | BPP857 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.FUBULOIL.LOCOREFUEL.BPP857.IS01
BR4_Tags | BPP857LOS01_A | Loco RF Sump Pump | Lock Off Stop Trip | BPP857LOS01_A | CAT_P1 | LOCOREFUEL1 | PRIV_ALARMACK | A_P1_FUEL | Lock Off Stop Trip | BPP857LOS01_A | C_LOPRI | BPP857 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.FUBULOIL.LOCOREFUEL.BPP857.LOS01
BR4_Tags | BPP857MC01_A | Loco RF Sump Pump | Main Contactor Faulted Trip | BPP857MC01_A | CAT_P3 | LOCOREFUEL1 | PRIV_ALARMACK | A_P1_FUEL | Main Contactor Failure | BPP857MC01_A | C_LOPRI | BPP857 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.FUBULOIL.LOCOREFUEL.BPP857.MC01
BR4_Tags | BPP857DCR01_A | Loco RF Sump Pump | Decontactor Not Connected | BPP857DCR01_A | CAT_P3 | LOCOREFUEL1 | PRIV_ALARMACK | A_P1_FUEL | Decontactor Not Connected | BPP857DCR01_A | C_LOPRI | BPP857 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.FUBULOIL.LOCOREFUEL.BPP857.DCR01
BR4_Tags | BPP857_RnngFlt_A | Loco RF Sump Pump | Running Too Long | BPP857_RnngFlt_A | CAT_P3 | LOCOREFUEL1 | PRIV_ALARMACK | A_P1_FUEL | Excessive Run Time | BPP857_RnngFlt_A | C_LOPRI | BPP857 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.FUBULOIL.LOCOREFUEL.BPP857
BR4_Tags | BSM857LSH01_A | Loco RF Sump Pump | Sump Running And Level Remains High | BSM857LSH01_A | CAT_P3 | LOCOREFUEL1 | PRIV_ALARMACK | A_P1_FUEL | Level Not Dropping | BSM857LSH01_A | C_LOPRI | BPP857 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.FUBULOIL.LOCOREFUEL.BPP857
BR4_Tags | BSM857_LSX_A | Loco RF Sump Pump | Level Switch Fault Trip | BSM857_LSX_A | CAT_P3 | LOCOREFUEL1 | PRIV_ALARMACK | A_P1_FUEL | Level Switch Fault | BSM857_LSX_A | C_LOPRI | BPP857 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.FUBULOIL.LOCOREFUEL.BPP857
BR4_Tags | BPP857_Rqd_A | Loco RF Sump Pump | Required And Not Running | BPP857_Rqd_A | CAT_P3 | LOCOREFUEL1 | PRIV_ALARMACK | A_P1_FUEL | Required But Not Running | BPP857_Rqd_A | C_LOPRI | BPP857 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.FUBULOIL.LOCOREFUEL.BPP857
BR4_Tags | BPP859_TesysTCommsOK_A | Loco RF MaintVeh Diesel Pump | Motor Management Controller Comms Fault | BPP859_TesysTCommsOK_A | CAT_P3 | LOCOREFUEL1 | PRIV_ALARMACK | A_P1_FUEL | Motor Management Controller Comms Fault | BPP859_TesysTCommsOK_A | C_LOPRI | BPP859 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.FUBULOIL.LOCOREFUEL.BPP859.TesysT
BR4_Tags | BPP859_TesysTSysFlt_A | Loco RF MaintVeh Diesel Pump | Motor Management Controller Tripped | BPP859_TesysTSysFlt_A | CAT_P3 | LOCOREFUEL1 | PRIV_ALARMACK | A_P1_FUEL | Motor Management Controller Fault | BPP859_TesysTSysFlt_A | C_LOPRI | BPP859 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.FUBULOIL.LOCOREFUEL.BPP859.TesysT
BR4_Tags | BPP859ACOK_A | Loco RF MaintVeh Diesel Pump | 240VAC Power Supply Trip | BPP859ACOK_A | CAT_P3 | LOCOREFUEL1 | PRIV_ALARMACK | A_P1_FUEL | Loss of 240 V AC supply | BPP859ACOK_A | C_LOPRI | BPP859 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.FUBULOIL.LOCOREFUEL.BPP859
BR4_Tags | BPP859IS01_A | Loco RF MaintVeh Diesel Pump | Isolator Open Trip | BPP859IS01_A | CAT_P3 | LOCOREFUEL1 | PRIV_ALARMACK | A_P1_FUEL | Isolator Not Closed | BPP859IS01_A | C_LOPRI | BPP859 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.FUBULOIL.LOCOREFUEL.BPP859.IS01
BR4_Tags | BPP859LOS01_A | Loco RF MaintVeh Diesel Pump | Lock Off Stop Trip | BPP859LOS01_A | CAT_P1 | LOCOREFUEL1 | PRIV_ALARMACK | A_P1_FUEL | Lock Off Stop Trip | BPP859LOS01_A | C_LOPRI | BPP859 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.FUBULOIL.LOCOREFUEL.BPP859.LOS01
BR4_Tags | BPP859MC01_A | Loco RF MaintVeh Diesel Pump | Main Contactor Faulted Trip | BPP859MC01_A | CAT_P3 | LOCOREFUEL1 | PRIV_ALARMACK | A_P1_FUEL | Main Contactor Failure | BPP859MC01_A | C_LOPRI | BPP859 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.FUBULOIL.LOCOREFUEL.BPP859.MC01
BR4_Tags | BTK851FV01_OpnLmtFlt_A | Loco RF Diesel Tk Outflw Valve | Failed to Open Trip | BTK851FV01_OpnLmtFlt_A | CAT_P3 | LOCOREFUEL1 | PRIV_ALARMACK | A_P1_FUEL | Failed to Open Trip | BTK851FV01_OpnLmtFlt_A | C_LOPRI | BTK851FV01 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.FUBULOIL.LOCOREFUEL.BTK851.FV01
BR4_Tags | BTK851FV01_ClsLmtFlt_A | Loco RF Diesel Tk Outflw Valve | Failed to Close Trip | BTK851FV01_ClsLmtFlt_A | CAT_P3 | LOCOREFUEL1 | PRIV_ALARMACK | A_P1_FUEL | Failed to Close Trip | BTK851FV01_ClsLmtFlt_A | C_LOPRI | BTK851FV01 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.FUBULOIL.LOCOREFUEL.BTK851.FV01
BR4_Tags | BTK851FV01_LmtFlt_A | Loco RF Diesel Tk Outflw Valve | Opened/Closed Limits Fault Trip | BTK851FV01_LmtFlt_A | CAT_P3 | LOCOREFUEL1 | PRIV_ALARMACK | A_P1_FUEL | Opened/Closed Limits Fault Trip | BTK851FV01_LmtFlt_A | C_LOPRI | BTK851FV01 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.FUBULOIL.LOCOREFUEL.BTK851.FV01
BR4_Tags | BTK851FV02_OpnLmtFlt_A | Loco RF Diesel Tk Inlet Valve | Failed to Open Trip | BTK851FV02_OpnLmtFlt_A | CAT_P3 | LOCOREFUEL1 | PRIV_ALARMACK | A_P1_FUEL | Failed to Open Trip | BTK851FV02_OpnLmtFlt_A | C_LOPRI | BTK851FV02 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.FUBULOIL.LOCOREFUEL.BTK851.FV02
BR4_Tags | BTK851FV02_ClsLmtFlt_A | Loco RF Diesel Tk Inlet Valve | Failed to Close Trip | BTK851FV02_ClsLmtFlt_A | CAT_P3 | LOCOREFUEL1 | PRIV_ALARMACK | A_P1_FUEL | Failed to Close Trip | BTK851FV02_ClsLmtFlt_A | C_LOPRI | BTK851FV02 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.FUBULOIL.LOCOREFUEL.BTK851.FV02
BR4_Tags | BTK851FV02_LmtFlt_A | Loco RF Diesel Tk Inlet Valve | Opened/Closed Limits Fault Trip | BTK851FV02_LmtFlt_A | CAT_P3 | LOCOREFUEL1 | PRIV_ALARMACK | A_P1_FUEL | Opened/Closed Limits Fault Trip | BTK851FV02_LmtFlt_A | C_LOPRI | BTK851FV02 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.FUBULOIL.LOCOREFUEL.BTK851.FV02
BR4_Tags | BTK851DCOK_A | Loco RF Diesel Tank | 24VDC Power Supply Trip | BTK851DCOK_A | CAT_P3 | LOCOREFUEL1 | PRIV_ALARMACK | A_P1_FUEL | Loss of 24 V DC supply | BTK851DCOK_A | C_LOPRI | BTK851 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.FUBULOIL.LOCOREFUEL.BTK851
BR4_Tags | BTK851LS01_A | Loco RF Diesel Tank | Level High High | BTK851LS01_A | CAT_P3 | LOCOREFUEL1 | PRIV_ALARMACK | A_P1_FUEL | Level Low Low Trip | BTK851LS01_A | C_LOPRI | BTK851 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.FUBULOIL.LOCOREFUEL.BTK851
BR4_Tags | BTK851LT01_Hi_A | Loco RF Diesel Tank | Level High | BTK851LT01_Hi_A | CAT_P3 | LOCOREFUEL1 | PRIV_ALARMACK | A_P1_FUEL | Level High | BTK851LT01_Hi_A | C_LOPRI | BTK851 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.FUBULOIL.LOCOREFUEL.BTK851.LT01
BR4_Tags | BTK851LT01_Lo_A | Loco RF Diesel Tank | Level Low | BTK851LT01_Lo_A | CAT_P3 | LOCOREFUEL1 | PRIV_ALARMACK | A_P1_FUEL | Level Low | BTK851LT01_Lo_A | C_LOPRI | BTK851 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.FUBULOIL.LOCOREFUEL.BTK851.LT01
BR4_Tags | BTK851LT01_LoLo_A | Loco RF Diesel Tank | Level Low Low Trip | BTK851LT01_LoLo_A | CAT_P3 | LOCOREFUEL1 | PRIV_ALARMACK | A_P1_FUEL | Level Low Low | BTK851LT01_LoLo_A | C_LOPRI | BTK851 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.FUBULOIL.LOCOREFUEL.BTK851.LT01
BR4_Tags | BPP850FV01_OpnLmtFlt_A | Loco RF Loadng Arm Sel Valve | Failed to Open Trip | BPP850FV01_OpnLmtFlt_A | CAT_P3 | LOCOREFUEL1 | PRIV_ALARMACK | A_P1_FUEL | Failed to Open Trip | BPP850FV01_OpnLmtFlt_A | C_LOPRI | BPP850FV01 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.FUBULOIL.LOCOREFUEL.BPP850.FV01
BR4_Tags | BPP850FV01_ClsLmtFlt_A | Loco RF Loadng Arm Sel Valve | Failed to Close Trip | BPP850FV01_ClsLmtFlt_A | CAT_P3 | LOCOREFUEL1 | PRIV_ALARMACK | A_P1_FUEL | Failed to Close Trip | BPP850FV01_ClsLmtFlt_A | C_LOPRI | BPP850FV01 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.FUBULOIL.LOCOREFUEL.BPP850.FV01
BR4_Tags | BPP850FV01_LmtFlt_A | Loco RF Loadng Arm Sel Valve | Opened/Closed Limits Fault Trip | BPP850FV01_LmtFlt_A | CAT_P3 | LOCOREFUEL1 | PRIV_ALARMACK | A_P1_FUEL | Opened/Closed Limits Fault Trip | BPP850FV01_LmtFlt_A | C_LOPRI | BPP850FV01 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.FUBULOIL.LOCOREFUEL.BPP850.FV01
BR4_Tags | BPP850FV01DCOK_A | Loco RF Loadng Arm Sel Valve | 24VDC Power Supply Trip | BPP850FV01DCOK_A | CAT_P3 | LOCOREFUEL1 | PRIV_ALARMACK | A_P1_FUEL | Loss of 24 V DC supply | BPP850FV01DCOK_A | C_LOPRI | BPP850FV01 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.FUBULOIL.LOCOREFUEL.BPP850.FV01
BR4_Tags | BPP850SS01_A | Loco RF Loadng Arm Sel Valve | Both Loading Arms Selected Trip | BPP850SS01_A | CAT_P3 | LOCOREFUEL1 | PRIV_ALARMACK | A_P1_FUEL | Both Loading Arms Selected | BPP850SS01_A | C_LOPRI | BPP850FV01 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.FUBULOIL.LOCOREFUEL.BPP850
BR4_Tags | BLA850FV01_OpnLmtFlt_A | Loco RF Load Arm 1 ESD Valve | Failed to Open Trip | BLA850FV01_OpnLmtFlt_A | CAT_P3 | LOCOREFUEL1 | PRIV_ALARMACK | A_P1_FUEL | Failed to Open Trip | BLA850FV01_OpnLmtFlt_A | C_LOPRI | BLA850FV01 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.FUBULOIL.LOCOREFUEL.BLA850FV01
BR4_Tags | BLA850FV01_ClsLmtFlt_A | Loco RF Load Arm 1 ESD Valve | Failed to Close Trip | BLA850FV01_ClsLmtFlt_A | CAT_P3 | LOCOREFUEL1 | PRIV_ALARMACK | A_P1_FUEL | Failed to Close Trip | BLA850FV01_ClsLmtFlt_A | C_LOPRI | BLA850FV01 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.FUBULOIL.LOCOREFUEL.BLA850FV01
BR4_Tags | BLA850FV01_LmtFlt_A | Loco RF Load Arm 1 ESD Valve | Opened/Closed Limits Fault Trip | BLA850FV01_LmtFlt_A | CAT_P3 | LOCOREFUEL1 | PRIV_ALARMACK | A_P1_FUEL | Opened/Closed Limits Fault Trip | BLA850FV01_LmtFlt_A | C_LOPRI | BLA850FV01 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.FUBULOIL.LOCOREFUEL.BLA850FV01
BR4_Tags | BLA851FV01_OpnLmtFlt_A | Loco RF Load Arm 2 ESD Valve | Failed to Open Trip | BLA851FV01_OpnLmtFlt_A | CAT_P3 | LOCOREFUEL1 | PRIV_ALARMACK | A_P1_FUEL | Failed to Open Trip | BLA851FV01_OpnLmtFlt_A | C_LOPRI | BLA851FV01 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.FUBULOIL.LOCOREFUEL.BLA851FV01
BR4_Tags | BLA851FV01_ClsLmtFlt_A | Loco RF Load Arm 2 ESD Valve | Failed to Close Trip | BLA851FV01_ClsLmtFlt_A | CAT_P3 | LOCOREFUEL1 | PRIV_ALARMACK | A_P1_FUEL | Failed to Close Trip | BLA851FV01_ClsLmtFlt_A | C_LOPRI | BLA851FV01 | Class_Process | BR4_Cluster1 | BR4.UTILITIES.FUBULOIL.LOCOREFUEL.BLA851FV01