## Sub IO Assignment
Item | Box | Node | PLC | Bus | Drop | Rack | Slot | Ch | Terminal | Node Type | IO Type | CPP | Rev | Instrument Tag | Device | Instrument List Description | Desc2 | State | Location | Drive | Datatype | Address | Drawing | Rev | Notes | FAT | SAT | Raw_Zero | Raw_Full | Eng_Zero | Eng_Full | Format | TS | T1 | T2 | T3 | T4 | Alm_AREA | Alm_PRIV | Alm_HELP | Alm_CATEGORY | Alm_CUSTOM1 | Alm_CUSTOM2 | Alm_CUSTOM3 | Alm_CUSTOM4 | Alm_CUSTOM5 | Alm_CUSTOM6 | Alm_CUSTOM7 | Alm_CUSTOM8
BSR130DX01
BSR130 | DX01 | DIO0 | 130 | 0 | 0 | 0 | 0 | Chassis |  | BMEXBP1200
BSR130 | DX01 | DIO0 | 130 | 0 | 0 | 0 | 0 | Power |  | BMXCPS4022
BSR130 | DX01 | DIO0 | 130 | 0 | 0 | 0 | 0 | CPU |  | BMEP586040 | DX01ES01 | [5 empty] | BPL130
BSR130 | DX01 | DIO0 | 130 | 0 | 0 | 0 | 0A | MEM |  | BMXRMS004GPF
BSR130 | DX01 | DIO0 | 130 | 0 | 0 | 0 | 2 | Spare - X |  | BMXX0
BSR130 | DX01 | DIO0 | 130 | 0 | 0 | 0 | 3 | Comms |  | BMENOC0301 | C | [5 empty] | PLC Comms
BSR130 | DX01 | DIO0 | 130 | 0 | 0 | 0 | 4 | Comms |  | BMENOC0301 | N/C CAT6 | [5 empty] | HMI Comms
BSR130 | DX01 | DIO0 | 130 | 0 | 0 | 0 | 5 | Comms |  | BMENOC0301 | DX01ES01 | [5 empty] | I/O
BSR130 | DX01 | DIO0 | 130 | 0 | 0 | 0 | 6 | Spare - E&X |  | BMXX0
BSR130 | DX01 | DIO0 | 130 | 0 | 0 | 0 | 7 | Spare - E&X |  | BMXX0
BSR130 | DX01 | DIO0 | 130 | 0 | 0 | 0 | 8 | Spare - X |  | BMXX0
BSR130 | DX01 | DIO0 | 130 | 0 | 0 | 0 | 9 | Spare - E&X |  | BMXX0
BSR130 | DX01 | DIO0 | 130 | 0 | 0 | 0 | 10 | Spare - X |  | BMXX0
BSR130 | DX01 | DIO0 | 130 | 0 | 0 | 0 | 11 | Spare - X |  | BMXX0
EIO node 1
BSR130 | DX01 | DIO1 | 130 | 2 | 1 | 0 | 0 | Chassis |  | BMEXBP1200
BSR130 | DX01 | DIO1 | 130 | 2 | 1 | 0 | 0 | Power |  | BMXCPS4022 |  |  | total |  | spare |  | % spare
BSR130 | DX01 | DIO1 | 130 | 2 | 1 | 0 | 0 | Comms |  | BMECRA31210 | DX1ES1 |  | 208 |  | 68 |  | 32.69% |  |  |  |  | 2.1\0.0:Comms
BSR130 | DX01 | DIO1 | 130 | 2 | 1 | 0 | 1 | 0 | BMXFCW303 | BMXDDI3202K | DI |  | 4 | BSR130BC02 | VDC02 |  | Battery Charger 110VDC Tripping Supply | Healthy | K112 | BSR130BC02 |  | 2.1\0.1:0 | BR4-2110-E-00240 | A | BSR130BC02-C3 | [7 empty] | F1 | 1 | 2
BSR130 | DX01 | DIO1 | 130 | 2 | 1 | 0 | 1 | 1 |  |  | DI |  | 4 | BSR130BC02 | CB02 |  | BMC1301INC01 110VDC INC01 Tripping Supply Circuit Breaker | Closed | Q114 | BSR130BC02 |  | 2.1\0.1:1 | BR4-2110-E-00240 | A | [8 empty] | F1 | 3 | 4
BSR130 | DX01 | DIO1 | 130 | 2 | 1 | 0 | 1 | 2 |  |  | DI |  | 4 | BSR130BC02 | CB03 |  | BMC1302INC01 110VDC INC01 Tripping Supply Circuit Breaker | Closed | Q117 | BSR130BC02 |  | 2.1\0.1:2 | BR4-2110-E-00240 | A | [8 empty] | F1 | 5 | 6
BSR130 | DX01 | DIO1 | 130 | 2 | 1 | 0 | 1 | 3 |  |  | DI |  | 4 | BSR130BC02 | CB04 |  | BMC1302INC02 110VDC INC02 Tripping Supply Circuit Breaker | Closed | Q120 | BSR130BC02 |  | 2.1\0.1:3 | BR4-2110-E-00240 | A | [8 empty] | F1 | 7 | 8
BSR130 | DX01 | DIO1 | 130 | 2 | 1 | 0 | 1 | 4 |  |  | DI |  | 4 | BSR130BC02 | CB05 |  | BMC1302INC03 110VDC INC03 Tripping Supply Circuit Breaker | Closed | Q123 | BSR130BC02 |  | 2.1\0.1:4 | BR4-2110-E-00240 | A | [8 empty] | F1 | 9 | 10
BSR130 | DX01 | DIO1 | 130 | 2 | 1 | 0 | 1 | 5 |  |  | DI |  | 4 | BSR130BC02 | CB06 |  | BSR130RSP01 110VDC Supply Circuit Breaker | Closed | Q126 | BSR130BC02 |  | 2.1\0.1:5 | BR4-2110-E-00240 | A | [8 empty] | F1 | 11 | 12
BSR130 | DX01 | DIO1 | 130 | 2 | 1 | 0 | 1 | 6 |  |  | DI |  | 4 | BSR130BC02 | CB07 |  | BJC130VS01 110VDC Supply Circuit Breaker | Closed | Q129 | BSR130BC02 |  | 2.1\0.1:6 | BR4-2110-E-00240 | A | [8 empty] | F1 | 13 | 14
BSR130 | DX01 | DIO1 | 130 | 2 | 1 | 0 | 1 | 7 |  |  | DI |  | 4 | BSR130BC02 | CB08 |  | BCV130VS01 110VDC Supply Circuit Breaker | Closed | Q132 | BSR130BC02 |  | 2.1\0.1:7 | BR4-2110-E-00240 | A | [8 empty] | F1 | 15 | 16
BSR130 | DX01 | DIO1 | 130 | 2 | 1 | 0 | 1 | 8 |  |  | DI |  | 4 | BSR130BC02 | CB09 |  | BSB1301 110VDC Supply Circuit Breaker | Closed | Q135 | BSR130BC02 |  | 2.1\0.1:8 | BR4-2110-E-00240 | A | [8 empty] | F1 | 17 | 18
BSR130 | DX01 | DIO1 | 130 | 2 | 1 | 0 | 1 | 9 |  |  | DI |  | 4 | BSR130BC02 | CB10 |  | Spare 110VDC Tripping Supply Circuit Breaker | Closed | Q138 | BSR130BC02 |  | 2.1\0.1:9 | BR4-2110-E-00240 | A | [8 empty] | F1 | 19 | 20
BSR130 | DX01 | DIO1 | 130 | 2 | 1 | 0 | 1 | 10 |  |  | DI |  | 4 | BSR130BC02 | CB11 |  | Spare 110VDC Tripping Supply Circuit Breaker | Closed | Q141 | BSR130BC02 |  | 2.1\0.1:10 | BR4-2110-E-00240 | A | [8 empty] | F1 | 21 | 22
BSR130 | DX01 | DIO1 | 130 | 2 | 1 | 0 | 1 | 11 |  |  | DI |  | 4 | BSR130BC02 | CB12 |  | Spare 110VDC Tripping Supply Circuit Breaker | Closed | Q144 | BSR130BC02 |  | 2.1\0.1:11 | BR4-2110-E-00240 | A | [8 empty] | F1 | 23 | 24
BSR130 | DX01 | DIO1 | 130 | 2 | 1 | 0 | 1 | 12 |  |  | DI | [10 empty] | 2.1\0.1:12 | [10 empty] | F1 | 25 | 26
BSR130 | DX01 | DIO1 | 130 | 2 | 1 | 0 | 1 | 13 |  |  | DI | [10 empty] | 2.1\0.1:13 | [10 empty] | F1 | 27 | 28
BSR130 | DX01 | DIO1 | 130 | 2 | 1 | 0 | 1 | 14 |  |  | DI | [10 empty] | 2.1\0.1:14 | [10 empty] | F1 | 29 | 30
BSR130 | DX01 | DIO1 | 130 | 2 | 1 | 0 | 1 | 15 |  |  | DI | [10 empty] | 2.1\0.1:15 | [10 empty] | F1 | 31 | 32
BSR130 | DX01 | DIO1 | 130 | 2 | 1 | 0 | 1 | 16 |  |  | DI | [10 empty] | 2.1\0.1:16 | [10 empty] | F1 | 33 | 34
BSR130 | DX01 | DIO1 | 130 | 2 | 1 | 0 | 1 | 17 |  |  | DI | [10 empty] | 2.1\0.1:17 | [10 empty] | F1 | 35 | 36
BSR130 | DX01 | DIO1 | 130 | 2 | 1 | 0 | 1 | 18 |  |  | DI | [10 empty] | 2.1\0.1:18 | [10 empty] | F1 | 37 | 38
BSR130 | DX01 | DIO1 | 130 | 2 | 1 | 0 | 1 | 19 |  |  | DI | [10 empty] | 2.1\0.1:19 | [10 empty] | F1 | 39 | 40
BSR130 | DX01 | DIO1 | 130 | 2 | 1 | 0 | 1 | 20 |  |  | DI |  | 4 | BSR130UP01SW01 | XS01 |  | Ups Surge Filter | Healthy |  | BSR130UP01 |  | 2.1\0.1:20 | BR4-2110-E-00249 | A | BSR130UP01SD01-C1 | [7 empty] | F1 | 41 | 42
BSR130 | DX01 | DIO1 | 130 | 2 | 1 | 0 | 1 | 21 |  |  | DI |  | 4 | BSR130UP01 | SW01 |  | UPS Bypassed / Test | Active |  | BSR130UP01 |  | 2.1\0.1:21 | BR4-2110-E-00249 | A | BSR130UP01SW01-C2 UPDATED TO 4 PR SCHEMATIC TO BE CREATED | [7 empty] | F1 | 43 | 44
BSR130 | DX01 | DIO1 | 130 | 2 | 1 | 0 | 1 | 22 |  |  | DI | [10 empty] | 2.1\0.1:22 |  | A | [8 empty] | F1 | 45 | 46
BSR130 | DX01 | DIO1 | 130 | 2 | 1 | 0 | 1 | 23 |  |  | DI |  | 4 | BSR130UP01SW01 | ZS01 |  | UPS In Normal Mode | Active |  | BSR130UP01 |  | 2.1\0.1:23 | BR4-2110-E-00249 | A | [8 empty] | F1 | 47 | 48
BSR130 | DX01 | DIO1 | 130 | 2 | 1 | 0 | 1 | 24 |  |  | DI | [10 empty] | 2.1\0.1:24 |  | A | [8 empty] | F1 | 49 | 50
BSR130 | DX01 | DIO1 | 130 | 2 | 1 | 0 | 1 | 25 |  |  | DI | [10 empty] | 2.1\0.1:25 | [10 empty] | F1 | 51 | 52
BSR130 | DX01 | DIO1 | 130 | 2 | 1 | 0 | 1 | 26 |  |  | DI | [10 empty] | 2.1\0.1:26 | [10 empty] | F1 | 53 | 54
BSR130 | DX01 | DIO1 | 130 | 2 | 1 | 0 | 1 | 27 |  |  | DI | [10 empty] | 2.1\0.1:27 | [10 empty] | F1 | 55 | 56
BSR130 | DX01 | DIO1 | 130 | 2 | 1 | 0 | 1 | 28 |  |  | DI | [10 empty] | 2.1\0.1:28 | [10 empty] | F1 | 57 | 58
BSR130 | DX01 | DIO1 | 130 | 2 | 1 | 0 | 1 | 29 |  |  | DI | [10 empty] | 2.1\0.1:29 | [10 empty] | F1 | 59 | 60
BSR130 | DX01 | DIO1 | 130 | 2 | 1 | 0 | 1 | 30 |  |  | DI | [10 empty] | 2.1\0.1:30 | [10 empty] | F1 | 61 | 62
BSR130 | DX01 | DIO1 | 130 | 2 | 1 | 0 | 1 | 31 |  |  | DI | [10 empty] | 2.1\0.1:31 | [10 empty] | F1 | 63 | 64
BSR130 | DX01 | DIO1 | 130 | 2 | 1 | 0 | 2 | 0 | BMXFCW303 | BMXDDI3202K | DI | [10 empty] | 2.1\0.2:0 | [10 empty] | F2 | 1 | 2
BSR130 | DX01 | DIO1 | 130 | 2 | 1 | 0 | 2 | 1 |  |  | DI |  | 4 | BSR130UP01DB01 | R1 |  | BSR130DX01 Primary 240VAC UPS Circuit Breaker | Closed | R1 | BSR130UP01DB01 |  | 2.1\0.2:1 | BR4-2110-E-00254 | A | BSR130UP01DB01-C2 30 pair | [7 empty] | F2 | 3 | 4
BSR130 | DX01 | DIO1 | 130 | 2 | 1 | 0 | 2 | 2 |  |  | DI |  | 4 | BSR130UP01DB01 | W1 |  | BSR130DX01 Secondary 240VAC UPS Circuit Breaker | Closed | W1 | BSR130UP01DB01 |  | 2.1\0.2:2 | BR4-2110-E-00254 | A | [8 empty] | F2 | 5 | 6
BSR130 | DX01 | DIO1 | 130 | 2 | 1 | 0 | 2 | 3 |  |  | DI |  | 4 | BSR130UP01DB01 | B1 |  | BSR130DX02 Primary 240VAC UPS Circuit Breaker | Closed | B1 | BSR130UP01DB01 |  | 2.1\0.2:3 | BR4-2110-E-00254 | A | [8 empty] | F2 | 7 | 8
BSR130 | DX01 | DIO1 | 130 | 2 | 1 | 0 | 2 | 4 |  |  | DI |  | 4 | BSR130UP01DB01 | R2 |  | BSR130DX02 Secondary 240VAC UPS Circuit Breaker | Closed | R2 | BSR130UP01DB01 |  | 2.1\0.2:4 | BR4-2110-E-00254 | A | [8 empty] | F2 | 9 | 10
BSR130 | DX01 | DIO1 | 130 | 2 | 1 | 0 | 2 | 5 |  |  | DI |  | 4 | BSR130UP01DB01 | W2 |  | DX03 240VAC UPS Circuit Breaker | Closed | W2 | BSR130UP01DB01 |  | 2.1\0.2:5 | BR4-2110-E-00254 | A | [8 empty] | F2 | 11 | 12
BSR130 | DX01 | DIO1 | 130 | 2 | 1 | 0 | 2 | 6 |  |  | DI |  | 4 | BSR130UP01DB01 | B2 |  | DX04 240VAC UPS Circuit Breaker | Closed | B2 | BSR130UP01DB01 |  | 2.1\0.2:6 | BR4-2110-E-00254 | A | [8 empty] | F2 | 13 | 14
BSR130 | DX01 | DIO1 | 130 | 2 | 1 | 0 | 2 | 7 |  |  | DI |  | 4 | BSR130UP01DB01 | R3 |  | DX05 240VAC UPS Circuit Breaker | Closed | R3 | BSR130UP01DB01 |  | 2.1\0.2:7 | BR4-2110-E-00254 | A | [8 empty] | F2 | 15 | 16
BSR130 | DX01 | DIO1 | 130 | 2 | 1 | 0 | 2 | 8 |  |  | DI |  | 4 | BSR130UP01DB01 | W3 |  | DX06 240VAC UPS Circuit Breaker | Closed | W3 | BSR130UP01DB01 |  | 2.1\0.2:8 | BR4-2110-E-00254 | A | [8 empty] | F2 | 17 | 18
BSR130 | DX01 | DIO1 | 130 | 2 | 1 | 0 | 2 | 9 |  |  | DI |  | 4 | BSR130UP01DB01 | B3 |  | DX07 240VAC UPS Circuit Breaker | Closed | B3 | BSR130UP01DB01 |  | 2.1\0.2:9 | BR4-2110-E-00254 | A | [8 empty] | F2 | 19 | 20
BSR130 | DX01 | DIO1 | 130 | 2 | 1 | 0 | 2 | 10 |  |  | DI |  | 4 | BSR130UP01DB01 | R4 |  | DX08 240VAC UPS Circuit Breaker | Closed | R4 | BSR130UP01DB01 |  | 2.1\0.2:10 | BR4-2110-E-00254 | A | [8 empty] | F2 | 21 | 22
BSR130 | DX01 | DIO1 | 130 | 2 | 1 | 0 | 2 | 11 |  |  | DI |  | 4 | BSR130UP01DB01 | W4 |  | DX09 240VAC UPS Circuit Breaker | Closed | W4 | BSR130UP01DB01 |  | 2.1\0.2:11 | BR4-2110-E-00254 | A | [8 empty] | F2 | 23 | 24
BSR130 | DX01 | DIO1 | 130 | 2 | 1 | 0 | 2 | 12 |  |  | DI |  | 4 | BSR130UP01DB01 | B4 |  | BSR130NEP01 240VAC Primary UPS Circuit Breaker | Closed | B4 | BSR130UP01DB01 |  | 2.1\0.2:12 | BR4-2110-E-00254 | A | [8 empty] | F2 | 25 | 26
BSR130 | DX01 | DIO1 | 130 | 2 | 1 | 0 | 2 | 13 |  |  | DI |  | 4 | BSR130UP01DB01 | R5 |  | BSR130NEP01 240VAC Secondary UPS Circuit Breaker | Closed | R5 | BSR130UP01DB01 |  | 2.1\0.2:13 | BR4-2110-E-00254 | A | [8 empty] | F2 | 27 | 28
BSR130 | DX01 | DIO1 | 130 | 2 | 1 | 0 | 2 | 14 |  |  | DI |  | 4 | BSR130UP01DB01 | W5 |  | HVAC Panel 240VAC UPS Circuit Breaker | Closed | W5 | BSR130UP01DB01 |  | 2.1\0.2:14 | BR4-2110-E-00254 | A | [8 empty] | F2 | 29 | 30
BSR130 | DX01 | DIO1 | 130 | 2 | 1 | 0 | 2 | 15 |  |  | DI |  | 4 | BSR130UP01DB01 | B5 |  | BSR130RIS02 Fis 240VAC UPS Circuit Breaker | Closed | B5 | BSR130UP01DB01 |  | 2.1\0.2:15 | BR4-2110-E-00254 | A | [8 empty] | F2 | 31 | 32
BSR130 | DX01 | DIO1 | 130 | 2 | 1 | 0 | 2 | 16 |  |  | DI |  | 4 | BSR130UP01DB01 | R6 |  | BSR130FIP01 Fire Panel 240VAC UPS Circuit Breaker | Closed | R6 | BSR130UP01DB01 |  | 2.1\0.2:16 | BR4-2110-E-00254 | A | [8 empty] | F2 | 33 | 34
BSR130 | DX01 | DIO1 | 130 | 2 | 1 | 0 | 2 | 17 |  |  | DI |  | 4 | BSR130UP01DB01 | W6 |  | BSR130VES01 Vesda Fire Detection Panel Breaker | Closed | W6 | BSR130UP01DB01 |  | 2.1\0.2:17 | BR4-2110-E-00254 | A | [8 empty] | F2 | 35 | 36
BSR130 | DX01 | DIO1 | 130 | 2 | 1 | 0 | 2 | 18 |  |  | DI |  | 4 | BSR130UP01DB01 | B6 |  | Cardax 240VAC UPS Circuit Breaker | Closed | B6 | BSR130UP01DB01 |  | 2.1\0.2:18 | BR4-2110-E-00254 | A | [8 empty] | F2 | 37 | 38
BSR130 | DX01 | DIO1 | 130 | 2 | 1 | 0 | 2 | 19 |  |  | DI |  | 4 | BSR130UP01DB01 | R7 |  | BSR130FSS01PN01 Supression Control Panel Breaker | Closed | R7 | BSR130UP01DB01 |  | 2.1\0.2:19 | BR4-2110-E-00254 | A | [8 empty] | F2 | 39 | 40
BSR130 | DX01 | DIO1 | 130 | 2 | 1 | 0 | 2 | 20 |  |  | DI |  | 4 | BSR130UP01DB01 | W7 |  | Spare | Closed | W7 | BSR130UP01DB01 |  | 2.1\0.2:20 | BR4-2110-E-00254 | A | [8 empty] | F2 | 41 | 42
BSR130 | DX01 | DIO1 | 130 | 2 | 1 | 0 | 2 | 21 |  |  | DI |  | 4 | BSR130UP01DB01 | B7 |  | BBD130CTV01 240VAC UPS Circuit Breaker | Closed | B7 | BSR130UP01DB01 |  | 2.1\0.2:21 | BR4-2110-E-00254 | A | [8 empty] | F2 | 43 | 44
BSR130 | DX01 | DIO1 | 130 | 2 | 1 | 0 | 2 | 22 |  |  | DI |  | 4 | BSR130UP01DB01 | R8 |  | BBD130CTV02 240VAC UPS Circuit Breaker | Closed | R8 | BSR130UP01DB01 |  | 2.1\0.2:22 | BR4-2110-E-00254 | A | [8 empty] | F2 | 45 | 46
BSR130 | DX01 | DIO1 | 130 | 2 | 1 | 0 | 2 | 23 |  |  | DI |  | 4 | BSR130UP01DB01 | W8 |  | BBD130CTV03 240VAC UPS Circuit Breaker | Closed | W8 | BSR130UP01DB01 |  | 2.1\0.2:23 | BR4-2110-E-00254 | A | [8 empty] | F2 | 47 | 48
BSR130 | DX01 | DIO1 | 130 | 2 | 1 | 0 | 2 | 24 |  |  | DI |  | 4 | BSR130UP01DB01 | B8 |  | BCV130CTV01 240VAC UPS Circuit Breaker | Closed | B8 | BSR130UP01DB01 |  | 2.1\0.2:24 | BR4-2110-E-00254 | A | [8 empty] | F2 | 49 | 50
BSR130 | DX01 | DIO1 | 130 | 2 | 1 | 0 | 2 | 25 |  |  | DI |  | 4 | BSR130UP01DB01 | R9 |  | BTN130CTV01 240VAC UPS Circuit Breaker | Closed | R9 | BSR130UP01DB01 |  | 2.1\0.2:25 | BR4-2110-E-00254 | A | [8 empty] | F2 | 51 | 52
BSR130 | DX01 | DIO1 | 130 | 2 | 1 | 0 | 2 | 26 |  |  | DI |  | 4 | BSR130UP01DB01 | W9 |  | BCV131DX12 240VAC UPS Circuit Breaker | Closed | W9 | BSR130UP01DB01 |  | 2.1\0.2:26 | BR4-2110-E-00254 | A | [8 empty] | F2 | 53 | 54
BSR130 | DX01 | DIO1 | 130 | 2 | 1 | 0 | 2 | 27 |  |  | DI |  | 4 | BSR130UP01DB01 | B9 |  | BCV131AX19-33 240VAC UPS Circuit Breaker | Closed | B9 | BSR130UP01DB01 |  | 2.1\0.2:27 | BR4-2110-E-00254 | A | [8 empty] | F2 | 55 | 56
BSR130 | DX01 | DIO1 | 130 | 2 | 1 | 0 | 2 | 28 |  |  | DI |  | 4 | BSR130UP01DB01 | R10 |  | BCV131AX20-34 240VAC UPS Circuit Breaker | Closed | R10 | BSR130UP01DB01 |  | 2.1\0.2:28 | BR4-2110-E-00254 | A | [8 empty] | F2 | 57 | 58
BSR130 | DX01 | DIO1 | 130 | 2 | 1 | 0 | 2 | 29 |  |  | DI |  | 4 | BSR130UP01DB01 | W10 |  | Spare | Closed | W10 | BSR130UP01DB01 |  | 2.1\0.2:29 | [10 empty] | F2 | 59 | 60
BSR130 | DX01 | DIO1 | 130 | 2 | 1 | 0 | 2 | 30 |  |  | DI |  | 4 | BSR130UP01DB01 | B10 |  | Rockbreaker Cabin 240VAC UPS Circuit Breaker | Closed | B10 | BSR130UP01DB01 |  | 2.1\0.2:30 | BR4-2110-E-00254 | A | [8 empty] | F2 | 61 | 62
BSR130 | DX01 | DIO1 | 130 | 2 | 1 | 0 | 2 | 31 |  |  | DI | [10 empty] | 2.1\0.2:31 | [10 empty] | F2 | 63 | 64
BSR130 | DX01 | DIO1 | 130 | 2 | 1 | 0 | 3 | 0 | BMXFCW303 | BMXDDI3202K | DI |  | 4 | BSR130 | PB01 |  | BSR130 Shutdown Pushbutton | Healthy | SESP | BSR130 |  | 2.1\0.3:0 | BR4-2110-E-00081 | A | NO CABLE BSR132PB01-C1 CREATED 1 PAIR | [7 empty] | F3 | 1 | 2
BSR130 | DX01 | DIO1 | 130 | 2 | 1 | 0 | 3 | 1 |  |  | DI |  | 4 | BSR130DX01 | XS01 |  | DX01 24VDC Power Supply 1 | Healthy | U103A | BSR130DX01 |  | 2.1\0.3:1 | BR4-2110-E-00081 | A | INTERNAL WIRING | [7 empty] | F3 | 3 | 4
BSR130 | DX01 | DIO1 | 130 | 2 | 1 | 0 | 3 | 2 |  |  | DI |  | 4 | BSR130DX01 | XS02 |  | DX01 24VDC Power Supply 2 | Healthy | U103B | BSR130DX01 |  | 2.1\0.3:2 | BR4-2110-E-00081 | A | INTERNAL WIRING | [7 empty] | F3 | 5 | 6
BSR130 | DX01 | DIO1 | 130 | 2 | 1 | 0 | 3 | 3 |  |  | DI |  | 4 | BSR130NEP01 | CB01 |  | BSR130NEP01 Primary PDU Circuit Breaker | Healthy | Q130 | BSR130NEP01 |  | 2.1\0.3:3 | BR4-2110-E-00081 | A | BSR132NEP02-C6 4 PAIR | [7 empty] | F3 | 7 | 8
BSR130 | DX01 | DIO1 | 130 | 2 | 1 | 0 | 3 | 4 |  |  | DI |  | 4 | BSR130NEP01 | CB02 |  | NEP Secondary PDU Circuit Breaker | Healthy | Q180 | BSR130NEP01 |  | 2.1\0.3:4 | BR4-2110-E-00081 | A | [8 empty] | F3 | 9 | 10
BSR130 | DX01 | DIO1 | 130 | 2 | 1 | 0 | 3 | 5 |  |  | DI |  | 4 | BSR130FIP01 | XS01 |  | Fire Panel | Healthy |  | BSR130FIP01 |  | 2.1\0.3:5 | BR4-2110-E-00081 | A | BSR132FIP01-C1 4 PAIR | [7 empty] | F3 | 11 | 12
BSR130 | DX01 | DIO1 | 130 | 2 | 1 | 0 | 3 | 6 |  |  | DI |  | 4 | BSR130FIP01 | IS01 |  | Fire Panel Isolated | Healthy |  | BSR130FIP01 |  | 2.1\0.3:6 | BR4-2110-E-00081 | A | [8 empty] | F3 | 13 | 14
BSR130 | DX01 | DIO1 | 130 | 2 | 1 | 0 | 3 | 7 |  |  | DI |  | 4 | BSR130FIP01 | XS02 |  | Fire Alarm | Healthy |  | BSR130FIP01 |  | 2.1\0.3:7 | BR4-2110-E-00081 | A | [8 empty] | F3 | 15 | 16
BSR130 | DX01 | DIO1 | 130 | 2 | 1 | 0 | 3 | 8 |  |  | DI |  | 4 | BSR130PN01 | TS01 |  | Airlock High Temperature | Alarm |  | BSR130PN01 |  | 2.1\0.3:8 | BR4-2110-E-00081 | A | NO CABLE BSR130PN01-C2 CREATED 10 PAIR | [7 empty] | F3 | 17 | 18
BSR130 | DX01 | DIO1 | 130 | 2 | 1 | 0 | 3 | 9 |  |  | DI |  | 4 | BSR130PN01 | TS02 |  | Fixed Plant Room High Temperature | Alarm |  | BSR130PN01 |  | 2.1\0.3:9 | BR4-2110-E-00081 | A | [8 empty] | F3 | 19 | 20
BSR130 | DX01 | DIO1 | 130 | 2 | 1 | 0 | 3 | 10 |  |  | DI |  | 4 | BSR130PN01 | PS01 |  | Switchroom Pressurisation Fan Filter | Alarm |  | BSR130PN01 |  | 2.1\0.3:10 | BR4-2110-E-00081 | A | [8 empty] | F3 | 21 | 22
BSR130 | DX01 | DIO1 | 130 | 2 | 1 | 0 | 3 | 11 |  |  | DI |  | 4 | BSR130PN01 | XS01 |  | Air Conditioner | Healthy |  | BSR130PN01 |  | 2.1\0.3:11 | BR4-2110-E-00081 | A | [8 empty] | F3 | 23 | 24
BSR130 | DX01 | DIO1 | 130 | 2 | 1 | 0 | 3 | 12 |  |  | DI |  | 4 | BSR130PN01 | XS02 |  | Air Conditioner Filter Blocked | Alarm |  | BSR130PN01 |  | 2.1\0.3:12 | BR4-2110-E-00081 | A | [8 empty] | F3 | 25 | 26
BSR130 | DX01 | DIO1 | 130 | 2 | 1 | 0 | 3 | 13 |  |  | DI |  | 5 | BSR130PN01 | XS03 |  | Air Conditioner 1 - Fixed Plant Room | Fault |  | BSR130PN01 |  | 2.1\0.3:13 | BR4-2110-E-00081 | A | [8 empty] | F3 | 27 | 28
BSR130 | DX01 | DIO1 | 130 | 2 | 1 | 0 | 3 | 14 |  |  | DI |  | 5 | BSR130PN01 | XS04 |  | Air Conditioner 2 - Fixed Plant Room | Fault |  | BSR130PN01 |  | 2.1\0.3:14 | BR4-2110-E-00081 | A | [8 empty] | F3 | 29 | 30
BSR130 | DX01 | DIO1 | 130 | 2 | 1 | 0 | 3 | 15 |  |  | DI |  | 5 | BSR130PN01 | XS05 |  | Air Conditioner 7 - Airlock | Fault |  | BSR130PN01 |  | 2.1\0.3:15 | BR4-2110-E-00081 | A | [8 empty] | F3 | 31 | 32
BSR130 | DX01 | DIO1 | 130 | 2 | 1 | 0 | 3 | 16 |  |  | DI |  | 5 | BSR130PN01 | XS06 |  | Air Conditioner 8 - Airlock | Fault |  | BSR130PN01 |  | 2.1\0.3:16 | BR4-2110-E-00081 | A | [8 empty] | F3 | 33 | 34
BSR130 | DX01 | DIO1 | 130 | 2 | 1 | 0 | 3 | 17 |  |  | DI |  | 5 | BSR130PN01 | XS07 |  | SPARE |  |  | BSR130PN01 |  | 2.1\0.3:17 | BR4-2110-E-00081 | A | [8 empty] | F3 | 35 | 36
BSR130 | DX01 | DIO1 | 130 | 2 | 1 | 0 | 3 | 18 |  |  | DI |  | 4 | BSR130DB01 | XS01 |  | BSR130DB01 Surge Protection | Healthy | SD106 | BSR130DB01 |  | 2.1\0.3:18 | BR4-2110-E-00081 | A | BSR132DB01-C1 | [7 empty] | F3 | 37 | 38
BSR130 | DX01 | DIO1 | 130 | 2 | 1 | 0 | 3 | 19 |  |  | DI |  | 4 | BSR130UP01DB01 | XS01 |  | BSR130UP01DB01 Surge Protection | Healthy | SD106 | BSR130UP01DB01 |  | 2.1\0.3:19 | BR4-2110-E-00081 | A | BSR130UP01DB01-C3 1 Pair | [7 empty] | F3 | 39 | 40
BSR130 | DX01 | DIO1 | 130 | 2 | 1 | 0 | 3 | 20 |  |  | DI |  | 5 | BSR130FIP01 | XS03 |  | Substation Gas | Discharged |  | BSR130FIP01 |  | 2.1\0.3:20 | BR4-2110-E-00081 | A | missing on Rev A | [7 empty] | F3 | 41 | 42
BSR130 | DX01 | DIO1 | 130 | 2 | 1 | 0 | 3 | 21 |  |  | DI | [10 empty] | 2.1\0.3:21 | BR4-2110-E-00081 | A | [8 empty] | F3 | 43 | 44
BSR130 | DX01 | DIO1 | 130 | 2 | 1 | 0 | 3 | 22 |  |  | DI | [10 empty] | 2.1\0.3:22 | BR4-2110-E-00081 | A | [8 empty] | F3 | 45 | 46
BSR130 | DX01 | DIO1 | 130 | 2 | 1 | 0 | 3 | 23 |  |  | DI |  | 4 | BSR130UP01DB01 | R11 |  | Rockbreaker BRB130 240VAC Ups Circuit Breaker | Closed | R11 | BSR130UP01DB01 |  | 2.1\0.3:23 | BR4-2110-E-00254 | A | BSR130UP01DB01-C4 4 Pair | [7 empty] | F3 | 47 | 48
BSR130 | DX01 | DIO1 | 130 | 2 | 1 | 0 | 3 | 24 |  |  | DI |  | 4 | BSR130UP01DB01 | W11 |  | Rockbreaker BRB131 240VAC Ups Circuit Breaker | Closed | W11 | BSR130UP01DB01 |  | 2.1\0.3:24 | BR4-2110-E-00254 | A | [8 empty] | F3 | 49 | 50
BSR130 | DX01 | DIO1 | 130 | 2 | 1 | 0 | 3 | 25 |  |  | DI |  | 4 | BSR130UP01DB01 | B11 |  | Spare | Closed | B11 | BSR130UP01DB01 |  | 2.1\0.3:25 | BR4-2110-E-00254 | A | [8 empty] | F3 | 51 | 52
BSR130 | DX01 | DIO1 | 130 | 2 | 1 | 0 | 3 | 26 |  |  | DI |  | 4 | BSR130UP01DB01 | R12 |  | Spare | Closed | R12 | BSR130UP01DB01 |  | 2.1\0.3:26 | BR4-2110-E-00254 | A | [8 empty] | F3 | 53 | 54
BSR130 | DX01 | DIO1 | 130 | 2 | 1 | 0 | 3 | 27 |  |  | DI |  | 4 | BSR130UP01DB01 | W12 |  | Spare | Closed | W12 | BSR130UP01DB01 |  | 2.1\0.3:27 | BR4-2110-E-00254 | A | [8 empty] | F3 | 55 | 56
BSR130 | DX01 | DIO1 | 130 | 2 | 1 | 0 | 3 | 28 |  |  | DI |  | 4 | BSR130UP01DB01 | B12 |  | Spare | Closed | B12 | BSR130UP01DB01 |  | 2.1\0.3:28 | BR4-2110-E-00254 | A | [8 empty] | F3 | 57 | 58
BSR130 | DX01 | DIO1 | 130 | 2 | 1 | 0 | 3 | 29 |  |  | DI | [10 empty] | 2.1\0.3:29 | [10 empty] | F3 | 59 | 60
BSR130 | DX01 | DIO1 | 130 | 2 | 1 | 0 | 3 | 30 |  |  | DI | [10 empty] | 2.1\0.3:30 | [10 empty] | F3 | 61 | 62
BSR130 | DX01 | DIO1 | 130 | 2 | 1 | 0 | 3 | 31 |  |  | DI | [10 empty] | 2.1\0.3:31 | [10 empty] | F3 | 63 | 64
BSR130 | DX01 | DIO1 | 130 | 2 | 1 | 0 | 4 | 0 | BMXFCW303 | BMXDDI3202K | DI |  | 4 | BMC1301INC01 | VDC01 |  | BMC1301 24VDC Control Supply | Healthy | Q267 | BMC1301INC01 |  | 2.1\0.4:0 | BR4-2110-E-00045 | A | BSR130UP01DB01-C3 8 Pair | [7 empty] | F4 | 1 | 2
BSR130 | DX01 | DIO1 | 130 | 2 | 1 | 0 | 4 | 1 |  |  | DI |  | 4 | BMC1301INC01 | CB02 |  | BMC1301 Arc Flash Supply | Healthy | Q204 | BMC1301INC01 |  | 2.1\0.4:1 | BR4-2110-E-00045 | A | [8 empty] | F4 | 3 | 4
BSR130 | DX01 | DIO1 | 130 | 2 | 1 | 0 | 4 | 2 |  |  | DI |  | 4 | BMC1301INC01 | TRP02 |  | BMC1301 Arc Flash Trip Alarm | Healthy |  | BMC1301INC01 |  | 2.1\0.4:2 | BR4-2110-E-00045 | A | [8 empty] | F4 | 5 | 6
BSR130 | DX01 | DIO1 | 130 | 2 | 1 | 0 | 4 | 3 |  |  | DI |  | 4 | BMC1301INC01 | XS02 |  | BMC1301 Arc Falsh System | Healthy |  | BMC1301INC01 |  | 2.1\0.4:3 | BR4-2110-E-00045 | A | [8 empty] | F4 | 7 | 8
BSR130 | DX01 | DIO1 | 130 | 2 | 1 | 0 | 4 | 4 |  |  | DI |  | 4 | BMC1301INC01 | CB03 |  | BMC1301 INC01 Spring Charge Supply OK | Healthy | Q212 | BMC1301INC01 |  | 2.1\0.4:4 | BR4-2110-E-00045 | A | [8 empty] | F4 | 9 | 10
BSR130 | DX01 | DIO1 | 130 | 2 | 1 | 0 | 4 | 5 |  |  | DI |  | 4 | BMC1301INC01 | CB04 |  | BMC1301 INC01 Trip Supply OK | Healthy | Q220 | BMC1301INC01 |  | 2.1\0.4:5 | BR4-2110-E-00045 | A | [8 empty] | F4 | 11 | 12
BSR130 | DX01 | DIO1 | 130 | 2 | 1 | 0 | 4 | 6 |  |  | DI |  | 4 | BMC1301INC01 | CB05 |  | BMC1301 INC01 Circuit Breaker 24VDC Cubicle Bus Supply OK | Healthy | Q256 | BMC1301INC01 |  | 2.1\0.4:6 | BR4-2110-E-00045 | A | [8 empty] | F4 | 13 | 14
BSR130 | DX01 | DIO1 | 130 | 2 | 1 | 0 | 4 | 7 |  |  | DI |  | 4 | BMC1301INC01 | XS03 |  | BMC1321 INC01 Surge Protection | Healthy | SD144-146 | BMC1301INC01 |  | 2.1\0.4:7 | BR4-2110-E-00045 | A | [8 empty] | F4 | 15 | 16
BSR130 | DX01 | DIO1 | 130 | 2 | 1 | 0 | 4 | 8 |  |  | DI |  | 4 | BMC1301INC01 | CB06 |  | BMC1301 INC01 110/24VDC Power Supply | Healthy | Q215 | BMC1301INC01 |  | 2.1\0.4:8 | BR4-2110-E-00045 | A | [8 empty] | F4 | 17 | 18
BSR130 | DX01 | DIO1 | 130 | 2 | 1 | 0 | 4 | 9 |  |  | DI | [10 empty] | 2.1\0.4:9 | [10 empty] | F4 | 19 | 20
BSR130 | DX01 | DIO1 | 130 | 2 | 1 | 0 | 4 | 10 |  |  | DI | [10 empty] | 2.1\0.4:10 | [10 empty] | F4 | 21 | 22
BSR130 | DX01 | DIO1 | 130 | 2 | 1 | 0 | 4 | 11 |  |  | DI | [10 empty] | 2.1\0.4:11 | [10 empty] | F4 | 23 | 24
BSR130 | DX01 | DIO1 | 130 | 2 | 1 | 0 | 4 | 12 |  |  | DI | [10 empty] | 2.1\0.4:12 | [10 empty] | F4 | 25 | 26
BSR130 | DX01 | DIO1 | 130 | 2 | 1 | 0 | 4 | 13 |  |  | DI | [10 empty] | 2.1\0.4:13 | [10 empty] | F4 | 27 | 28
BSR130 | DX01 | DIO1 | 130 | 2 | 1 | 0 | 4 | 14 |  |  | DI | [10 empty] | 2.1\0.4:14 | [10 empty] | F4 | 29 | 30
BSR130 | DX01 | DIO1 | 130 | 2 | 1 | 0 | 4 | 15 |  |  | DI |  | 4 | BAF130HT01 | VDC01 |  | 24VDC Control Supply | Healthy | Q155 | BAF130HT01 |  | 2.1\0.4:15 | BR4-2110-E-00057 | A | [8 empty] | F4 | 31 | 32
BSR130 | DX01 | DIO1 | 130 | 2 | 1 | 0 | 4 | 16 |  |  | DI |  | 4 | BAF130HT01 | CB01 |  | Main Circuit Breaker | Closed | Q103 | BAF130HT01 |  | 2.1\0.4:16 | BR4-2110-E-00057 | A | [8 empty] | F4 | 33 | 34
BSR130 | DX01 | DIO1 | 130 | 2 | 1 | 0 | 4 | 17 |  |  | DI |  | 4 | BAF130HT01 | TRP01 |  | Main Circuit Breaker | Tripped | Q103 | BAF130HT01 |  | 2.1\0.4:17 | BR4-2110-E-00057 | A | BAF130HT01-C1 | [7 empty] | F4 | 35 | 36
BSR130 | DX01 | DIO1 | 130 | 2 | 1 | 0 | 4 | 18 |  |  | DI |  | 4 | BAF130HT01 | CAX01 |  | Contactor Aux | Closed | K148 | BAF130HT01 |  | 2.1\0.4:18 | BR4-2110-E-00057 | A | [8 empty] | F4 | 37 | 38
BSR130 | DX01 | DIO1 | 130 | 2 | 1 | 0 | 4 | 19 |  |  | DI |  | 4 | BAF130HT02 | VDC01 |  | 24VDC Control Supply | Healthy | Q155 | BAF130HT02 |  | 2.1\0.4:19 | BR4-2110-E-00049 | A | [8 empty] | F4 | 39 | 40
BSR130 | DX01 | DIO1 | 130 | 2 | 1 | 0 | 4 | 20 |  |  | DI |  | 4 | BAF130HT02 | CB01 |  | Main Circuit Breaker | Closed | Q103 | BAF130HT02 |  | 2.1\0.4:20 | BR4-2110-E-00049 | A | BAF130HT02-C1 | [7 empty] | F4 | 41 | 42
BSR130 | DX01 | DIO1 | 130 | 2 | 1 | 0 | 4 | 21 |  |  | DI |  | 4 | BAF130HT02 | TRP01 |  | Main Circuit Breaker | Tripped | Q103 | BAF130HT02 |  | 2.1\0.4:21 | BR4-2110-E-00049 | A | [8 empty] | F4 | 43 | 44
BSR130 | DX01 | DIO1 | 130 | 2 | 1 | 0 | 4 | 22 |  |  | DI |  | 4 | BAF130HT02 | CAX01 |  | Contactor Aux | Closed | K148 | BAF130HT02 |  | 2.1\0.4:22 | BR4-2110-E-00049 | A | [8 empty] | F4 | 45 | 46
BSR130 | DX01 | DIO1 | 130 | 2 | 1 | 0 | 4 | 23 |  |  | DI |  | 4 | BDU130CP01 | VDC01 |  | 24VDC Control Supply | Healthy | Q155 | BDU130CP01 |  | 2.1\0.4:23 | BR4-2110-E-00060 | A | BDU130CP01PN01-C1 | [7 empty] | F4 | 47 | 48
BSR130 | DX01 | DIO1 | 130 | 2 | 1 | 0 | 4 | 24 |  |  | DI |  | 4 | BDU130CP01 | CB01 |  | Main Circuit Breaker | Closed | Q103 | BDU130CP01 |  | 2.1\0.4:24 | BR4-2110-E-00060 | A | [8 empty] | F4 | 49 | 50
BSR130 | DX01 | DIO1 | 130 | 2 | 1 | 0 | 4 | 25 |  |  | DI |  | 4 | BDU130CP01 | TRP01 |  | Main Circuit Breaker | Tripped | Q103 | BDU130CP01 |  | 2.1\0.4:25 | BR4-2110-E-00060 | A | [8 empty] | F4 | 51 | 52
BSR130 | DX01 | DIO1 | 130 | 2 | 1 | 0 | 4 | 26 |  |  | DI |  | 4 | BRB131HP01 | VDC01 |  | 24VDC Control Supply | Healthy | Q155 | BRB131HP01 |  | 2.1\0.4:26 | BR4-2110-E-00065 | A | BRB131HP01PN01-C1 | [7 empty] | F4 | 53 | 54
BSR130 | DX01 | DIO1 | 130 | 2 | 1 | 0 | 4 | 27 |  |  | DI |  | 4 | BRB131HP01 | CB01 |  | Main Circuit Breaker | Closed | Q103 | BRB131HP01 |  | 2.1\0.4:27 | BR4-2110-E-00065 | A | [8 empty] | F4 | 55 | 56
BSR130 | DX01 | DIO1 | 130 | 2 | 1 | 0 | 4 | 28 |  |  | DI |  | 4 | BRB131HP01 | TRP01 |  | Main Circuit Breaker | Tripped | Q103 | BRB131HP01 |  | 2.1\0.4:28 | BR4-2110-E-00065 | A | [8 empty] | F4 | 57 | 58
BSR130 | DX01 | DIO1 | 130 | 2 | 1 | 0 | 4 | 29 |  |  | DI |  | 4 | BRB132HP01 | VDC01 |  | 24VDC Control Supply | Healthy | Q155 | BRB132HP01 |  | 2.1\0.4:29 | BR4-2110-E-00064 | A | BRB132HP01PN01-C1 | [7 empty] | F4 | 59 | 60
BSR130 | DX01 | DIO1 | 130 | 2 | 1 | 0 | 4 | 30 |  |  | DI |  | 4 | BRB132HP01 | CB01 |  | Main Circuit Breaker | Closed | Q103 | BRB132HP01 |  | 2.1\0.4:30 | BR4-2110-E-00064 | A | [8 empty] | F4 | 61 | 62
BSR130 | DX01 | DIO1 | 130 | 2 | 1 | 0 | 4 | 31 |  |  | DI |  | 4 | BRB132HP01 | TRP01 |  | Main Circuit Breaker | Tripped | Q103 | BRB132HP01 |  | 2.1\0.4:31 | BR4-2110-E-00064 | A | [8 empty] | F4 | 63 | 64
BSR130 | DX01 | DIO1 | 130 | 2 | 1 | 0 | 5 | 0 | BMXFCW303 | BMXDDI3202K | DI |  | 4 | BSR130DX01 | VDC01 |  | DX01 24VDC Control Supply Healthy | Healthy | Q110 | BSR130DX01 |  | 2.1\0.5:0 | BR4-2110-E-00084 | 0 | INTERNAL WIRING | [7 empty] | F5 | 1 | 2
BSR130 | DX01 | DIO1 | 130 | 2 | 1 | 0 | 5 | 1 |  |  | DI |  | 4 | BSR130DX01 | VDC02 |  | DX01 24VDC Output Module Control Supply | Healthy | Q165 | BSR130DX01 |  | 2.1\0.5:1 | BR4-2110-E-00084 | 0 | [8 empty] | F5 | 3 | 4
BSR130 | DX01 | DIO1 | 130 | 2 | 1 | 0 | 5 | 2 |  |  | DI |  | 4 | BSR130DX01 | VDC03 |  | BSR130UP01 24VDC Control Supply | Healthy | Q254 | BSR130DX01 |  | 2.1\0.5:2 | BR4-2110-E-00085 | 0 | [8 empty] | F5 | 5 | 6
BSR130 | DX01 | DIO1 | 130 | 2 | 1 | 0 | 5 | 3 |  |  | DI |  | 4 | BSR130DX01 | VDC04 |  | BSR130BC01 24VDC Control Supply | Healthy | Q257 | BSR130DX01 |  | 2.1\0.5:3 | BR4-2110-E-00085 | 0 | [8 empty] | F5 | 7 | 8
BSR130 | DX01 | DIO1 | 130 | 2 | 1 | 0 | 5 | 4 |  |  | DI |  | 4 | BSR130DX01 | VDC05 |  | BSR130BC02 24VDC Control Supply | Healthy | Q260 | BSR130DX01 |  | 2.1\0.5:4 | BR4-2110-E-00085 | 0 | [8 empty] | F5 | 9 | 10
BSR130 | DX01 | DIO1 | 130 | 2 | 1 | 0 | 5 | 5 |  |  | DI |  | 4 | BSR130DX01 | VDC06 |  | BSR130UP01DB01 24VDC Control Supply | Healthy | Q263 | BSR130DX01 |  | 2.1\0.5:5 | BR4-2110-E-00085 | 0 | [8 empty] | F5 | 11 | 12
BSR130 | DX01 | DIO1 | 130 | 2 | 1 | 0 | 5 | 6 |  |  | DI |  | 4 | BSR130DX01 | VDC07 |  | Misc Switchroom Alarms 24VDC Control Supply | Healthy | Q266 | BSR130DX01 |  | 2.1\0.5:6 | BR4-2110-E-00085 | 0 | [8 empty] | F5 | 13 | 14
BSR130 | DX01 | DIO1 | 130 | 2 | 1 | 0 | 5 | 7 |  |  | DI |  | 4 | BSR130DX01 | VDC08 |  | BAF130 24VDC Control Supply | Healthy | Q269 | BSR130DX01 |  | 2.1\0.5:7 | BR4-2110-E-00085 | 0 | [8 empty] | F5 | 15 | 16
BSR130 | DX01 | DIO1 | 130 | 2 | 1 | 0 | 5 | 8 |  |  | DI |  | 4 | BSR130DX01 | VDC09 |  | BJC130 24VDC Control Supply | Healthy | Q272 | BSR130DX01 |  | 2.1\0.5:8 | BR4-2110-E-00085 | 0 | [8 empty] | F5 | 17 | 18
BSR130 | DX01 | DIO1 | 130 | 2 | 1 | 0 | 5 | 9 |  |  | DI |  | 4 | BSR130DX01 | VDC10 |  | BJC130VS01 | Healthy | Q275 | BSR130DX01 |  | 2.1\0.5:9 | BR4-2110-E-00085 | 0 | [8 empty] | F5 | 19 | 20
BSR130 | DX01 | DIO1 | 130 | 2 | 1 | 0 | 5 | 10 |  |  | DI |  | 4 | BSR130DX01 | VDC11 |  | BAF130GA01 24VDC Control Supply | Healthy | Q278 | BSR130DX01 |  | 2.1\0.5:10 | BR4-2110-E-00085 | 0 | [8 empty] | F5 | 21 | 22
BSR130 | DX01 | DIO1 | 130 | 2 | 1 | 0 | 5 | 11 |  |  | DI |  | 4 | BSR130DX01 | VDC12 |  | Spare | Healthy | Q281 | BSR130DX01 |  | 2.1\0.5:11 | BR4-2110-E-00085 | 0 | [8 empty] | F5 | 23 | 24
BSR130 | DX01 | DIO1 | 130 | 2 | 1 | 0 | 5 | 12 |  |  | DI |  | 4 | [8 empty] | 2.1\0.5:12 | [10 empty] | F5 | 25 | 26
BSR130 | DX01 | DIO1 | 130 | 2 | 1 | 0 | 5 | 13 |  |  | DI |  | 4 | BAF130PP07 | VDC01 |  | 24VDC Control Supply | Healthy | Q155 | BAF130PP07 |  | 2.1\0.5:13 | BR4-2110-E-00050 | A | [8 empty] | F5 | 27 | 28
BSR130 | DX01 | DIO1 | 130 | 2 | 1 | 0 | 5 | 14 |  |  | DI |  | 4 | BAF130PP01 | VDC01 |  | 24VDC Control Supply | Healthy | Q155 | BAF130PP01 |  | 2.1\0.5:14 | BR4-2110-E-00051 | A | [8 empty] | F5 | 29 | 30
BSR130 | DX01 | DIO1 | 130 | 2 | 1 | 0 | 5 | 15 |  |  | DI |  | 4 | BAF130PP02 | VDC01 |  | 24VDC Control Supply | Healthy | Q155 | BAF130PP02 |  | 2.1\0.5:15 | BR4-2110-E-00052 | A | [8 empty] | F5 | 31 | 32
BSR130 | DX01 | DIO1 | 130 | 2 | 1 | 0 | 5 | 16 |  |  | DI |  | 4 | BAF130PP04 | VDC01 |  | 24VDC Control Supply | Healthy | Q155 | BAF130PP04 |  | 2.1\0.5:16 | BR4-2110-E-00053 | A | [8 empty] | F5 | 33 | 34
BSR130 | DX01 | DIO1 | 130 | 2 | 1 | 0 | 5 | 17 |  |  | DI |  | 4 | BAF130FN01 | VDC01 |  | 24VDC Control Supply | Healthy | Q155 | BAF130FN01 |  | 2.1\0.5:17 | BR4-2110-E-00054 | A | [8 empty] | F5 | 35 | 36
BSR130 | DX01 | DIO1 | 130 | 2 | 1 | 0 | 5 | 18 |  |  | DI |  | 4 | BAF130FN02 | VDC01 |  | 24VDC Control Supply | Healthy | Q155 | BAF130FN02 |  | 2.1\0.5:18 | BR4-2110-E-00055 | A | [8 empty] | F5 | 37 | 38
BSR130 | DX01 | DIO1 | 130 | 2 | 1 | 0 | 5 | 19 |  |  | DI |  | 4 | BAF130FN03 | VDC01 |  | 24VDC Control Supply | Healthy | Q155 | BAF130FN03 |  | 2.1\0.5:19 | BR4-2110-E-00062 | A | [8 empty] | F5 | 39 | 40
BSR130 | DX01 | DIO1 | 130 | 2 | 1 | 0 | 5 | 20 |  |  | DI |  | 4 | BAF130PP05 | VDC01 |  | 24VDC Control Supply | Healthy | Q155 | BAF130PP05 |  | 2.1\0.5:20 | BR4-2110-E-00056 | A | [8 empty] | F5 | 41 | 42
BSR130 | DX01 | DIO1 | 130 | 2 | 1 | 0 | 5 | 21 |  |  | DI |  | 4 | BDU130FN01 | VDC01 |  | 24VDC Control Supply | Healthy | Q155 | BDU130FN01 |  | 2.1\0.5:21 | BR4-2110-E-00058 | A | [8 empty] | F5 | 43 | 44
BSR130 | DX01 | DIO1 | 130 | 2 | 1 | 0 | 5 | 22 |  |  | DI |  | 4 | BDU130RV01 | VDC01 |  | 24VDC Control Supply | Healthy | Q155 | BDU130RV01 |  | 2.1\0.5:22 | BR4-2110-E-00059 | A | [8 empty] | F5 | 45 | 46
BSR130 | DX01 | DIO1 | 130 | 2 | 1 | 0 | 5 | 23 |  |  | DI |  | 4 | BVG130DA01 | VDC01 |  | 24VDC Control Supply | Healthy | Q155 | BVG130DA01 |  | 2.1\0.5:23 | BR4-2110-E-00061 | A | [8 empty] | F5 | 47 | 48
BSR130 | DX01 | DIO1 | 130 | 2 | 1 | 0 | 5 | 24 |  |  | DI |  | 4 | BJC130PP01 | VDC01 |  | 24VDC Control Supply | Healthy | Q155 | BJC130PP01 |  | 2.1\0.5:24 | BR4-2110-E-00067 | A | [8 empty] | F5 | 49 | 50
BSR130 | DX01 | DIO1 | 130 | 2 | 1 | 0 | 5 | 25 |  |  | DI | [10 empty] | 2.1\0.5:25 | [10 empty] | F5 | 51 | 52
BSR130 | DX01 | DIO1 | 130 | 2 | 1 | 0 | 5 | 26 |  |  | DI | [10 empty] | 2.1\0.5:26 | [10 empty] | F5 | 53 | 54
BSR130 | DX01 | DIO1 | 130 | 2 | 1 | 0 | 5 | 27 |  |  | DI | [10 empty] | 2.1\0.5:27 | [10 empty] | F5 | 55 | 56
BSR130 | DX01 | DIO1 | 130 | 2 | 1 | 0 | 5 | 28 |  |  | DI | [10 empty] | 2.1\0.5:28 | [10 empty] | F5 | 57 | 58
BSR130 | DX01 | DIO1 | 130 | 2 | 1 | 0 | 5 | 29 |  |  | DI |  | 4 | BJC130HP01PN01 | VDC01 |  | 24VDC Control Supply | Healthy | Q155 | BJC130HP01PN01 |  | 2.1\0.5:29 | BR4-2110-E-00071 | A | [8 empty] | F5 | 59 | 60
BSR130 | DX01 | DIO1 | 130 | 2 | 1 | 0 | 5 | 30 |  |  | DI |  | 4 | BJC130HP01PN01 | CB01 |  | Main Circuit Breaker | Closed | Q103 | BJC130HP01PN01 |  | 2.1\0.5:30 | BR4-2110-E-00071 | A | [8 empty] | F5 | 61 | 62
BSR130 | DX01 | DIO1 | 130 | 2 | 1 | 0 | 5 | 31 |  |  | DI |  | 4 | BJC130HP01PN01 | TRP01 |  | Main Circuit Breaker | Tripped | Q103 | BJC130HP01PN01 |  | 2.1\0.5:31 | BR4-2110-E-00071 | A | [8 empty] | F5 | 63 | 64
BSR130 | DX01 | DIO1 | 130 | 2 | 1 | 0 | 6 | 0 | BMXFCW303 | BMXDDI3202K | DI |  | 4 | BJC130VS01 | VDC01 |  | 24Vdc Control Supply | Healthy | Q267 | BJC130VS01 |  | 2.1\0.6:0 | BR4-2110-E-00069 | A | BJC130VS01-C1 10 PAIR | [7 empty] | F6 | 1 | 2
BSR130 | DX01 | DIO1 | 130 | 2 | 1 | 0 | 6 | 1 |  |  | DI |  | 4 | BJC130VS01 | TRP01 |  | Downstream Circuit Breaker | Trip | K260 | BJC130VS01 |  | 2.1\0.6:1 | BR4-2110-E-00069 | [9 empty] | F6 | 3 | 4
BSR130 | DX01 | DIO1 | 130 | 2 | 1 | 0 | 6 | 2 |  |  | DI |  | 4 | BJC130VS01 | CB03 |  | Spring ChArge Supply Ok | Healthy | Q212 | BJC130VS01 |  | 2.1\0.6:2 | BR4-2110-E-00069 | A | [8 empty] | F6 | 5 | 6
BSR130 | DX01 | DIO1 | 130 | 2 | 1 | 0 | 6 | 3 |  |  | DI |  | 4 | BJC130VS01 | CB04 |  | Trip Supply Ok | Healthy | Q220 | BJC130VS01 |  | 2.1\0.6:3 | BR4-2110-E-00069 | A | [8 empty] | F6 | 7 | 8
BSR130 | DX01 | DIO1 | 130 | 2 | 1 | 0 | 6 | 4 |  |  | DI |  | 4 | BJC130VS01 | CB05 |  | 24Vdc Cubicle Bus Supply Ok | Healthy | Q256 | BJC130VS01 |  | 2.1\0.6:4 | BR4-2110-E-00069 | A | [8 empty] | F6 | 9 | 10
BSR130 | DX01 | DIO1 | 130 | 2 | 1 | 0 | 6 | 5 |  |  | DI |  | 4 | BJC130VS01 | CB07 |  | 110/24Vdc Power Supply Ok | Healthy | Q253 | BJC130VS01 |  | 2.1\0.6:5 | BR4-2110-E-00069 | A | [8 empty] | F6 | 11 | 12
BSR130 | DX01 | DIO1 | 130 | 2 | 1 | 0 | 6 | 6 |  |  | DI | [10 empty] | 2.1\0.6:6 |  |  | SAFETY RELAY ARRANGEMENT IN DX - INTERNAL WIRING | [7 empty] | F6 | 13 | 14
BSR130 | DX01 | DIO1 | 130 | 2 | 1 | 0 | 6 | 7 |  |  | DI | [10 empty] | 2.1\0.6:7 | [10 empty] | F6 | 15 | 16
BSR130 | DX01 | DIO1 | 130 | 2 | 1 | 0 | 6 | 8 |  |  | DI | [10 empty] | 2.1\0.6:8 | [10 empty] | F6 | 17 | 18
BSR130 | DX01 | DIO1 | 130 | 2 | 1 | 0 | 6 | 9 |  |  | DI | [10 empty] | 2.1\0.6:9 | [10 empty] | F6 | 19 | 20
BSR130 | DX01 | DIO1 | 130 | 2 | 1 | 0 | 6 | 10 |  |  | DI |  | 4 | BAF130 | SY01 |  | Safety Interlock Relay | Healthy | K103-1 | BAF130 |  | 2.1\0.6:10 | BR4-2110-E-00174 | 0 | BPQE2106PN01-C1 2 PAIR | [7 empty] | F6 | 21 | 22
BSR130 | DX01 | DIO1 | 130 | 2 | 1 | 0 | 6 | 11 |  |  | DI |  | 4 | BAF130FN | SY01 |  | Safety Interlock Relay | Healthy | K130-1 | BAF130FN |  | 2.1\0.6:11 | BR4-2110-E-00174 | 0 | BPQE2106PN01-C1 2 PAIR | [7 empty] | F6 | 23 | 24
BSR130 | DX01 | DIO1 | 130 | 2 | 1 | 0 | 6 | 12 |  |  | DI |  | 4 | BJC130 | SY01 |  | Safety Interlock Relay | Healthy | K203 | BJC130 |  | 2.1\0.6:12 | BR4-2110-E-00175 | 0 | BPQE2106DB01-C1 2 PAIR | [7 empty] | F6 | 25 | 26
BSR130 | DX01 | DIO1 | 130 | 2 | 1 | 0 | 6 | 13 |  |  | DI |  | 4 | BAF130GA01 | SY01 |  | Safety Interlock Relay | Healthy | K303 | BAF130GA01 |  | 2.1\0.6:13 | BR4-2110-E-00176 | 0 | BPQE2106DB01-C1 2 PAIR | [7 empty] | F6 | 27 | 28
BSR130 | DX01 | DIO1 | 130 | 2 | 1 | 0 | 6 | 14 |  |  | DI | [10 empty] | 2.1\0.6:14 | BR4-2150-E-00082 | A | BPQE2106DB01-C1 2 PAIR | [7 empty] | F6 | 29 | 30
BSR130 | DX01 | DIO1 | 130 | 2 | 1 | 0 | 6 | 15 |  |  | DI | [10 empty] | 2.1\0.6:15 | [10 empty] | F6 | 31 | 32
BSR130 | DX01 | DIO1 | 130 | 2 | 1 | 0 | 6 | 16 |  |  | DI | [10 empty] | 2.1\0.6:16 | [10 empty] | F6 | 33 | 34
BSR130 | DX01 | DIO1 | 130 | 2 | 1 | 0 | 6 | 17 |  |  | DI | [10 empty] | 2.1\0.6:17 | BR4-2150-E-00124 | 0 | [8 empty] | F6 | 35 | 36
BSR130 | DX01 | DIO1 | 130 | 2 | 1 | 0 | 6 | 18 |  |  | DI | [10 empty] | 2.1\0.6:18 | BR4-2150-E-00047 | A | BCV131AVS01-C4 2 PAIR | [7 empty] | F6 | 37 | 38
BSR130 | DX01 | DIO1 | 130 | 2 | 1 | 0 | 6 | 19 |  |  | DI | [10 empty] | 2.1\0.6:19 | BR4-2150-E-00047 | A | BCV131AVS01-C4 2 PAIR | [7 empty] | F6 | 39 | 40
BSR130 | DX01 | DIO1 | 130 | 2 | 1 | 0 | 6 | 20 |  |  | DI | [10 empty] | 2.1\0.6:20 | BR4-2150-E-00047 | A | BCV131AVS01-C4 2 PAIR | [7 empty] | F6 | 41 | 42
BSR130 | DX01 | DIO1 | 130 | 2 | 1 | 0 | 6 | 21 |  |  | DI | [10 empty] | 2.1\0.6:21 | [10 empty] | F6 | 43 | 44
BSR130 | DX01 | DIO1 | 130 | 2 | 1 | 0 | 6 | 22 |  |  | DI | [10 empty] | 2.1\0.6:22 | BR4-2150-E-00124 | 0 | [8 empty] | F6 | 45 | 46
BSR130 | DX01 | DIO1 | 130 | 2 | 1 | 0 | 6 | 23 |  |  | DI | [10 empty] | 2.1\0.6:23 | BR4-2150-E-00050 | A | BCV131BVS01-C4 2 PAIR | [7 empty] | F6 | 47 | 48
BSR130 | DX01 | DIO1 | 130 | 2 | 1 | 0 | 6 | 24 |  |  | DI | [10 empty] | 2.1\0.6:24 | BR4-2150-E-00050 | A | BCV131BVS01-C4 2 PAIR | [7 empty] | F6 | 49 | 50
BSR130 | DX01 | DIO1 | 130 | 2 | 1 | 0 | 6 | 25 |  |  | DI | [10 empty] | 2.1\0.6:25 | BR4-2150-E-00050 | A | BCV131BVS01-C4 2 PAIR | [7 empty] | F6 | 51 | 52
BSR130 | DX01 | DIO1 | 130 | 2 | 1 | 0 | 6 | 26 |  |  | DI | [10 empty] | 2.1\0.6:26 | [10 empty] | F6 | 53 | 54
BSR130 | DX01 | DIO1 | 130 | 2 | 1 | 0 | 6 | 27 |  |  | DI | [10 empty] | 2.1\0.6:27 | BR4-2150-E-00124 | 0 | [8 empty] | F6 | 55 | 56
BSR130 | DX01 | DIO1 | 130 | 2 | 1 | 0 | 6 | 28 |  |  | DI | [10 empty] | 2.1\0.6:28 | BR4-2150-E-00053 | A | BCV131CVS01-C4 2 PAIR | [7 empty] | F6 | 57 | 58
BSR130 | DX01 | DIO1 | 130 | 2 | 1 | 0 | 6 | 29 |  |  | DI | [10 empty] | 2.1\0.6:29 | BR4-2150-E-00053 | A | BCV131CVS01-C4 2 PAIR | [7 empty] | F6 | 59 | 60
BSR130 | DX01 | DIO1 | 130 | 2 | 1 | 0 | 6 | 30 |  |  | DI | [10 empty] | 2.1\0.6:30 | BR4-2150-E-00053 | A | BCV131CVS01-C4 2 PAIR | [7 empty] | F6 | 61 | 62
BSR130 | DX01 | DIO1 | 130 | 2 | 1 | 0 | 6 | 31 |  |  | DI | [10 empty] | 2.1\0.6:31 | [10 empty] | F6 | 63 | 64
BSR130 | DX01 | DIO1 | 130 | 2 | 1 | 0 | 7 | 0 | BMXFTB2010 | BMXDDO1602 | DO |  | 4 | BAF130HT01 | SR01 |  | Start Relay |  |  | BAF130HT01 |  | 2.1\0.7:0 | BR4-2110-E-00057 | A | [8 empty] | F7 | 1 | 2
BSR130 | DX01 | DIO1 | 130 | 2 | 1 | 0 | 7 | 1 |  |  | DO |  | 4 | BAF130HT02 | SR01 |  | Start Relay |  |  | BAF130HT02 |  | 2.1\0.7:1 | BR4-2110-E-00050 | A | [8 empty] | F7 | 3 | 4
BSR130 | DX01 | DIO1 | 130 | 2 | 1 | 0 | 7 | 2 |  |  | DO |  | 5 | BCV130MT01EM01 | SHT01 |  | Shunt Trip |  |  | BCV130MT01EM01 |  | 2.1\0.7:2 | BR4-2110-E-00236_0 | RL | [8 empty] | F7 | 5 | 6
BSR130 | DX01 | DIO1 | 130 | 2 | 1 | 0 | 7 | 3 |  |  | DO |  | 5 | BCV130MT01EM02 | SHT01 |  | Shunt Trip |  |  | BCV130MT01EM02 |  | 2.1\0.7:3 | BR4-2110-E-00237_0 | RL | [8 empty] | F7 | 7 | 8
BSR130 | DX01 | DIO1 | 130 | 2 | 1 | 0 | 7 | 4 |  |  | DO | [10 empty] | 2.1\0.7:4 | [10 empty] | F7 | 9 | 10
BSR130 | DX01 | DIO1 | 130 | 2 | 1 | 0 | 7 | 5 |  |  | DO | [10 empty] | 2.1\0.7:5 | [10 empty] | F7 | 11 | 12
BSR130 | DX01 | DIO1 | 130 | 2 | 1 | 0 | 7 | 6 |  |  | DO | [10 empty] | 2.1\0.7:6 | [10 empty] | F7 | 13 | 14
BSR130 | DX01 | DIO1 | 130 | 2 | 1 | 0 | 7 | 7 |  |  | DO | [10 empty] | 2.1\0.7:7 | [10 empty] | F7 | 15 | 16
BSR130 | DX01 | DIO1 | 130 | 2 | 1 | 0 | 7 | 8 |  |  | DO | [10 empty] | 2.1\0.7:8 | [10 empty] | F7 | 17 | 18
BSR130 | DX01 | DIO1 | 130 | 2 | 1 | 0 | 7 | 9 |  |  | DO | [10 empty] | 2.1\0.7:9 | [10 empty] | F7 | 19 | 20
BSR130 | DX01 | DIO1 | 130 | 2 | 1 | 0 | 7 | 10 |  |  | DO | [10 empty] | 2.1\0.7:10 | [10 empty] | F7 | 21 | 22
BSR130 | DX01 | DIO1 | 130 | 2 | 1 | 0 | 7 | 11 |  |  | DO | [10 empty] | 2.1\0.7:11 | [10 empty] | F7 | 23 | 24
BSR130 | DX01 | DIO1 | 130 | 2 | 1 | 0 | 7 | 12 |  |  | DO | [10 empty] | 2.1\0.7:12 | [10 empty] | F7 | 25 | 26
BSR130 | DX01 | DIO1 | 130 | 2 | 1 | 0 | 7 | 13 |  |  | DO | [10 empty] | 2.1\0.7:13 | [10 empty] | F7 | 27 | 28
BSR130 | DX01 | DIO1 | 130 | 2 | 1 | 0 | 7 | 14 |  |  | DO | [10 empty] | 2.1\0.7:14 | [10 empty] | F7 | 29 | 30
BSR130 | DX01 | DIO1 | 130 | 2 | 1 | 0 | 7 | 15 |  |  | DO |  | 4 | BSR130DB01 | SR01 |  | Lighting Control Relay |  |  | BSR130DB01 |  | 2.1\0.7:15 | [10 empty] | F7 | 31 | 32
BSR130 | DX01 | DIO1 | 130 | 2 | 1 | 0 | 8 | 0 |  | BMXX0 | [11 empty] | 2.1\0.8:0
BSR130 | DX01 | DIO1 | 130 | 2 | 1 | 0 | 8 | 1 | [13 empty] | 2.1\0.8:1
BSR130 | DX01 | DIO1 | 130 | 2 | 1 | 0 | 8 | 2 | [13 empty] | 2.1\0.8:2
BSR130 | DX01 | DIO1 | 130 | 2 | 1 | 0 | 8 | 3 | [13 empty] | 2.1\0.8:3
BSR130 | DX01 | DIO1 | 130 | 2 | 1 | 0 | 9 | 0 |  | BMXX0 | [11 empty] | 2.1\0.9:0
BSR130 | DX01 | DIO1 | 130 | 2 | 1 | 0 | 9 | 1 | [13 empty] | 2.1\0.9:1
BSR130 | DX01 | DIO1 | 130 | 2 | 1 | 0 | 9 | 2 | [13 empty] | 2.1\0.9:2
BSR130 | DX01 | DIO1 | 130 | 2 | 1 | 0 | 9 | 3 | [13 empty] | 2.1\0.9:3
BSR130 | DX01 | DIO1 | 130 | 2 | 1 | 0 | 10 | 0 |  | BMXX0 | [11 empty] | 2.1\0.10:0
BSR130 | DX01 | DIO1 | 130 | 2 | 1 | 0 | 10 | 1 | [13 empty] | 2.1\0.10:1
BSR130 | DX01 | DIO1 | 130 | 2 | 1 | 0 | 10 | 2 | [13 empty] | 2.1\0.10:2
BSR130 | DX01 | DIO1 | 130 | 2 | 1 | 0 | 10 | 3 | [13 empty] | 2.1\0.10:3
BSR130 | DX01 | DIO1 | 130 | 2 | 1 | 0 | 11 | 0 |  | BMXX0 | [11 empty] | 2.1\0.11:0
BSR130 | DX01 | DIO1 | 130 | 2 | 1 | 0 | 11 | 1 | [13 empty] | 2.1\0.11:1
BSR130 | DX01 | DIO1 | 130 | 2 | 1 | 0 | 11 | 2 | [13 empty] | 2.1\0.11:2
BSR130 | DX01 | DIO1 | 130 | 2 | 1 | 0 | 11 | 3 | [13 empty] | 2.1\0.11:3
BSR130 | DX01 |  | 130 | [6 empty] | PNOZs4 |  |  | 4 |  |  |  | BAF130 DX04 Summary of Devices |  | K103-1 | BAF130 | [12 empty] | F12 | 1 | 2 | 3 | 4
BSR130 | DX01 |  | 130 | [6 empty] | PNOZs4 |  |  | 4 |  |  |  | BAF130HP01 field LOS (BAF130HP01LCS02) to subDX relay |  | K130-1 | BAF130 | [12 empty] | F12 | 5 | 6 | 7 | 8
[13 empty] | 4 |  |  |  | BAF130LU01 field LOS to BAF130PP07 bucket |  | field link | BAF130 | [12 empty] | F12 | 9 | 10 | 11 | 12
[13 empty] | 4 |  |  |  | Field LOS to BVG130 bucket |  | field link | BVG130 | [12 empty] | F12 | 13 | 14 | 15 | 16
|  |  | 130 | [6 empty] | PNOZs4 |  |  | 4 |  |  |  | BAF130HP01 MASTER to BAF130PP01 bucket |  | K103-1 | BAF130 | [12 empty] | F12 | 17 | 18 | 19 | 20
|  |  | 130 | [6 empty] | PNOZs7.1 |  |  | 4 |  |  |  | BAF130HP01 MASTER to BAF130PP02 bucket |  | K103-2 | BAF130 | [12 empty] | F12 | 21 | 22 | 23 | 24
|  |  | 130 | [6 empty] | PNOZs7.2 |  |  | 4 |  |  |  | BAF130HP01 MASTER to BAF130PP04 bucket |  | K103-3 | BAF130 | [12 empty] | F12 | 25 | 26 | 27 | 28
|  |  | 130 | [6 empty] | PNOZs4 |  |  | 4 |  |  |  | BAF130FN01 MASTER (to BAF130FN01 bucket) |  | K130-1 | BAF130 | [12 empty] | F12 | 29 | 30 | 31 | 32
|  |  | 130 | [6 empty] | PNOZs7.1 |  |  | 4 |  |  |  | BAF130FN01 master to BAF130FN02 bucket |  | K130-2 | BAF130 | [12 empty] | F12 | 33 | 34 | 35 | 36
|  |  | 130 | [6 empty] | PNOZs7.2 |  |  | 4 |  |  |  | BAF130FN01 master to BAF130FN03 bucket |  | K130-3 | BAF130 | [12 empty] | F12 | 37 | 38 | 39 | 40
|  |  | 130 | [6 empty] | PNOZs4 |  |  | 4 |  |  |  | BJC130 MASTER to VSD SAFE TORQUE OFF |  | K203 | BJC130 | [12 empty] | F12 | 41 | 42 | 43 | 44
|  |  | 130 | [6 empty] | PNOZs4 |  |  | 4 |  |  |  | BJC130 DX05 Summary of Devices |  | K203 | BJC130 | [12 empty] | F12 | 45 | 50 | 51 | 52
[13 empty] | 4 |  |  |  | Field LOS to BJC130 bucket |  | field link | BJC130PP01 | [12 empty] | F12 | 49 | 50 | 51 | 52
[33 empty] | F12 | 53 | 54 | 55 | 56
[33 empty] | F12 | 53 | 54 | 55 | 56
[33 empty] | F12 | 57 | 58 | 59 | 60
[33 empty] | F12 | 65 | 66 | 67 | 68
[33 empty] | F12 | 69 | 70 | 71 | 72
[33 empty] | F12 | 73 | 74 | 75 | 76
[33 empty] | F12 | 77 | 78 | 79 | 80
[33 empty] | F12 | 81 | 82 | 83 | 84
[33 empty] | F12 | 85 | 86 | 87 | 88
[33 empty] | F12 | 89 | 90 | 91 | 92
[33 empty] | F12 | 93 | 94 | 95 | 96
[33 empty] | F12 | 97 | 98 | 99 | 100
[10 empty] | PNOZs4 |  |  | 4 |  |  |  | BAF130GA01 DX06 Summary of Devices |  | K303 | BAF130GA01 | [12 empty] | F12 | 101 | 102 | 103 | 104
[13 empty] | 4 |  |  |  | BAF130GA01 MASTER to BAF130PP05 bucket |  | K303 | [13 empty] | F12 | 105 | 106 | 107 | 108
[13 empty] | 4 |  |  |  | Field LOS to BDU130RV01 bucket |  | field link | [13 empty] | F12 | 109 | 110 | 111 | 112
[13 empty] | 4 |  |  |  | Field LOS to BDU130RV01 bucket |  | field link | [13 empty] | F12 | 113 | 114 | 115 | 116
[13 empty] | 4 | [6 empty] | BAF130GA01 | [12 empty] | F12 | 117 | 118 | 119 | 120
[33 empty] | F12 | 121 | 122 | 123
|  | TeSysT |  |  |  | PR | 1 | 1 | C / I1 | TeSysT | DI |  | 4 |  | CB01 |  | Drive Circuit Breaker | Closed | Q103 | BAF130PP07 |  |  | BR4-2110-E-00050 | A
[6 empty] | PR | 1 | 2 | C / I2 | DX01ES01 | DI |  | 5 |  | TRP02 |  | Drive Circuit Breaker | Tripped | Q103 | BAF130PP07 |  |  | BR4-2110-E-00050 | A
[6 empty] | PR | 1 | 3 | C / I3 |  | DI |  | 5 |  | CAX01 |  | Drive Contactor | Closed | K148 | BAF130PP07 |  |  | BR4-2110-E-00050 | A
[6 empty] | PR | 1 | 4 | C / I4 |  | DI |  | 4 |  | SY01 |  | Safety Interlock Relay | Healthy | K165 | BAF130PP07 |  |  | BR4-2110-E-00050 | A
[6 empty] | PR | 1 | 5 | C / I5 |  | DI | [8 empty] | BAF130PP07 |  |  | BR4-2110-E-00050 | A
[6 empty] | PR | 1 | 6 | C / I6 |  | DI |  | 4 |  | SW01 |  | Remote Mode | Selected |  | BAF130PP07 |  |  | BR4-2110-E-00050 | A
[6 empty] | PR | 1 | 1 | 13 / 14 |  | DO |  | 4 |  | SR01 |  | Start Relay | Closed | K159 | BAF130PP07 |  |  | BR4-2110-E-00050 | A
[6 empty] | PR | 1 | 2 | 23 / 24 |  | DO |  | 5 |  | SHT01 |  | Shunt Trip | Activated | K161 | BAF130PP07 |  |  | BR4-2110-E-00050 | A
[6 empty] | PR | 1 | 3 | 33 / 34 |  | DO |  | 5 | [6 empty] | BAF130PP07 |  |  | BR4-2110-E-00050 | A
[6 empty] | PR | 1 | 4 | 95 / 96 |  | DO |  | 5 |  | TRP01 |  | Drive Circuit Breaker | Trip | Q103 | BAF130PP07 |  |  | BR4-2110-E-00050 | A
|  | TeSysT |  |  |  | PR | 1 | 1 | C / I1 | TeSysT | DI |  | 4 |  | CB01 |  | Drive Circuit Breaker | Closed | Q103 | BAF130PP01 |  |  | BR4-2110-E-00051 | 0
[6 empty] | PR | 1 | 2 | C / I2 | DX01ES01 | DI |  | 5 |  | TRP02 |  | Drive Circuit Breaker | Tripped | Q103 | BAF130PP01 |  |  | BR4-2110-E-00051 | 0
[6 empty] | PR | 1 | 3 | C / I3 |  | DI |  | 4 |  | CAX01 |  | Drive Contactor | Closed | K148 | BAF130PP01 |  |  | BR4-2110-E-00051 | 0
[6 empty] | PR | 1 | 4 | C / I4 |  | DI |  | 4 |  | SY01 |  | Safety Interlock Relay | Healthy | K165 | BAF130PP01 |  |  | BR4-2110-E-00051 | 0
[6 empty] | PR | 1 | 5 | C / I5 |  | DI |  | 5 | [6 empty] | BAF130PP01 |  |  | BR4-2110-E-00051 | 0
[6 empty] | PR | 1 | 6 | C / I6 |  | DI |  | 4 |  | SW01 |  | Remote Mode | Selected |  | BAF130PP01 |  |  | BR4-2110-E-00051 | 0
[6 empty] | PR | 1 | 1 | 13 / 14 |  | DO |  | 4 |  | SR01 |  | Start Relay | Closed | K159 | BAF130PP01 |  |  | BR4-2110-E-00051 | 0
[6 empty] | PR | 1 | 2 | 23 / 24 |  | DO |  | 5 |  | SHT01 |  | Shunt Trip | Activated | K161 | BAF130PP01
[6 empty] | PR | 1 | 3 | 33 / 34 |  | DO |  | 5 | [6 empty] | BAF130PP01
[6 empty] | PR | 1 | 4 | 95 / 96 |  | DO |  | 5 |  | TRP01 |  | Drive Circuit Breaker | Trip | Q103 | BAF130PP01
[6 empty] | PR | 1 | 7 | C / I7 |  | DI |  | 5 | [6 empty] | BAF130PP01
[6 empty] | PR | 1 | 8 | C / I8 |  | DI |  | 5 |  | VAC01 |  | 240VAC Supply OK | Healthy | K146 | BAF130PP01
[6 empty] | PR | 1 | 9 | C / I9 |  | DI |  | 5 | [6 empty] | BAF130PP01
[6 empty] | PR | 1 | 10 | C / I10 |  | DI |  | 5 | [6 empty] | BAF130PP01
|  | TeSysT |  |  |  | PR | 1 | 1 | C / I1 | TeSysT | DI |  | 4 |  | CB01 |  | Drive Circuit Breaker | Closed | Q103 | BAF130PP02 |  |  | BR4-2110-E-00052 | 0
[6 empty] | PR | 1 | 2 | C / I2 | DX01ES01 | DI |  | 5 |  | TRP02 |  | Drive Circuit Breaker | Tripped | Q103 | BAF130PP02 |  |  | BR4-2110-E-00052 | 0
[6 empty] | PR | 1 | 3 | C / I3 |  | DI |  | 4 |  | CAX01 |  | Drive Contactor | Closed | K148 | BAF130PP02 |  |  | BR4-2110-E-00052 | 0
[6 empty] | PR | 1 | 4 | C / I4 |  | DI |  | 4 |  | SY01 |  | Safety Interlock Relay | Healthy | K165 | BAF130PP02 |  |  | BR4-2110-E-00052 | 0
[6 empty] | PR | 1 | 5 | C / I5 |  | DI |  | 5 | [6 empty] | BAF130PP02 |  |  | BR4-2110-E-00052 | 0
[6 empty] | PR | 1 | 6 | C / I6 |  | DI |  | 4 |  | SW01 |  | Remote Mode | Selected |  | BAF130PP02 |  |  | BR4-2110-E-00052 | 0
[6 empty] | PR | 1 | 1 | 13 / 14 |  | DO |  | 4 |  | SR01 |  | Start Relay | Closed | K159 | BAF130PP02 |  |  | BR4-2110-E-00052 | 0
[6 empty] | PR | 1 | 2 | 23 / 24 |  | DO |  | 5 |  | SHT01 |  | Shunt Trip | Activated | K161 | BAF130PP02
[6 empty] | PR | 1 | 3 | 33 / 34 |  | DO |  | 5 | [6 empty] | BAF130PP02
[6 empty] | PR | 1 | 4 | 95 / 96 |  | DO |  | 5 |  | TRP01 |  | Drive Circuit Breaker | Trip | Q103 | BAF130PP02
[6 empty] | PR | 1 | 7 | C / I7 |  | DI |  | 5 | [6 empty] | BAF130PP02
[6 empty] | PR | 1 | 8 | C / I8 |  | DI |  | 5 |  | VAC01 |  | 240VAC Supply OK | Healthy | K146 | BAF130PP02
[6 empty] | PR | 1 | 9 | C / I9 |  | DI |  | 5 | [6 empty] | BAF130PP02
[6 empty] | PR | 1 | 10 | C / I10 |  | DI |  | 5 | [6 empty] | BAF130PP02
|  | TeSysT |  |  |  | PR | 1 | 1 | C / I1 | TeSysT | DI |  | 4 |  | CB01 |  | Drive Circuit Breaker | Closed | Q103 | BAF130PP04 |  |  | BR4-2110-E-00053 | A
[6 empty] | PR | 1 | 2 | C / I2 | DX01ES01 | DI |  | 5 |  | TRP02 |  | Drive Circuit Breaker | Tripped | Q103 | BAF130PP04 |  |  | BR4-2110-E-00053 | A
[6 empty] | PR | 1 | 3 | C / I3 |  | DI |  | 5 |  | CAX01 |  | Drive Contactor | Closed | K148 | BAF130PP04 |  |  | BR4-2110-E-00053 | A
[6 empty] | PR | 1 | 4 | C / I4 |  | DI |  | 4 |  | SY01 |  | Safety Interlock Relay | Healthy | K165 | BAF130PP04 |  |  | BR4-2110-E-00053 | A
[6 empty] | PR | 1 | 5 | C / I5 |  | DI | [8 empty] | BAF130PP04 |  |  | BR4-2110-E-00053 | A
[6 empty] | PR | 1 | 6 | C / I6 |  | DI |  | 4 |  | SW01 |  | Remote Mode | Selected |  | BAF130PP04 |  |  | BR4-2110-E-00053 | A
[6 empty] | PR | 1 | 1 | 13 / 14 |  | DO |  | 4 |  | SR01 |  | Start Relay | Closed | K159 | BAF130PP04 |  |  | BR4-2110-E-00053 | A
[6 empty] | PR | 1 | 2 | 23 / 24 |  | DO |  | 5 |  | SHT01 |  | Shunt Trip | Activated | K161 | BAF130PP04 |  |  | BR4-2110-E-00053 | A
[6 empty] | PR | 1 | 3 | 33 / 34 |  | DO |  | 5 | [6 empty] | BAF130PP04 |  |  | BR4-2110-E-00053 | A
[6 empty] | PR | 1 | 4 | 95 / 96 |  | DO |  | 5 |  | TRP01 |  | Drive Circuit Breaker | Trip | Q103 | BAF130PP04 |  |  | BR4-2110-E-00053 | A
|  | TeSysT |  |  |  | PR | 1 | 1 | C / I1 | TeSysT | DI |  | 4 |  | CB01 |  | Drive Circuit Breaker | Closed | Q103 | BAF130FN01 |  |  | BR4-2110-E-00054 | A
[6 empty] | PR | 1 | 2 | C / I2 | DX01ES01 | DI |  | 5 |  | TRP02 |  | Drive Circuit Breaker | Tripped | Q103 | BAF130FN01 |  |  | BR4-2110-E-00054 | A
[6 empty] | PR | 1 | 3 | C / I3 |  | DI |  | 5 |  | CAX01 |  | Drive Contactor | Closed | K148 | BAF130FN01 |  |  | BR4-2110-E-00054 | A
[6 empty] | PR | 1 | 4 | C / I4 |  | DI |  | 4 |  | SY01 |  | Safety Interlock Relay | Healthy | K165 | BAF130FN01 |  |  | BR4-2110-E-00054 | A
[6 empty] | PR | 1 | 5 | C / I5 |  | DI | [8 empty] | BAF130FN01 |  |  | BR4-2110-E-00054 | A
[6 empty] | PR | 1 | 6 | C / I6 |  | DI |  | 4 |  | SW01 |  | Remote Mode | Selected |  | BAF130FN01 |  |  | BR4-2110-E-00054 | A
[6 empty] | PR | 1 | 1 | 13 / 14 |  | DO |  | 4 |  | SR01 |  | Start Relay | Closed | K159 | BAF130FN01 |  |  | BR4-2110-E-00054 | A
[6 empty] | PR | 1 | 2 | 23 / 24 |  | DO |  | 5 |  | SHT01 |  | Shunt Trip | Activated | K161 | BAF130FN01 |  |  | BR4-2110-E-00054 | A
[6 empty] | PR | 1 | 3 | 33 / 34 |  | DO |  | 5 | [6 empty] | BAF130FN01 |  |  | BR4-2110-E-00054 | A
[6 empty] | PR | 1 | 4 | 95 / 96 |  | DO |  | 5 |  | TRP01 |  | Drive Circuit Breaker | Trip | Q103 | BAF130FN01 |  |  | BR4-2110-E-00054 | A
|  | TeSysT |  |  |  | PR | 1 | 1 | C / I1 | TeSysT | DI |  | 4 |  | CB01 |  | Drive Circuit Breaker | Closed | Q103 | BAF130FN02 |  |  | BR4-2110-E-00055 | A
[6 empty] | PR | 1 | 2 | C / I2 | DX01ES01 | DI |  | 5 |  | TRP02 |  | Drive Circuit Breaker | Tripped | Q103 | BAF130FN02 |  |  | BR4-2110-E-00055 | A
[6 empty] | PR | 1 | 3 | C / I3 |  | DI |  | 5 |  | CAX01 |  | Drive Contactor | Closed | K148 | BAF130FN02 |  |  | BR4-2110-E-00055 | A
[6 empty] | PR | 1 | 4 | C / I4 |  | DI |  | 4 |  | SY01 |  | Safety Interlock Relay | Healthy | K165 | BAF130FN02 |  |  | BR4-2110-E-00055 | A
[6 empty] | PR | 1 | 5 | C / I5 |  | DI | [8 empty] | BAF130FN02 |  |  | BR4-2110-E-00055 | A
[6 empty] | PR | 1 | 6 | C / I6 |  | DI |  | 4 |  | SW01 |  | Remote Mode | Selected |  | BAF130FN02 |  |  | BR4-2110-E-00055 | A
[6 empty] | PR | 1 | 1 | 13 / 14 |  | DO |  | 4 |  | SR01 |  | Start Relay | Closed | K159 | BAF130FN02 |  |  | BR4-2110-E-00055 | A
[6 empty] | PR | 1 | 2 | 23 / 24 |  | DO |  | 5 |  | SHT01 |  | Shunt Trip | Activated | K161 | BAF130FN02 |  |  | BR4-2110-E-00055 | A
[6 empty] | PR | 1 | 3 | 33 / 34 |  | DO |  | 5 | [6 empty] | BAF130FN02 |  |  | BR4-2110-E-00055 | A
[6 empty] | PR | 1 | 4 | 95 / 96 |  | DO |  | 5 |  | TRP01 |  | Drive Circuit Breaker | Trip | Q103 | BAF130FN02 |  |  | BR4-2110-E-00055 | A
|  | TeSysT |  |  |  | PR | 1 | 1 | C / I1 | TeSysT | DI |  | 4 |  | CB01 |  | Drive Circuit Breaker | Closed | Q103 | BAF130FN03 |  |  | BR4-2110-E-00062 | A
[6 empty] | PR | 1 | 2 | C / I2 | DX01ES01 | DI |  | 5 |  | TRP02 |  | Drive Circuit Breaker | Tripped | Q103 | BAF130FN03 |  |  | BR4-2110-E-00062 | A
[6 empty] | PR | 1 | 3 | C / I3 |  | DI |  | 5 |  | CAX01 |  | Drive Contactor | Closed | K148 | BAF130FN03 |  |  | BR4-2110-E-00062 | A
[6 empty] | PR | 1 | 4 | C / I4 |  | DI |  | 4 |  | SY01 |  | Safety Interlock Relay | Healthy | K165 | BAF130FN03 |  |  | BR4-2110-E-00062 | A
[6 empty] | PR | 1 | 5 | C / I5 |  | DI | [8 empty] | BAF130FN03 |  |  | BR4-2110-E-00062 | A
[6 empty] | PR | 1 | 6 | C / I6 |  | DI |  | 4 |  | SW01 |  | Remote Mode | Selected |  | BAF130FN03 |  |  | BR4-2110-E-00062 | A
[6 empty] | PR | 1 | 1 | 13 / 14 |  | DO |  | 4 |  | SR01 |  | Start Relay | Closed | K159 | BAF130FN03 |  |  | BR4-2110-E-00062 | A
[6 empty] | PR | 1 | 2 | 23 / 24 |  | DO |  | 5 |  | SHT01 |  | Shunt Trip | Activated | K161 | BAF130FN03 |  |  | BR4-2110-E-00062 | A
[6 empty] | PR | 1 | 3 | 33 / 34 |  | DO |  | 5 | [6 empty] | BAF130FN03 |  |  | BR4-2110-E-00062 | A
[6 empty] | PR | 1 | 4 | 95 / 96 |  | DO |  | 5 |  | TRP01 |  | Drive Circuit Breaker | Trip | Q103 | BAF130FN03 |  |  | BR4-2110-E-00062 | A
|  | TeSysT |  |  |  | PR | 1 | 1 | C / I1 | TeSysT | DI |  | 4 |  | CB01 |  | Drive Circuit Breaker | Closed | Q103 | BAF130PP05 |  |  | BR4-2110-E-00056 | A
[6 empty] | PR | 1 | 2 | C / I2 | DX01ES01 | DI |  | 5 |  | TRP02 |  | Drive Circuit Breaker | Tripped | Q103 | BAF130PP05 |  |  | BR4-2110-E-00056 | A
[6 empty] | PR | 1 | 3 | C / I3 |  | DI |  | 5 |  | CAX01 |  | Drive Contactor | Closed | K148 | BAF130PP05 |  |  | BR4-2110-E-00056 | A
[6 empty] | PR | 1 | 4 | C / I4 |  | DI |  | 4 |  | SY01 |  | Safety Interlock Relay | Healthy | K165 | BAF130PP05 |  |  | BR4-2110-E-00056 | A
[6 empty] | PR | 1 | 5 | C / I5 |  | DI | [8 empty] | BAF130PP05 |  |  | BR4-2110-E-00056 | A
[6 empty] | PR | 1 | 6 | C / I6 |  | DI |  | 4 |  | SW01 |  | Remote Mode | Selected |  | BAF130PP05 |  |  | BR4-2110-E-00056 | A
[6 empty] | PR | 1 | 1 | 13 / 14 |  | DO |  | 4 |  | SR01 |  | Start Relay | Closed | K159 | BAF130PP05 |  |  | BR4-2110-E-00056 | A
[6 empty] | PR | 1 | 2 | 23 / 24 |  | DO |  | 5 |  | SHT01 |  | Shunt Trip | Activated | K161 | BAF130PP05 |  |  | BR4-2110-E-00056 | A
[6 empty] | PR | 1 | 3 | 33 / 34 |  | DO |  | 5 | [6 empty] | BAF130PP05 |  |  | BR4-2110-E-00056 | A
[6 empty] | PR | 1 | 4 | 95 / 96 |  | DO |  | 5 |  | TRP01 |  | Drive Circuit Breaker | Trip | Q103 | BAF130PP05 |  |  | BR4-2110-E-00056 | A
|  | TeSysT |  |  |  | PR | 1 | 1 | C / I1 | TeSysT | DI |  | 4 |  | CB01 |  | Drive Circuit Breaker | Closed | Q103 | BDU130FN01 |  |  | BR4-2110-E-00058 | A
[6 empty] | PR | 1 | 2 | C / I2 | DX01ES01 | DI |  | 5 |  | TRP02 |  | Drive Circuit Breaker | Tripped | Q103 | BDU130FN01 |  |  | BR4-2110-E-00058 | A
[6 empty] | PR | 1 | 3 | C / I3 |  | DI |  | 4 |  | CAX01 |  | Drive Contactor | Closed | K148 | BDU130FN01 |  |  | BR4-2110-E-00058 | A
[6 empty] | PR | 1 | 4 | C / I4 |  | DI |  | 4 |  | SY01 |  | Safety Interlock Relay | Healthy | K165 | BDU130FN01 |  |  | BR4-2110-E-00058 | A
[6 empty] | PR | 1 | 5 | C / I5 |  | DI |  | 5 | [6 empty] | BDU130FN01
[6 empty] | PR | 1 | 6 | C / I6 |  | DI |  | 4 |  | SW01 |  | Remote Mode | Selected |  | BDU130FN01 |  |  | BR4-2110-E-00058 | A
[6 empty] | PR | 1 | 1 | 13 / 14 |  | DO |  | 4 |  | SR01 |  | Start Relay | Closed | K159 | BDU130FN01 |  |  | BR4-2110-E-00058 | A
[6 empty] | PR | 1 | 2 | 23 / 24 |  | DO |  | 5 |  | SHT01 |  | Shunt Trip | Activated | K161 | BDU130FN01
[6 empty] | PR | 1 | 3 | 33 / 34 |  | DO |  | 5 | [6 empty] | BDU130FN01
[6 empty] | PR | 1 | 4 | 95 / 96 |  | DO |  | 5 |  | TRP01 |  | Drive Circuit Breaker | Trip | Q103 | BDU130FN01
[6 empty] | PR | 1 | 7 | C / I7 |  | DI |  | 5 | [6 empty] | BDU130FN01
[6 empty] | PR | 1 | 8 | C / I8 |  | DI |  | 5 |  | VAC01 |  | 240VAC Supply OK | Healthy | K146 | BDU130FN01
[6 empty] | PR | 1 | 9 | C / I9 |  | DI |  | 5 | [6 empty] | BDU130FN01
[6 empty] | PR | 1 | 10 | C / I10 |  | DI |  | 5 | [6 empty] | BDU130FN01
|  | TeSysT |  |  |  | PR | 1 | 1 | C / I1 | TeSysT | DI |  | 4 |  | CB01 |  | Drive Circuit Breaker | Closed | Q103 | BDU130RV01 |  |  | BR4-2110-E-00059 | A
[6 empty] | PR | 1 | 2 | C / I2 | DX01ES01 | DI |  | 5 |  | TRP02 |  | Drive Circuit Breaker | Tripped | Q103 | BDU130RV01 |  |  | BR4-2110-E-00059 | A
[6 empty] | PR | 1 | 3 | C / I3 |  | DI |  | 5 |  | CAX01 |  | Drive Contactor | Closed | K148 | BDU130RV01 |  |  | BR4-2110-E-00059 | A
[6 empty] | PR | 1 | 4 | C / I4 |  | DI |  | 4 |  | SY01 |  | Safety Interlock Relay | Healthy | K165 | BDU130RV01 |  |  | BR4-2110-E-00059 | A
[6 empty] | PR | 1 | 5 | C / I5 |  | DI | [8 empty] | BDU130RV01 |  |  | BR4-2110-E-00059 | A
[6 empty] | PR | 1 | 6 | C / I6 |  | DI |  | 4 |  | SW01 |  | Remote Mode | Selected |  | BDU130RV01 |  |  | BR4-2110-E-00059 | A
[6 empty] | PR | 1 | 1 | 13 / 14 |  | DO |  | 4 |  | SR01 |  | Start Relay | Closed | K159 | BDU130RV01 |  |  | BR4-2110-E-00059 | A
[6 empty] | PR | 1 | 2 | 23 / 24 |  | DO |  | 5 |  | SHT01 |  | Shunt Trip | Activated | K161 | BDU130RV01 |  |  | BR4-2110-E-00059 | A
[6 empty] | PR | 1 | 3 | 33 / 34 |  | DO |  | 5 | [6 empty] | BDU130RV01 |  |  | BR4-2110-E-00059 | A
[6 empty] | PR | 1 | 4 | 95 / 96 |  | DO |  | 5 |  | TRP01 |  | Drive Circuit Breaker | Trip | Q103 | BDU130RV01 |  |  | BR4-2110-E-00059 | A
|  | TeSysT |  |  |  | PR | 1 | 1 | C / I1 | TeSysT | DI |  | 4 |  | CB01 |  | Drive Circuit Breaker | Closed | Q103 | BVG130DA01 |  |  | BR4-2110-E-00061 | A
[6 empty] | PR | 1 | 2 | C / I2 | DX01ES01 | DI |  | 5 |  | TRP02 |  | Drive Circuit Breaker | Tripped | Q103 | BVG130DA01 |  |  | BR4-2110-E-00061 | A
[6 empty] | PR | 1 | 3 | C / I3 |  | DI |  | 4 |  | CAX01 |  | Drive Contactor | Closed | K148 | BVG130DA01 |  |  | BR4-2110-E-00061 | A
[6 empty] | PR | 1 | 4 | C / I4 |  | DI |  | 4 |  | SY01 |  | Safety Interlock Relay | Healthy | K165 | BVG130DA01 |  |  | BR4-2110-E-00061 | A
[6 empty] | PR | 1 | 5 | C / I5 |  | DI |  | 5 | [6 empty] | BVG130DA01
[6 empty] | PR | 1 | 6 | C / I6 |  | DI |  | 4 |  | SW01 |  | Remote Mode | Selected |  | BVG130DA01 |  |  | BR4-2110-E-00061 | A
[6 empty] | PR | 1 | 1 | 13 / 14 |  | DO |  | 4 |  | SR01 |  | Start Relay | Closed | K159 | BVG130DA01 |  |  | BR4-2110-E-00061 | A
[6 empty] | PR | 1 | 2 | 23 / 24 |  | DO |  | 5 |  | SHT01 |  | Shunt Trip | Activated | K161 | BVG130DA01
[6 empty] | PR | 1 | 3 | 33 / 34 |  | DO |  | 5 | [6 empty] | BVG130DA01
[6 empty] | PR | 1 | 4 | 95 / 96 |  | DO |  | 5 |  | TRP01 |  | Drive Circuit Breaker | Trip | Q103 | BVG130DA01
[6 empty] | PR | 1 | 7 | C / I7 |  | DI |  | 5 | [6 empty] | BVG130DA01
[6 empty] | PR | 1 | 8 | C / I8 |  | DI |  | 5 |  | VAC01 |  | 240VAC Supply OK | Healthy | K146 | BVG130DA01
[6 empty] | PR | 1 | 9 | C / I9 |  | DI |  | 5 | [6 empty] | BVG130DA01
[6 empty] | PR | 1 | 10 | C / I10 |  | DI |  | 5 | [6 empty] | BVG130DA01
|  | TeSysT |  |  |  | PR | 1 | 1 | C / I1 | TeSysT | DI |  | 4 |  | CB01 |  | Drive Circuit Breaker | Closed | Q103 | BJC130PP01 |  |  | BR4-2110-E-00067 | A
[6 empty] | PR | 1 | 2 | C / I2 | DX01ES01 | DI |  | 5 |  | TRP02 |  | Drive Circuit Breaker | Tripped | Q103 | BJC130PP01 |  |  | BR4-2110-E-00067 | A
[6 empty] | PR | 1 | 3 | C / I3 |  | DI |  | 5 |  | CAX01 |  | Drive Contactor | Closed | K148 | BJC130PP01 |  |  | BR4-2110-E-00067 | A
[6 empty] | PR | 1 | 4 | C / I4 |  | DI |  | 4 |  | SY01 |  | Safety Interlock Relay | Healthy | K165 | BJC130PP01 |  |  | BR4-2110-E-00067 | A
[6 empty] | PR | 1 | 5 | C / I5 |  | DI | [8 empty] | BJC130PP01 |  |  | BR4-2110-E-00067 | A
[6 empty] | PR | 1 | 6 | C / I6 |  | DI |  | 4 |  | SW01 |  | Remote Mode | Selected |  | BJC130PP01 |  |  | BR4-2110-E-00067 | A
[6 empty] | PR | 1 | 1 | 13 / 14 |  | DO |  | 4 |  | SR01 |  | Start Relay | Closed | K159 | BJC130PP01 |  |  | BR4-2110-E-00067 | A
[6 empty] | PR | 1 | 2 | 23 / 24 |  | DO |  | 5 |  | SHT01 |  | Shunt Trip | Activated | K161 | BJC130PP01 |  |  | BR4-2110-E-00067 | A
[6 empty] | PR | 1 | 3 | 33 / 34 |  | DO |  | 5 | [6 empty] | BJC130PP01 |  |  | BR4-2110-E-00067 | A
[6 empty] | PR | 1 | 4 | 95 / 96 |  | DO |  | 5 |  | TRP01 |  | Drive Circuit Breaker | Trip | Q103 | BJC130PP01 |  |  | BR4-2110-E-00067 | A
|  | ACS880 |  |  |  |  | 1 | 1 | XDI:1 | ACS880 | DI |  | 4 |  | ENB01 |  | Run |  |  | BJC130 |  |  | BR4-2110-E-00069 | A
[7 empty] | 1 | 2 | XDI:2 |  | DI
[7 empty] | 1 | 3 | XDI:3 |  | DI |  | 4 |  | IS01 |  | Drive Isolator | Closed |  | BJC130 |  |  | BR4-2110-E-00069 | A
[7 empty] | 1 | 6 | XDI:6 |  | DI
[7 empty] | 1 |  | STO |  | DI |  | 4 |  | VS01SY01 |  | STO Relay | Healthy |  | BJC130 |  |  | BR4-2110-E-00069 | A
|  | PR |  |  |  |  | 1 |  |  | MASTERPACT_VAMP |  |  | 4 | [6 empty] | BMC1301INC01 |  |  | BR4-2110-E-00044 | A | Process Bus A Incomer
|  | PR |  |  |  |  | 1 |  | VAMP RJ45 | DX01ES01 |  |  | 4
|  | PR |  |  |  |  | 1 |  | CUB RJ45 | DX01ES01 |  |  | 4
BSR130DX02
EIO node 2
BSR130 | DX02 | DIO1 | 130 | 2 | 2 | 0 | 0 | Chassis |  | BMEXBP1200
BSR130 | DX02 | DIO1 | 130 | 2 | 2 | 0 | 0 | Power |  | BMXCPS4022 |  |  | total |  | spare |  | % spare
BSR130 | DX02 | DIO1 | 130 | 2 | 2 | 0 | 0 | Comms |  | BMECRA31210 | DX1ES1 |  | 160 |  | 111 |  | 69.38% |  |  |  |  | 2.2\0.0:Comms
BSR130 | DX02 | DIO1 | 130 | 2 | 2 | 0 | 1 | 0 | BMXFCW303 | BMXDDI3202K | DI |  | 4 | BSR130DX02 | XS01 |  | DX02 24VDC Power Supply 1 | Healthy | U103A | BSR130DX02 |  | 2.2\0.1:0 | BR4-2110-E-00081 | A | INTERNAL WIRING | [7 empty] | F21 | 1 | 2
BSR130 | DX02 | DIO1 | 130 | 2 | 2 | 0 | 1 | 1 |  |  | DI |  | 4 | BSR130DX02 | XS02 |  | DX02 24VDC Power Supply 2 | Healthy | U103B | BSR130DX02 |  | 2.2\0.1:1 | BR4-2110-E-00081 | A | [8 empty] | F21 | 3 | 4
BSR130 | DX02 | DIO1 | 130 | 2 | 2 | 0 | 1 | 2 |  |  | DI | [10 empty] | 2.2\0.1:2 | [10 empty] | F21 | 5 | 6
BSR130 | DX02 | DIO1 | 130 | 2 | 2 | 0 | 1 | 3 |  |  | DI |  | 4 | BMC1302INC01 | VDC01 |  | BMC1302 24VDC Control Supply | Healthy | Q267 | BMC1302INC01 |  | 2.2\0.1:3 | BR4-2110-E-00223 |  | BMC1302INC01-C1 8 PAIR | [7 empty] | F21 | 7 | 8
BSR130 | DX02 | DIO1 | 130 | 2 | 2 | 0 | 1 | 4 |  |  | DI |  | 4 | BMC1302INC01 | CB02 |  | BMC1302 Arc Flash Supply | Healthy | Q204 | BMC1302INC01 |  | 2.2\0.1:4 | BR4-2110-E-00223 | [9 empty] | F21 | 9 | 10
BSR130 | DX02 | DIO1 | 130 | 2 | 2 | 0 | 1 | 5 |  |  | DI |  | 4 | BMC1302INC01 | TRP02 |  | BMC1302 Arc Flash Trip Alarm | Healthy |  | BMC1302INC01 |  | 2.2\0.1:5 | BR4-2110-E-00223 | [9 empty] | F21 | 11 | 12
BSR130 | DX02 | DIO1 | 130 | 2 | 2 | 0 | 1 | 6 |  |  | DI |  | 4 | BMC1302INC01 | XS02 |  | BMC1302 Arc Flash System | Healthy |  | BMC1302INC01 |  | 2.2\0.1:6 | BR4-2110-E-00223 | [9 empty] | F21 | 13 | 14
BSR130 | DX02 | DIO1 | 130 | 2 | 2 | 0 | 1 | 7 |  |  | DI |  | 4 | BMC1302INC01 | CB03 |  | BMC1302 INC01 Spring Charge Supply OK | Healthy | Q212 | BMC1302INC01 |  | 2.2\0.1:7 | BR4-2110-E-00223 | [9 empty] | F21 | 15 | 16
BSR130 | DX02 | DIO1 | 130 | 2 | 2 | 0 | 1 | 8 |  |  | DI |  | 4 | BMC1302INC01 | CB04 |  | BMC1302 INC01 Trip Supply OK | Healthy | Q220 | BMC1302INC01 |  | 2.2\0.1:8 | BR4-2110-E-00223 | [9 empty] | F21 | 17 | 18
BSR130 | DX02 | DIO1 | 130 | 2 | 2 | 0 | 1 | 9 |  |  | DI |  | 4 | BMC1302INC01 | CB05 |  | BMC1302 INC01 Circuit Breaker 24VDC Cubicle Bus Supply OK | Healthy | Q256 | BMC1302INC01 |  | 2.2\0.1:9 | BR4-2110-E-00223 | [9 empty] | F21 | 19 | 20
BSR130 | DX02 | DIO1 | 130 | 2 | 2 | 0 | 1 | 10 |  |  | DI |  | 4 | BMC1302INC01 | XS03 |  | BMC1302 INC01 Surge Protection | Healthy | SD144-146 | BMC1302INC01 |  | 2.2\0.1:10 | BR4-2110-E-00223 | [9 empty] | F21 | 21 | 22
BSR130 | DX02 | DIO1 | 130 | 2 | 2 | 0 | 1 | 11 |  |  | DI |  | 4 | BMC1302INC01 | CB06 |  | BMC1302 INC01 110/24VDC Power Supply | Healthy | Q215 | BMC1302INC01 |  | 2.2\0.1:11 | BR4-2110-E-00223 | [9 empty] | F21 | 23 | 24
BSR130 | DX02 | DIO1 | 130 | 2 | 2 | 0 | 1 | 12 |  |  | DI | [10 empty] | 2.2\0.1:12 | [10 empty] | F21 | 25 | 26
BSR130 | DX02 | DIO1 | 130 | 2 | 2 | 0 | 1 | 13 |  |  | DI |  | 4 | BMC1302INC02 | VDC01 |  | BMC1302 Essential Bus 24VDC Control Supply | Healthy | Q267 | BMC1302INC02 |  | 2.2\0.1:13 | BR4-2110-E-00225 |  | BMC1302INC02-C1 8 PAIR (3 SPARE) | [7 empty] | F21 | 27 | 28
BSR130 | DX02 | DIO1 | 130 | 2 | 2 | 0 | 1 | 14 |  |  | DI |  | 4 | BMC1302INC02 | CB03 |  | BMC1302 Essential Bus INC02 Spring Charge Supply OK | Healthy | Q212 | BMC1302INC02 |  | 2.2\0.1:14 | BR4-2110-E-00225 | [9 empty] | F21 | 29 | 30
BSR130 | DX02 | DIO1 | 130 | 2 | 2 | 0 | 1 | 15 |  |  | DI |  | 4 | BMC1302INC02 | CB04 |  | BMC1302 Essential Bus INC02 Trip Supply OK | Healthy | Q220 | BMC1302INC02 |  | 2.2\0.1:15 | BR4-2110-E-00225 | [9 empty] | F21 | 31 | 32
BSR130 | DX02 | DIO1 | 130 | 2 | 2 | 0 | 1 | 16 |  |  | DI |  | 4 | BMC1302INC02 | CB05 |  | BMC1302 Essential Bus INC02 24VDC Cubicle Bus Supply OK | Healthy | Q256 | BMC1302INC02 |  | 2.2\0.1:16 | BR4-2110-E-00225 | [9 empty] | F21 | 33 | 34
BSR130 | DX02 | DIO1 | 130 | 2 | 2 | 0 | 1 | 17 |  |  | DI |  | 4 | BMC1302INC02 | XS03 |  | BMC1302 Essential Bus INC02 Surge Protection | Healthy | SD144-146 | BMC1302INC02 |  | 2.2\0.1:17 | BR4-2110-E-00225 | [9 empty] | F21 | 35 | 36
BSR130 | DX02 | DIO1 | 130 | 2 | 2 | 0 | 1 | 18 |  |  | DI |  | 4 | BMC1302INC02 | CB06 |  | BMC1302 Essential Bus INC02 110/24VDC Power Supply | Healthy | Q215 | BMC1302INC02 |  | 2.2\0.1:18 | BR4-2110-E-00225 | [9 empty] | F21 | 37 | 38
BSR130 | DX02 | DIO1 | 130 | 2 | 2 | 0 | 1 | 19 |  |  | DI |  | 4 | BMC1302INC03 | VDC01 |  | BMC1302 INC03 Bus 24VDC Control Supply | Healthy | Q267 | BMC1302INC03 |  | 2.2\0.1:19 | BR4-2110-E-00227 |  | BMC1302INC03-C1 8 PAIR (2 SPARE) | [7 empty] | F21 | 39 | 40
BSR130 | DX02 | DIO1 | 130 | 2 | 2 | 0 | 1 | 20 |  |  | DI |  | 4 | BMC1302INC03 | TRP02 |  | BMC1302 INC03 Arc Flash Trip Alarm | Healthy | F110 | BMC1302INC03 |  | 2.2\0.1:20 | BR4-2110-E-00227 | [9 empty] | F21 | 41 | 42
BSR130 | DX02 | DIO1 | 130 | 2 | 2 | 0 | 1 | 21 |  |  | DI |  | 4 | BMC1302INC03 | CB03 |  | BMC1302 INC03 Bus INC03 Spring Charge Supply OK | Healthy | Q212 | BMC1302INC03 |  | 2.2\0.1:21 | BR4-2110-E-00227 | [9 empty] | F21 | 43 | 44
BSR130 | DX02 | DIO1 | 130 | 2 | 2 | 0 | 1 | 22 |  |  | DI |  | 4 | BMC1302INC03 | CB04 |  | BMC1302 INC03 Bus INC03 Trip Supply OK | Healthy | Q220 | BMC1302INC03 |  | 2.2\0.1:22 | BR4-2110-E-00227 | [9 empty] | F21 | 45 | 46
BSR130 | DX02 | DIO1 | 130 | 2 | 2 | 0 | 1 | 23 |  |  | DI |  | 4 | BMC1302INC03 | CB05 |  | BMC1302 INC03 Bus INC03 24VDC Cubicle Bus Supply OK | Healthy | Q256 | BMC1302INC03 |  | 2.2\0.1:23 | BR4-2110-E-00227 | [9 empty] | F21 | 47 | 48
BSR130 | DX02 | DIO1 | 130 | 2 | 2 | 0 | 1 | 24 |  |  | DI |  | 4 | BMC1302INC03 | CB06 |  | BMC1302 INC03 Arc Flash Expansion Module 24VDC Supply | Healthy | Q258 | BMC1302INC03 |  | 2.2\0.1:24 | BR4-2110-E-00227 | [9 empty] | F21 | 49 | 50
BSR130 | DX02 | DIO1 | 130 | 2 | 2 | 0 | 1 | 25 |  |  | DI |  | 4 | BMC1302INC03 | CB07 |  | BMC1302 INC03 110/24VDC Power Supply | Healthy | Q215 | BMC1302INC03 |  | 2.2\0.1:25 | BR4-2110-E-00227 | [9 empty] | F21 | 51 | 52
BSR130 | DX02 | DIO1 | 130 | 2 | 2 | 0 | 1 | 26 |  |  | DI | [10 empty] | 2.2\0.1:26 | [10 empty] | F21 | 53 | 54
BSR130 | DX02 | DIO1 | 130 | 2 | 2 | 0 | 1 | 27 |  |  | DI | [10 empty] | 2.2\0.1:27 | [10 empty] | F21 | 55 | 56
BSR130 | DX02 | DIO1 | 130 | 2 | 2 | 0 | 1 | 28 |  |  | DI | [10 empty] | 2.2\0.1:28 | [10 empty] | F21 | 57 | 58
BSR130 | DX02 | DIO1 | 130 | 2 | 2 | 0 | 1 | 29 |  |  | DI | [10 empty] | 2.2\0.1:29 | [10 empty] | F21 | 59 | 60
BSR130 | DX02 | DIO1 | 130 | 2 | 2 | 0 | 1 | 30 |  |  | DI | [10 empty] | 2.2\0.1:30 | [10 empty] | F21 | 61 | 62
BSR130 | DX02 | DIO1 | 130 | 2 | 2 | 0 | 1 | 31 |  |  | DI | [10 empty] | 2.2\0.1:31 | [10 empty] | F21 | 63 | 64
BSR130 | DX02 | DIO1 | 130 | 2 | 2 | 0 | 2 | 0 | BMXFCW303 | BMXDDI3202K | DI |  | 4 | BSR130BC01 | VDC01 |  | 24VDC Control Supply | Healthy | Q155 | BSR130BC01 |  | 2.2\0.2:0 | BR4-2110-E-00206 | A | [8 empty] | F22 | 1 | 2
BSR130 | DX02 | DIO1 | 130 | 2 | 2 | 0 | 2 | 1 |  |  | DI |  | 4 | BSR130BC01 | CB01 |  | Main Circuit Breaker | Closed | Q103 | BSR130BC01 |  | 2.2\0.2:1 | BR4-2110-E-00206 | A | [8 empty] | F22 | 3 | 4
BSR130 | DX02 | DIO1 | 130 | 2 | 2 | 0 | 2 | 2 |  |  | DI |  | 4 | BSR130BC01 | TRP01 |  | Main Circuit Breaker | Tripped | Q103 | BSR130BC01 |  | 2.2\0.2:2 | BR4-2110-E-00206 | A | [8 empty] | F22 | 5 | 6
BSR130 | DX02 | DIO1 | 130 | 2 | 2 | 0 | 2 | 3 |  |  | DI |  | 4 | BSR130BC02 | VDC01 |  | 24VDC Control Supply | Healthy | Q155 | BSR130BC02 |  | 2.2\0.2:3 | BR4-2110-E-00207 | A | [8 empty] | F22 | 7 | 8
BSR130 | DX02 | DIO1 | 130 | 2 | 2 | 0 | 2 | 4 |  |  | DI |  | 4 | BSR130BC02 | CB01 |  | Main Circuit Breaker | Closed | Q103 | BSR130BC02 |  | 2.2\0.2:4 | BR4-2110-E-00207 | A | [8 empty] | F22 | 9 | 10
BSR130 | DX02 | DIO1 | 130 | 2 | 2 | 0 | 2 | 5 |  |  | DI |  | 4 | BSR130BC02 | TRP01 |  | Main Circuit Breaker | Tripped | Q103 | BSR130BC02 |  | 2.2\0.2:5 | BR4-2110-E-00207 | A | [8 empty] | F22 | 11 | 12
BSR130 | DX02 | DIO1 | 130 | 2 | 2 | 0 | 2 | 6 |  |  | DI |  | 4 | BSR130AC01 | VDC01 |  | 24VDC Control Supply | Healthy | Q155 | BSR130AC01 |  | 2.2\0.2:6 | BR4-2110-E-00208 | A | [8 empty] | F22 | 13 | 14
BSR130 | DX02 | DIO1 | 130 | 2 | 2 | 0 | 2 | 7 |  |  | DI |  | 4 | BSR130AC01 | CB01 |  | Main Circuit Breaker | Closed | Q103 | BSR130AC01 |  | 2.2\0.2:7 | BR4-2110-E-00208 | A | [8 empty] | F22 | 15 | 16
BSR130 | DX02 | DIO1 | 130 | 2 | 2 | 0 | 2 | 8 |  |  | DI |  | 4 | BSR130AC01 | TRP01 |  | Main Circuit Breaker | Tripped | Q103 | BSR130AC01 |  | 2.2\0.2:8 | BR4-2110-E-00208 | A | [8 empty] | F22 | 17 | 18
BSR130 | DX02 | DIO1 | 130 | 2 | 2 | 0 | 2 | 9 |  |  | DI |  | 4 | BSR130AC02 | VDC01 |  | 24VDC Control Supply | Healthy | Q155 | BSR130AC02 |  | 2.2\0.2:9 | BR4-2110-E-00209 | A | [8 empty] | F22 | 19 | 20
BSR130 | DX02 | DIO1 | 130 | 2 | 2 | 0 | 2 | 10 |  |  | DI |  | 4 | BSR130AC02 | CB01 |  | Main Circuit Breaker | Closed | Q103 | BSR130AC02 |  | 2.2\0.2:10 | BR4-2110-E-00209 | A | [8 empty] | F22 | 21 | 22
BSR130 | DX02 | DIO1 | 130 | 2 | 2 | 0 | 2 | 11 |  |  | DI |  | 4 | BSR130AC02 | TRP01 |  | Main Circuit Breaker | Tripped | Q103 | BSR130AC02 |  | 2.2\0.2:11 | BR4-2110-E-00209 | A | [8 empty] | F22 | 23 | 24
BSR130 | DX02 | DIO1 | 130 | 2 | 2 | 0 | 2 | 12 |  |  | DI |  | 4 | BSR130UP01 | VDC01 |  | 24VDC Control Supply | Healthy | Q155 | BSR130UP01 |  | 2.2\0.2:12 | BR4-2110-E-00210 | A | [8 empty] | F22 | 25 | 26
BSR130 | DX02 | DIO1 | 130 | 2 | 2 | 0 | 2 | 13 |  |  | DI |  | 4 | BSR130UP01 | CB01 |  | Main Circuit Breaker | Closed | Q103 | BSR130UP01 |  | 2.2\0.2:13 | BR4-2110-E-00210 | A | [8 empty] | F22 | 27 | 28
BSR130 | DX02 | DIO1 | 130 | 2 | 2 | 0 | 2 | 14 |  |  | DI |  | 4 | BSR130UP01 | TRP01 |  | Main Circuit Breaker | Tripped | Q103 | BSR130UP01 |  | 2.2\0.2:14 | BR4-2110-E-00210 | A | [8 empty] | F22 | 29 | 30
BSR130 | DX02 | DIO1 | 130 | 2 | 2 | 0 | 2 | 15 |  |  | DI |  | 4 | BSR130DB01 | VDC01 |  | 24VDC Control Supply | Healthy | Q155 | BSR130DB01 |  | 2.2\0.2:15 | BR4-2110-E-00211 | A | [8 empty] | F22 | 31 | 32
BSR130 | DX02 | DIO1 | 130 | 2 | 2 | 0 | 2 | 16 |  |  | DI |  | 4 | BSR130DB01 | CB01 |  | Main Circuit Breaker | Closed | Q103 | BSR130DB01 |  | 2.2\0.2:16 | BR4-2110-E-00211 | A | [8 empty] | F22 | 33 | 34
BSR130 | DX02 | DIO1 | 130 | 2 | 2 | 0 | 2 | 17 |  |  | DI |  | 4 | BSR130DB01 | TRP01 |  | Main Circuit Breaker | Tripped | Q103 | BSR130DB01 |  | 2.2\0.2:17 | BR4-2110-E-00211 | A | [8 empty] | F22 | 35 | 36
BSR130 | DX02 | DIO1 | 130 | 2 | 2 | 0 | 2 | 18 |  |  | DI |  | 4 | BSR130DB02 | VDC01 |  | 24VDC Control Supply | Healthy | Q155 | BSR130DB02 |  | 2.2\0.2:18 | BR4-2110-E-00039 | A | [8 empty] | F22 | 37 | 38
BSR130 | DX02 | DIO1 | 130 | 2 | 2 | 0 | 2 | 19 |  |  | DI |  | 4 | BSR130DB02 | CB01 |  | Main Circuit Breaker | Closed | Q103 | BSR130DB02 |  | 2.2\0.2:19 | BR4-2110-E-00039 | A | [8 empty] | F22 | 39 | 40
BSR130 | DX02 | DIO1 | 130 | 2 | 2 | 0 | 2 | 20 |  |  | DI |  | 4 | BSR130DB02 | TRP01 |  | Main Circuit Breaker | Tripped | Q103 | BSR130DB02 |  | 2.2\0.2:20 | BR4-2110-E-00039 | A | [8 empty] | F22 | 41 | 42
BSR130 | DX02 | DIO1 | 130 | 2 | 2 | 0 | 2 | 21 |  |  | DI |  | 4 | BSR130DB03 | VDC01 |  | 24VDC Control Supply | Healthy | Q155 | BSR130DB03 |  | 2.2\0.2:21 | BR4-2110-E-00040 | A | [8 empty] | F22 | 43 | 44
BSR130 | DX02 | DIO1 | 130 | 2 | 2 | 0 | 2 | 22 |  |  | DI |  | 4 | BSR130DB03 | CB01 |  | Main Circuit Breaker | Closed | Q103 | BSR130DB03 |  | 2.2\0.2:22 | BR4-2110-E-00040 | A | [8 empty] | F22 | 45 | 46
BSR130 | DX02 | DIO1 | 130 | 2 | 2 | 0 | 2 | 23 |  |  | DI |  | 4 | BSR130DB03 | TRP01 |  | Main Circuit Breaker | Tripped | Q103 | BSR130DB03 |  | 2.2\0.2:23 | BR4-2110-E-00040 | A | [8 empty] | F22 | 47 | 48
BSR130 | DX02 | DIO1 | 130 | 2 | 2 | 0 | 2 | 24 |  |  | DI |  | 4 | BSR130DB04 | VDC01 |  | 24VDC Control Supply | Healthy | Q155 | BSR130DB04 |  | 2.2\0.2:24 | BR4-2110-E-00041 | A | [8 empty] | F22 | 49 | 50
BSR130 | DX02 | DIO1 | 130 | 2 | 2 | 0 | 2 | 25 |  |  | DI |  | 4 | BSR130DB04 | CB01 |  | Main Circuit Breaker | Closed | Q103 | BSR130DB04 |  | 2.2\0.2:25 | BR4-2110-E-00041 | A | [8 empty] | F22 | 51 | 52
BSR130 | DX02 | DIO1 | 130 | 2 | 2 | 0 | 2 | 26 |  |  | DI |  | 4 | BSR130DB04 | TRP01 |  | Main Circuit Breaker | Tripped | Q103 | BSR130DB04 |  | 2.2\0.2:26 | BR4-2110-E-00041 | A | [8 empty] | F22 | 53 | 54
BSR130 | DX02 | DIO1 | 130 | 2 | 2 | 0 | 2 | 27 |  |  | DI |  | 4 | BSR130DB05 | VDC01 |  | 24VDC Control Supply | Healthy | Q155 | BSR130DB05 |  | 2.2\0.2:27 | BR4-2110-E-00212 | A | [8 empty] | F22 | 55 | 56
BSR130 | DX02 | DIO1 | 130 | 2 | 2 | 0 | 2 | 28 |  |  | DI |  | 4 | BSR130DB05 | CB01 |  | Main Circuit Breaker | Closed | Q103 | BSR130DB05 |  | 2.2\0.2:28 | BR4-2110-E-00212 | A | [8 empty] | F22 | 57 | 58
BSR130 | DX02 | DIO1 | 130 | 2 | 2 | 0 | 2 | 29 |  |  | DI |  | 4 | BSR130DB05 | TRP01 |  | Main Circuit Breaker | Tripped | Q103 | BSR130DB05 |  | 2.2\0.2:29 | BR4-2110-E-00212 | A | [8 empty] | F22 | 59 | 60
BSR130 | DX02 | DIO1 | 130 | 2 | 2 | 0 | 2 | 30 |  |  | DI | [10 empty] | 2.2\0.2:30 | [10 empty] | F22 | 61 | 62
BSR130 | DX02 | DIO1 | 130 | 2 | 2 | 0 | 2 | 31 |  |  | DI | [10 empty] | 2.2\0.2:31 | [10 empty] | F22 | 63 | 64
BSR130 | DX02 | DIO1 | 130 | 2 | 2 | 0 | 3 | 0 | BMXFCW303 | BMXDDI3202K | DI |  | 4 | BRB131CC01DB01 | VDC01 |  | 24VDC Control Supply | Healthy | Q155 | BRB131CC01DB01 |  | 2.2\0.3:0 | BR4-2110-E-00066 | A | [8 empty] | F23 | 1 | 2
BSR130 | DX02 | DIO1 | 130 | 2 | 2 | 0 | 3 | 1 |  |  | DI |  | 4 | BRB131CC01DB01 | CB01 |  | Main Circuit Breaker | Closed | Q103 | BRB131CC01DB01 |  | 2.2\0.3:1 | BR4-2110-E-00066 | A | [8 empty] | F23 | 3 | 4
BSR130 | DX02 | DIO1 | 130 | 2 | 2 | 0 | 3 | 2 |  |  | DI |  | 4 | BRB131CC01DB01 | TRP01 |  | Main Circuit Breaker | Tripped | Q103 | BRB131CC01DB01 |  | 2.2\0.3:2 | BR4-2110-E-00066 | A | [8 empty] | F23 | 5 | 6
BSR130 | DX02 | DIO1 | 130 | 2 | 2 | 0 | 3 | 3 |  |  | DI |  | 4 | BCV130WN01PN01 | VDC01 |  | 24VDC Control Supply | Healthy | Q155 | BCV130WN01PN01 |  | 2.2\0.3:3 | BR4-2110-E-00247 | A | [8 empty] | F23 | 7 | 8
BSR130 | DX02 | DIO1 | 130 | 2 | 2 | 0 | 3 | 4 |  |  | DI |  | 4 | BCV130WN01PN01 | CB01 |  | Main Circuit Breaker | Closed | Q103 | BCV130WN01PN01 |  | 2.2\0.3:4 | BR4-2110-E-00247 | A | [8 empty] | F23 | 9 | 10
BSR130 | DX02 | DIO1 | 130 | 2 | 2 | 0 | 3 | 5 |  |  | DI |  | 4 | BCV130WN01PN01 | TRP01 |  | Main Circuit Breaker | Tripped | Q103 | BCV130WN01PN01 |  | 2.2\0.3:5 | BR4-2110-E-00247 | A | [8 empty] | F23 | 11 | 12
BSR130 | DX02 | DIO1 | 130 | 2 | 2 | 0 | 3 | 6 |  |  | DI |  | 4 | BCV130MA01PN01 | VDC01 |  | 24VDC Control Supply | Healthy | Q155 | BCV130MA01PN01 |  | 2.2\0.3:6 | BR4-2110-E-00232 | A | [8 empty] | F23 | 13 | 14
BSR130 | DX02 | DIO1 | 130 | 2 | 2 | 0 | 3 | 7 |  |  | DI |  | 4 | BCV130MA01PN01 | CB01 |  | Main Circuit Breaker | Closed | Q103 | BCV130MA01PN01 |  | 2.2\0.3:7 | BR4-2110-E-00232 | A | [8 empty] | F23 | 15 | 16
BSR130 | DX02 | DIO1 | 130 | 2 | 2 | 0 | 3 | 8 |  |  | DI |  | 4 | BCV130MA01PN01 | TRP01 |  | Main Circuit Breaker | Tripped | Q103 | BCV130MA01PN01 |  | 2.2\0.3:8 | BR4-2110-E-00232 | A | [8 empty] | F23 | 17 | 18
BSR130 | DX02 | DIO1 | 130 | 2 | 2 | 0 | 3 | 9 |  |  | DI | [10 empty] | 2.2\0.3:9 | [10 empty] | F23 | 19 | 20
BSR130 | DX02 | DIO1 | 130 | 2 | 2 | 0 | 3 | 10 |  |  | DI | [10 empty] | 2.2\0.3:10 | [10 empty] | F23 | 21 | 22
BSR130 | DX02 | DIO1 | 130 | 2 | 2 | 0 | 3 | 11 |  |  | DI | [10 empty] | 2.2\0.3:11 | [10 empty] | F23 | 23 | 24
BSR130 | DX02 | DIO1 | 130 | 2 | 2 | 0 | 3 | 12 |  |  | DI |  | 4 | BSB1301 | VDC01 |  | 24VDC Control Supply | Healthy | Q267 | BSB1301 |  | 2.2\0.3:12 | BR4-2110-E-00239 |  | BSB1301-C1 10 PAIR | [7 empty] | F23 | 25 | 26
BSR130 | DX02 | DIO1 | 130 | 2 | 2 | 0 | 3 | 13 |  |  | DI |  | 4 | BSB1301 | TRP01 |  | Downstream Circuit Breaker | Trip | K260 | BSB1301 |  | 2.2\0.3:13 | BR4-2110-E-00239 | [9 empty] | F23 | 27 | 28
BSR130 | DX02 | DIO1 | 130 | 2 | 2 | 0 | 3 | 14 |  |  | DI |  | 4 | BSB1301 | CB03 |  | Spring Charge Supply OK | Healthy | Q212 | BSB1301 |  | 2.2\0.3:14 | BR4-2110-E-00239 | [9 empty] | F23 | 29 | 30
BSR130 | DX02 | DIO1 | 130 | 2 | 2 | 0 | 3 | 15 |  |  | DI |  | 4 | BSB1301 | CB04 |  | Trip Supply OK | Healthy | Q220 | BSB1301 |  | 2.2\0.3:15 | BR4-2110-E-00239 | [9 empty] | F23 | 31 | 32
BSR130 | DX02 | DIO1 | 130 | 2 | 2 | 0 | 3 | 16 |  |  | DI |  | 4 | BSB1301 | CB05 |  | 24VDC Cubicle Bus Supply OK | Healthy | Q256 | BSB1301 |  | 2.2\0.3:16 | BR4-2110-E-00239 | [9 empty] | F23 | 33 | 34
BSR130 | DX02 | DIO1 | 130 | 2 | 2 | 0 | 3 | 17 |  |  | DI |  | 4 | BSB1301 | CB07 |  | 110/24VDC Power Supply OK | Healthy | Q253 | BSB1301 |  | 2.2\0.3:17 | BR4-2110-E-00239 | [9 empty] | F23 | 35 | 36
BSR130 | DX02 | DIO1 | 130 | 2 | 2 | 0 | 3 | 18 |  |  | DI |  | 4 | BCV130VS01 | VDC01 |  | 24VDC Control Supply | Healthy | Q267 | BCV130VS01 |  | 2.2\0.3:18 | BR4-2110-E-00229 |  | BCV130VS01-C1 10 PAIR | [7 empty] | F23 | 37 | 38
BSR130 | DX02 | DIO1 | 130 | 2 | 2 | 0 | 3 | 19 |  |  | DI |  | 4 | BCV130VS01 | TRP01 |  | Downstream Circuit Breaker | Trip | K260 | BCV130VS01 |  | 2.2\0.3:19 | BR4-2110-E-00229 | [9 empty] | F23 | 39 | 40
BSR130 | DX02 | DIO1 | 130 | 2 | 2 | 0 | 3 | 20 |  |  | DI |  | 4 | BCV130VS01 | CB03 |  | Spring Charge Supply OK | Healthy | Q212 | BCV130VS01 |  | 2.2\0.3:20 | BR4-2110-E-00229 | [9 empty] | F23 | 41 | 42
BSR130 | DX02 | DIO1 | 130 | 2 | 2 | 0 | 3 | 21 |  |  | DI |  | 4 | BCV130VS01 | CB04 |  | Trip Supply OK | Healthy | Q220 | BCV130VS01 |  | 2.2\0.3:21 | BR4-2110-E-00229 | [9 empty] | F23 | 43 | 44
BSR130 | DX02 | DIO1 | 130 | 2 | 2 | 0 | 3 | 22 |  |  | DI |  | 4 | BCV130VS01 | CB05 |  | 24VDC Cubicle Bus Supply OK | Healthy | Q256 | BCV130VS01 |  | 2.2\0.3:22 | BR4-2110-E-00229 | [9 empty] | F23 | 45 | 46
BSR130 | DX02 | DIO1 | 130 | 2 | 2 | 0 | 3 | 23 |  |  | DI |  | 4 | BCV130VS01 | CB07 |  | 110/24VDC Power Supply OK | Healthy | Q253 | BCV130VS01 |  | 2.2\0.3:23 | BR4-2110-E-00229 | [9 empty] | F23 | 47 | 48
BSR130 | DX02 | DIO1 | 130 | 2 | 2 | 0 | 3 | 24 |  |  | DI | [10 empty] | 2.2\0.3:24 | [10 empty] | F23 | 49 | 50
BSR130 | DX02 | DIO1 | 130 | 2 | 2 | 0 | 3 | 25 |  |  | DI | [10 empty] | 2.2\0.3:25 | [10 empty] | F23 | 51 | 52
BSR130 | DX02 | DIO1 | 130 | 2 | 2 | 0 | 3 | 26 |  |  | DI | [10 empty] | 2.2\0.3:26 | [10 empty] | F23 | 53 | 54
BSR130 | DX02 | DIO1 | 130 | 2 | 2 | 0 | 3 | 27 |  |  | DI | [10 empty] | 2.2\0.3:27 | [10 empty] | F23 | 55 | 56
BSR130 | DX02 | DIO1 | 130 | 2 | 2 | 0 | 3 | 28 |  |  | DI | [10 empty] | 2.2\0.3:28 | [10 empty] | F23 | 57 | 58
BSR130 | DX02 | DIO1 | 130 | 2 | 2 | 0 | 3 | 29 |  |  | DI | [10 empty] | 2.2\0.3:29 | [10 empty] | F23 | 59 | 60
BSR130 | DX02 | DIO1 | 130 | 2 | 2 | 0 | 3 | 30 |  |  | DI | [10 empty] | 2.2\0.3:30 | [10 empty] | F23 | 61 | 62
BSR130 | DX02 | DIO1 | 130 | 2 | 2 | 0 | 3 | 31 |  |  | DI | [10 empty] | 2.2\0.3:31 | [10 empty] | F23 | 63 | 64
BSR130 | DX02 | DIO1 | 130 | 2 | 2 | 0 | 4 | 0 | BMXFCW303 | BMXDDI3202K | DI |  | 4 | BSR130DX02 | VDC01 |  | DX02 24VDC Control Supply Healthy | Healthy | Q110 | BSR130DX02 |  | 2.2\0.4:0 | BR4-2110-E-00250 | 0 | [8 empty] | F24 | 1 | 2
BSR130 | DX02 | DIO1 | 130 | 2 | 2 | 0 | 4 | 1 |  |  | DI |  | 4 | BSR130DX02 | VDC02 |  | Spare | Healthy | Q254 | BSR130DX02 |  | 2.2\0.4:1 | BR4-2110-E-00251 | 0 | [8 empty] | F24 | 3 | 4
BSR130 | DX02 | DIO1 | 130 | 2 | 2 | 0 | 4 | 2 |  |  | DI |  | 4 | BSR130DX02 | VDC03 |  | Safety PLC Circuit 1 | Healthy | Q257 | BSR130DX02 |  | 2.2\0.4:2 | BR4-2110-E-00251 | 0 | [8 empty] | F24 | 5 | 6
BSR130 | DX02 | DIO1 | 130 | 2 | 2 | 0 | 4 | 3 |  |  | DI |  | 4 | BSR130DX02 | VDC04 |  | Safety PLC Circuit 2 | Healthy | Q260 | BSR130DX02 |  | 2.2\0.4:3 | BR4-2110-E-00251 | 0 | [8 empty] | F24 | 7 | 8
BSR130 | DX02 | DIO1 | 130 | 2 | 2 | 0 | 4 | 4 |  |  | DI |  | 4 | BSR130DX02 | VDC05 |  | Supply To BCV130VS01 | Healthy | Q263 | BSR130DX02 |  | 2.2\0.4:4 | BR4-2110-E-00251 | 0 | [8 empty] | F24 | 9 | 10
BSR130 | DX02 | DIO1 | 130 | 2 | 2 | 0 | 4 | 5 |  |  | DI |  | 4 | BSR130DX02 | VDC06 |  | BSR130DX02 Safety Relays | Healthy | Q266 | BSR130DX02 |  | 2.2\0.4:5 | BR4-2110-E-00251 | 0 | [8 empty] | F24 | 11 | 12
BSR130 | DX02 | DIO1 | 130 | 2 | 2 | 0 | 4 | 6 |  |  | DI |  | 4 | BSR130DX02 | VDC07 |  | Spare | Healthy | Q269 | BSR130DX02 |  | 2.2\0.4:6 | BR4-2110-E-00251 | 0 | [8 empty] | F24 | 13 | 14
BSR130 | DX02 | DIO1 | 130 | 2 | 2 | 0 | 4 | 7 |  |  | DI |  | 4 | BSR130DX02 | VDC08 |  | Spare | Healthy | Q272 | BSR130DX02 |  | 2.2\0.4:7 | BR4-2110-E-00251 | 0 | [8 empty] | F24 | 15 | 16
BSR130 | DX02 | DIO1 | 130 | 2 | 2 | 0 | 4 | 8 |  |  | DI |  | 4 | BSR130DX02 | VDC09 |  | Spare | Healthy | Q275 | BSR130DX02 |  | 2.2\0.4:8 | BR4-2110-E-00251 | 0 | [8 empty] | F24 | 17 | 18
BSR130 | DX02 | DIO1 | 130 | 2 | 2 | 0 | 4 | 9 |  |  | DI |  | 4 | BSR130DX02 | VDC10 |  | Spare | Healthy | Q278 | BSR130DX02 |  | 2.2\0.4:9 | BR4-2110-E-00251 | 0 | [8 empty] | F24 | 19 | 20
BSR130 | DX02 | DIO1 | 130 | 2 | 2 | 0 | 4 | 10 |  |  | DI |  | 4 | BSR130DX02 | VDC11 |  | Spare | Healthy | Q281 | BSR130DX02 |  | 2.2\0.4:10 | BR4-2110-E-00251 | 0 | [8 empty] | F24 | 21 | 22
BSR130 | DX02 | DIO1 | 130 | 2 | 2 | 0 | 4 | 11 |  |  | DI |  | 4 | BSR130DX02 | VDC12 |  | Spare | Healthy | Q284 | BSR130DX02 |  | 2.2\0.4:11 | BR4-2110-E-00251 | 0 | [8 empty] | F24 | 23 | 24
BSR130 | DX02 | DIO1 | 130 | 2 | 2 | 0 | 4 | 12 |  |  | DI | [10 empty] | 2.2\0.4:12 | [10 empty] | F24 | 25 | 26
BSR130 | DX02 | DIO1 | 130 | 2 | 2 | 0 | 4 | 13 |  |  | DI | [10 empty] | 2.2\0.4:13 | [10 empty] | F24 | 27 | 28
BSR130 | DX02 | DIO1 | 130 | 2 | 2 | 0 | 4 | 14 |  |  | DI | [10 empty] | 2.2\0.4:14 | [10 empty] | F24 | 29 | 30
BSR130 | DX02 | DIO1 | 130 | 2 | 2 | 0 | 4 | 15 |  |  | DI | [10 empty] | 2.2\0.4:15 | [10 empty] | F24 | 31 | 32
BSR130 | DX02 | DIO1 | 130 | 2 | 2 | 0 | 4 | 16 |  |  | DI |  | 4 | BBD130PP01 | VDC01 |  | 24VDC Control Supply | Healthy | Q155 | BBD130PP01 |  | 2.2\0.4:16 | BR4-2110-E-00042 | A | [8 empty] | F24 | 33 | 34
BSR130 | DX02 | DIO1 | 130 | 2 | 2 | 0 | 4 | 17 |  |  | DI |  | 4 | BTN130PP01 | VDC01 |  | 24VDC Control Supply | Healthy | Q155 | BTN130PP01 |  | 2.2\0.4:17 | BR4-2110-E-00213 | A | [8 empty] | F24 | 35 | 36
BSR130 | DX02 | DIO1 | 130 | 2 | 2 | 0 | 4 | 18 |  |  | DI |  | 4 | BCV130PP01 | VDC01 |  | 24VDC Control Supply | Healthy | Q155 | BCV130PP01 |  | 2.2\0.4:18 | BR4-2110-E-00215 | A | [8 empty] | F24 | 37 | 38
BSR130 | DX02 | DIO1 | 130 | 2 | 2 | 0 | 4 | 19 |  |  | DI |  | 5 | BCV131PP04 | VDC01 |  | 24VDC Control Supply | Healthy | Q155 | BCV131PP04 |  | 2.2\0.4:19 | BR4-2110-E-00218 | A | [8 empty] | F24 | 39 | 40
BSR130 | DX02 | DIO1 | 130 | 2 | 2 | 0 | 4 | 20 |  |  | DI |  | 4 | BCV131PP05 | VDC01 |  | 24VDC Control Supply | Healthy | Q155 | BCV131PP05 |  | 2.2\0.4:20 | BR4-2110-E-00217 | A | [8 empty] | F24 | 41 | 42
BSR130 | DX02 | DIO1 | 130 | 2 | 2 | 0 | 4 | 21 |  |  | DI |  | 4 | BCV130PP03 | VDC01 |  | 24VDC Control Supply | Healthy | Q155 | BCV130PP03 |  | 2.2\0.4:21 | [10 empty] | F24 | 43 | 44
BSR130 | DX02 | DIO1 | 130 | 2 | 2 | 0 | 4 | 22 |  |  | DI |  | 4 | BCV130FN01 | VDC01 |  | 24VDC Control Supply | Healthy | Q155 | BCV130FN01 |  | 2.2\0.4:22 | BR4-2110-E-00231 | A | [8 empty] | F24 | 45 | 46
BSR130 | DX02 | DIO1 | 130 | 2 | 2 | 0 | 4 | 23 |  |  | DI |  | 4 | BCV130FN02 | VDC01 |  | 24VDC Control Supply | Healthy | Q155 | BCV130FN02 |  | 2.2\0.4:23 | BR4-2110-E-00216 | A | [8 empty] | F24 | 47 | 48
BSR130 | DX02 | DIO1 | 130 | 2 | 2 | 0 | 4 | 24 |  |  | DI |  | 4 | BCV130PP02 | VDC01 |  | 24VDC Control Supply | Healthy | Q155 | BCV130PP02 |  | 2.2\0.4:24 | BR4-2110-E-00233 | A | [8 empty] | F24 | 49 | 50
BSR130 | DX02 | DIO1 | 130 | 2 | 2 | 0 | 4 | 25 |  |  | DI |  | 4 | BCV130FN03 | VDC01 |  | 24VDC Control Supply | Healthy | Q155 | BCV130FN03 |  | 2.2\0.4:25 | BR4-2110-E-00234 | A | [8 empty] | F24 | 51 | 52
BSR130 | DX02 | DIO1 | 130 | 2 | 2 | 0 | 4 | 26 |  |  | DI |  | 4 | BCV130FN04 | VDC01 |  | 24VDC Control Supply | Healthy | Q155 | BCV130FN04 |  | 2.2\0.4:26 | BR4-2110-E-00235 | A | [8 empty] | F24 | 53 | 54
BSR130 | DX02 | DIO1 | 130 | 2 | 2 | 0 | 4 | 27 |  |  | DI |  | 4 | BCV130MT01EM01 | VDC01 |  | 24VDC Control Supply | Healthy | Q155 | BCV130MT01EM01 |  | 2.2\0.4:27 | BR4-2110-E-00236 | A | [8 empty] | F24 | 55 | 56
BSR130 | DX02 | DIO1 | 130 | 2 | 2 | 0 | 4 | 28 |  |  | DI |  | 4 | BCV130MT01EM02 | VDC01 |  | 24VDC Control Supply | Healthy | Q155 | BCV130MT01EM02 |  | 2.2\0.4:28 | BR4-2110-E-00237 | A | [8 empty] | F24 | 57 | 58
BSR130 | DX02 | DIO1 | 130 | 2 | 2 | 0 | 4 | 29 |  |  | DI |  | 4 | BCV130PP04 | VDC01 |  | 24VDC Control Supply | Healthy | Q155 | BCV130PP04 |  | 2.2\0.4:29 | BR4-2110-E-00221 | A | [8 empty] | F24 | 59 | 60
BSR130 | DX02 | DIO1 | 130 | 2 | 2 | 0 | 4 | 30 |  |  | DI | [10 empty] | 2.2\0.4:30 | [10 empty] | F24 | 61 | 62
BSR130 | DX02 | DIO1 | 130 | 2 | 2 | 0 | 4 | 31 |  |  | DI | [10 empty] | 2.2\0.4:31 | [10 empty] | F24 | 63 | 64
BSR130 | DX02 | DIO1 | 130 | 2 | 2 | 0 | 5 | 0 | BMXFCW303 | BMXDDI3202K | DI |  | 4 | BCV131 | SLC01SY01 |  | Safety SLC01 Circuit | Healthy | K132 | BCV131 |  | 2.2\0.5:0 | [10 empty] | F25 | 1 | 2
BSR130 | DX02 | DIO1 | 130 | 2 | 2 | 0 | 5 | 1 |  |  | DI |  | 4 | BCV131 | SY01 |  | Safety Interlock Relay | Healthy | K155-1 | BCV131 |  | 2.2\0.5:1 | [10 empty] | F25 | 3 | 4
BSR130 | DX02 | DIO1 | 130 | 2 | 2 | 0 | 5 | 2 |  |  | DI |  | 4 | BCV131 | SLC02SY01 |  | Safety SLC02 Circuit | Healthy | K232 | BCV131 |  | 2.2\0.5:2 | [10 empty] | F25 | 5 | 6
BSR130 | DX02 | DIO1 | 130 | 2 | 2 | 0 | 5 | 3 |  |  | DI | [10 empty] | 2.2\0.5:3 | [10 empty] | F25 | 7 | 8
BSR130 | DX02 | DIO1 | 130 | 2 | 2 | 0 | 5 | 4 |  |  | DI | [10 empty] | 2.2\0.5:4 | [10 empty] | F25 | 9 | 10
BSR130 | DX02 | DIO1 | 130 | 2 | 2 | 0 | 5 | 5 |  |  | DI |  | 4 | BCV130 | SY01 |  | Safety Interlock Relay | Healthy | K305-1 | BCV130 |  | 2.2\0.5:5 | [10 empty] | F25 | 11 | 12
BSR130 | DX02 | DIO1 | 130 | 2 | 2 | 0 | 5 | 6 |  |  | DI |  | 4 | BCV130DX07 | SY01 |  | Safety Interlock Relay | Healthy | K403 | BCV130DX07 |  | 2.2\0.5:6 | [10 empty] | F25 | 13 | 14
BSR130 | DX02 | DIO1 | 130 | 2 | 2 | 0 | 5 | 7 |  |  | DI |  | 4 | BCV130DX08 | SY01 |  | Safety Interlock Relay | Healthy | K425 | BCV130DX08 |  | 2.2\0.5:7 | [10 empty] | F25 | 15 | 16
BSR130 | DX02 | DIO1 | 130 | 2 | 2 | 0 | 5 | 8 |  |  | DI |  | 4 | BCV130DX09 | SY01 |  | Safety Interlock Relay | Healthy | K453 | BCV130DX09 |  | 2.2\0.5:8 | [10 empty] | F25 | 17 | 18
BSR130 | DX02 | DIO1 | 130 | 2 | 2 | 0 | 5 | 9 |  |  | DI |  | 4 | BCV130MA01 | SY01 |  | Safety Interlock Relay | Healthy | K355-1 | BCV130MA01 |  | 2.2\0.5:9 | [10 empty] | F25 | 19 | 20
BSR130 | DX02 | DIO1 | 130 | 2 | 2 | 0 | 5 | 10 |  |  | DI |  | 4 | BCV130MA01 | SY02 |  | Safety Interlock Relay | Healthy | K375-1 | BCV130MA01 |  | 2.2\0.5:10 | [10 empty] | F25 | 21 | 22
BSR130 | DX02 | DIO1 | 130 | 2 | 2 | 0 | 5 | 11 |  |  | DI |  | 5 | BCV130GB01 | SY01 |  | Safety Interlock Relay | Healthy | K475-1 | BCV130GB01 |  | 2.2\0.5:11 | BR4-2110-E-00122 | 0 | [8 empty] | F25 | 23 | 24
BSR130 | DX02 | DIO1 | 130 | 2 | 2 | 0 | 5 | 12 |  |  | DI | [10 empty] | 2.2\0.5:12 | [10 empty] | F25 | 25 | 26
BSR130 | DX02 | DIO1 | 130 | 2 | 2 | 0 | 5 | 13 |  |  | DI | [10 empty] | 2.2\0.5:13 | [10 empty] | F25 | 27 | 28
BSR130 | DX02 | DIO1 | 130 | 2 | 2 | 0 | 5 | 14 |  |  | DI | [10 empty] | 2.2\0.5:14 | [10 empty] | F25 | 29 | 30
BSR130 | DX02 | DIO1 | 130 | 2 | 2 | 0 | 5 | 15 |  |  | DI | [10 empty] | 2.2\0.5:15 | [10 empty] | F25 | 31 | 32
BSR130 | DX02 | DIO1 | 130 | 2 | 2 | 0 | 5 | 16 |  |  | DI | [10 empty] | 2.2\0.5:16 | [10 empty] | F25 | 33 | 34
BSR130 | DX02 | DIO1 | 130 | 2 | 2 | 0 | 5 | 17 |  |  | DI | [10 empty] | 2.2\0.5:17 | [10 empty] | F25 | 35 | 36
BSR130 | DX02 | DIO1 | 130 | 2 | 2 | 0 | 5 | 18 |  |  | DI | [10 empty] | 2.2\0.5:18 | [10 empty] | F25 | 37 | 38
BSR130 | DX02 | DIO1 | 130 | 2 | 2 | 0 | 5 | 19 |  |  | DI | [10 empty] | 2.2\0.5:19 | [10 empty] | F25 | 39 | 40
BSR130 | DX02 | DIO1 | 130 | 2 | 2 | 0 | 5 | 20 |  |  | DI | [10 empty] | 2.2\0.5:20 | [10 empty] | F25 | 41 | 42
BSR130 | DX02 | DIO1 | 130 | 2 | 2 | 0 | 5 | 21 |  |  | DI | [10 empty] | 2.2\0.5:21 | [10 empty] | F25 | 43 | 44
BSR130 | DX02 | DIO1 | 130 | 2 | 2 | 0 | 5 | 22 |  |  | DI | [10 empty] | 2.2\0.5:22 | [10 empty] | F25 | 45 | 46
BSR130 | DX02 | DIO1 | 130 | 2 | 2 | 0 | 5 | 23 |  |  | DI | [10 empty] | 2.2\0.5:23 | [10 empty] | F25 | 47 | 48
BSR130 | DX02 | DIO1 | 130 | 2 | 2 | 0 | 5 | 24 |  |  | DI | [10 empty] | 2.2\0.5:24 | [10 empty] | F25 | 49 | 50
BSR130 | DX02 | DIO1 | 130 | 2 | 2 | 0 | 5 | 25 |  |  | DI | [10 empty] | 2.2\0.5:25 | [10 empty] | F25 | 51 | 52
BSR130 | DX02 | DIO1 | 130 | 2 | 2 | 0 | 5 | 26 |  |  | DI | [10 empty] | 2.2\0.5:26 | [10 empty] | F25 | 53 | 54
BSR130 | DX02 | DIO1 | 130 | 2 | 2 | 0 | 5 | 27 |  |  | DI | [10 empty] | 2.2\0.5:27 | [10 empty] | F25 | 55 | 56
BSR130 | DX02 | DIO1 | 130 | 2 | 2 | 0 | 5 | 28 |  |  | DI | [10 empty] | 2.2\0.5:28 | [10 empty] | F25 | 57 | 58
BSR130 | DX02 | DIO1 | 130 | 2 | 2 | 0 | 5 | 29 |  |  | DI | [10 empty] | 2.2\0.5:29 | [10 empty] | F25 | 59 | 60
BSR130 | DX02 | DIO1 | 130 | 2 | 2 | 0 | 5 | 30 |  |  | DI | [10 empty] | 2.2\0.5:30 | [10 empty] | F25 | 61 | 62
BSR130 | DX02 | DIO1 | 130 | 2 | 2 | 0 | 5 | 31 |  |  | DI | [10 empty] | 2.2\0.5:31 | [10 empty] | F25 | 63 | 64
BSR130 | DX02 | DIO1 | 130 | 2 | 2 | 0 | 6 | 0 |  | BMXX0 | [11 empty] | 2.2\0.6:0
BSR130 | DX02 | DIO1 | 130 | 2 | 2 | 0 | 6 | 1 | [13 empty] | 2.2\0.6:1
BSR130 | DX02 | DIO1 | 130 | 2 | 2 | 0 | 6 | 2 | [13 empty] | 2.2\0.6:2
BSR130 | DX02 | DIO1 | 130 | 2 | 2 | 0 | 6 | 3 | [13 empty] | 2.2\0.6:3
BSR130 | DX02 | DIO1 | 130 | 2 | 2 | 0 | 7 | 0 |  | BMXX0 | [11 empty] | 2.2\0.7:0
BSR130 | DX02 | DIO1 | 130 | 2 | 2 | 0 | 7 | 1 | [13 empty] | 2.2\0.7:1
BSR130 | DX02 | DIO1 | 130 | 2 | 2 | 0 | 7 | 2 | [13 empty] | 2.2\0.7:2
BSR130 | DX02 | DIO1 | 130 | 2 | 2 | 0 | 7 | 3 | [13 empty] | 2.2\0.7:3
BSR130 | DX02 | DIO1 | 130 | 2 | 2 | 0 | 8 | 0 |  | BMXX0 | [11 empty] | 2.2\0.8:0
BSR130 | DX02 | DIO1 | 130 | 2 | 2 | 0 | 8 | 1 | [13 empty] | 2.2\0.8:1
BSR130 | DX02 | DIO1 | 130 | 2 | 2 | 0 | 8 | 2 | [13 empty] | 2.2\0.8:2
BSR130 | DX02 | DIO1 | 130 | 2 | 2 | 0 | 8 | 3 | [13 empty] | 2.2\0.8:3
BSR130 | DX02 | DIO1 | 130 | 2 | 2 | 0 | 9 | 0 |  | BMXX0 | [11 empty] | 2.2\0.9:0
BSR130 | DX02 | DIO1 | 130 | 2 | 2 | 0 | 9 | 1 | [13 empty] | 2.2\0.9:1
BSR130 | DX02 | DIO1 | 130 | 2 | 2 | 0 | 9 | 2 | [13 empty] | 2.2\0.9:2
BSR130 | DX02 | DIO1 | 130 | 2 | 2 | 0 | 9 | 3 | [13 empty] | 2.2\0.9:3
BSR130 | DX02 | DIO1 | 130 | 2 | 2 | 0 | 10 | 0 |  | BMXX0 | [11 empty] | 2.2\0.10:0
BSR130 | DX02 | DIO1 | 130 | 2 | 2 | 0 | 10 | 1 | [13 empty] | 2.2\0.10:1
BSR130 | DX02 | DIO1 | 130 | 2 | 2 | 0 | 10 | 2 | [13 empty] | 2.2\0.10:2
BSR130 | DX02 | DIO1 | 130 | 2 | 2 | 0 | 10 | 3 | [13 empty] | 2.2\0.10:3
BSR130 | DX02 | DIO1 | 130 | 2 | 2 | 0 | 11 | 0 |  | BMXX0 | [11 empty] | 2.2\0.11:0
BSR130 | DX02 | DIO1 | 130 | 2 | 2 | 0 | 11 | 1 | [13 empty] | 2.2\0.11:1
BSR130 | DX02 | DIO1 | 130 | 2 | 2 | 0 | 11 | 2 | [13 empty] | 2.2\0.11:2
BSR130 | DX02 | DIO1 | 130 | 2 | 2 | 0 | 11 | 3 | [13 empty] | 2.2\0.11:3
BCV131SLC01 Flexisoft - Odd AXs
DX1ES01
|  |  |  | 1 | 18 | 0 | 0 | CPU SLC1 |  | 1059305 | Type 3 |  |  |  | FlexiSoft Bus | [6 empty] | 1.18\0.0:CPU SLC1 | BR4-2110-E-00119 | 0
|  |  |  | 1 | 18 | 0 |  | not used |  | 1044073 | [11 empty] | 1.18\0.:not used | BR4-2110-E-00119 | 0
BSR130 | DX02 | SIO1 | SLC01 | 1 | 18 | 0 | 1 | 1 | I1 | IgnoreMUG | SDI |  | 4 |  | XE01 |  | Emergency Stop Reset Request (programmed not wired) | enabled |  | BCV131 |  | 1.18\0.1:1 | BR4-2110-E-00119 | 0
BSR130 | DX02 |  |  | 1 | 18 | 0 | 1 | 2 | I2 |  | SDI |  | 4 |  | YA01 |  | Start-up Warning Request (programmed not wired) | enabled |  | BCV131 |  | 1.18\0.1:2 | BR4-2110-E-00119 | 0
BSR130 | DX02 |  |  | 1 | 18 | 0 | 1 | 3 | I3 | 1044125 | SDI |  | 4 | [6 empty] | BCV131 |  | 1.18\0.1:3 | BR4-2110-E-00119 | 0
BSR130 | DX02 |  |  | 1 | 18 | 0 | 1 | 4 | I4 | 1047162 | SDI |  | 4 | [6 empty] | BCV131 |  | 1.18\0.1:4 | BR4-2110-E-00119 | 0
BSR130 | DX02 |  |  | 1 | 18 | 0 | 1 | 5 | I5 < Y2 | SN# | SDI |  | 4 |  | CAX01 |  | 4RO module 6 Y1 / Y2 feedback | Closed |  | BCV131 |  | 1.18\0.1:5 | BR4-2110-E-00119 | 0
BSR130 | DX02 |  |  | 1 | 18 | 0 | 1 | 6 | I6 < Y4 |  | SDI |  | 4 |  | CAX02 |  | 4RO module 6 Y3 / Y4 feedback | Closed |  | BCV131 |  | 1.18\0.1:6 | BR4-2110-E-00119 | 0
BSR130 | DX02 |  |  | 1 | 18 | 0 | 1 | 7 | I7 |  | SDI |  | 4 | [6 empty] | BCV131 |  | 1.18\0.1:7 | BR4-2110-E-00119 | 0
BSR130 | DX02 |  |  | 1 | 18 | 0 | 1 | 8 | I8 |  | SDI |  | 4 | [6 empty] | BCV131 |  | 1.18\0.1:8 | BR4-2110-E-00119 | 0
BSR130 | DX02 |  |  | 1 | 18 | 0 | 1 | 1 | Q1 > B1 |  | SDO |  | 4 |  | SIL01 |  | Safety Interlock B1 - immediate | Healthy (Solid State Output) |  | BCV131 |  | 1.18\0.1:1 | BR4-2110-E-00119 | 0
BSR130 | DX02 |  |  | 1 | 18 | 0 | 1 | 2 | Q2 > B2 |  | SDO |  | 4 |  | SIL02 |  | Safety Interlock B2 - immediate | Healthy (Solid State Output) |  | BCV131 |  | 1.18\0.1:2 | BR4-2110-E-00119 | 0
BSR130 | DX02 |  |  | 1 | 18 | 0 | 1 | 3 | Q3 > B1 |  | SDO |  | 4 | [6 empty] | BCV131 |  | 1.18\0.1:3 | BR4-2110-E-00119 | 0
BSR130 | DX02 |  |  | 1 | 18 | 0 | 1 | 4 | Q4 > B2 |  | SDO |  | 4 | [6 empty] | BCV131 |  | 1.18\0.1:4 | BR4-2110-E-00119 | 0
BSR130 | DX02 |  |  | 1 | 18 | 0 | 2 | 1A | 13 / 14 | 4RO | SRO |  | 4 |  | SIL01A |  | FLEXISOFT PWS Bus 1 Statutory immediate circuit 1 healthy | Healthy |  | BCV131 |  | 1.18\0.2:1A | BR4-2110-E-00119 | 0 | wired to stat CCT
BSR130 | DX02 |  |  | 1 | 18 | 0 | 2 | 1B | 23 / 24 | 6026143 | SRO |  | 4 |  | SIL01B |  | FLEXISOFT PWS Bus 1 Statutory immediate circuit 1 healthy | Healthy |  | BCV131 |  | 1.18\0.2:1B | BR4-2110-E-00119 | 0 | monitored
BSR130 | DX02 |  |  | 1 | 18 | 0 | 2 | 1C | Y14 |  | SSDO |  | 4 |  | SIL01C |  | FLEXISOFT PWS Bus 1 Statutory immediate circuit 1 healthy | Healthy (Solid State Output) |  | BCV131 |  | 1.18\0.2:1C | BR4-2110-E-00119 | 0
BSR130 | DX02 |  |  | 1 | 18 | 0 | 2 | 1M | Y1>+ / Y2>I5 |  | SRMO |  | 4 |  | SIL01M |  | Feedback Channel 1A / 1B closed | Healthy Relay (Feedback) |  | BCV131 |  | 1.18\0.2:1M | BR4-2110-E-00119 | 0
BSR130 | DX02 |  |  | 1 | 18 | 0 | 2 | 2A | 33 / 34 |  | SRO |  | 4 |  | SIL02A |  | FLEXISOFT PWS Bus 1 Statutory immediate circuit 2 healthy | Healthy |  | BCV131 |  | 1.18\0.2:2A | BR4-2110-E-00119 | 0 | wired to stat CCT
BSR130 | DX02 |  |  | 1 | 18 | 0 | 2 | 2B | 43 / 44 |  | SRO |  | 4 |  | SIL02B |  | FLEXISOFT PWS Bus 1 Statutory immediate circuit 2 healthy | Healthy |  | BCV131 |  | 1.18\0.2:2B | BR4-2110-E-00119 | 0 | monitored
BSR130 | DX02 |  |  | 1 | 18 | 0 | 2 | 2C | Y24 |  | SSDO |  | 4 |  | SIL02C |  | FLEXISOFT PWS Bus 1 Statutory immediate circuit 2 healthy | Healthy (Solid State Output) |  | BCV131 |  | 1.18\0.2:2C | BR4-2110-E-00119 | 0
BSR130 | DX02 |  |  | 1 | 18 | 0 | 2 | 2M | Y3>+ / Y4>I6 |  | SRMO |  | 4 |  | SIL02M |  | Feedback Channel 2A / 2B closed | Healthy Relay (Feedback) |  | BCV131 |  | 1.18\0.2:2M | BR4-2110-E-00119 | 0
BCV131SLC02 Flexisoft - Even AXs
|  |  |  | 2 | 18 | 0 | 0 | CPU SLC1 |  | 1059305 | Type 3 |  |  |  | FlexiSoft Bus | [6 empty] | 2.18\0.0:CPU SLC1 | BR4-2110-E-00120 | 0
|  |  |  | 2 | 18 | 0 |  | not used | [13 empty] | 2.18\0.:not used | BR4-2110-E-00120 | 0
BSR130 | DX02 | SIO1 | SLC02 | 2 | 18 | 0 | 1 | 1 | I1 | IgnoreMUG | SDI |  | 4 |  | XE01 |  | Emergency Stop Reset Request (programmed not wired) | enabled |  | BCV131 |  | 2.18\0.1:1 | BR4-2110-E-00120 | 0
BSR130 | DX02 |  |  | 2 | 18 | 0 | 1 | 2 | I2 |  | SDI |  | 4 |  | YA01 |  | Start-up Warning Request (programmed not wired) | enabled |  | BCV131 |  | 2.18\0.1:2 | BR4-2110-E-00120 | 0
BSR130 | DX02 |  |  | 2 | 18 | 0 | 1 | 3 | I3 | 1044125 | SDI |  | 4 | [6 empty] | BCV131 |  | 2.18\0.1:3 | BR4-2110-E-00120 | 0
BSR130 | DX02 |  |  | 2 | 18 | 0 | 1 | 4 | I4 | 1047162 | SDI |  | 4 | [6 empty] | BCV131 |  | 2.18\0.1:4 | BR4-2110-E-00120 | 0
BSR130 | DX02 |  |  | 2 | 18 | 0 | 1 | 5 | I5 < Y2 | SN# | SDI |  | 4 |  | CAX01 |  | 4RO module 6 Y1 / Y2 feedback | Closed |  | BCV131 |  | 2.18\0.1:5 | BR4-2110-E-00120 | 0
BSR130 | DX02 |  |  | 2 | 18 | 0 | 1 | 6 | I6 < Y4 |  | SDI |  | 4 |  | CAX02 |  | 4RO module 6 Y3 / Y4 feedback | Closed |  | BCV131 |  | 2.18\0.1:6 | BR4-2110-E-00120 | 0
BSR130 | DX02 |  |  | 2 | 18 | 0 | 1 | 7 | I7 |  | SDI |  | 4 | [6 empty] | BCV131 |  | 2.18\0.1:7 | BR4-2110-E-00120 | 0
BSR130 | DX02 |  |  | 2 | 18 | 0 | 1 | 8 | I8 |  | SDI |  | 4 | [6 empty] | BCV131 |  | 2.18\0.1:8 | BR4-2110-E-00120 | 0
BSR130 | DX02 |  |  | 2 | 18 | 0 | 1 | 1 | Q1 > B1 |  | SDO |  | 4 |  | SIL01 |  | Safety Interlock B1 - immediate | Healthy (Solid State Output) |  | BCV131 |  | 2.18\0.1:1 | BR4-2110-E-00120 | 0
BSR130 | DX02 |  |  | 2 | 18 | 0 | 1 | 2 | Q2 > B2 |  | SDO |  | 4 |  | SIL02 |  | Safety Interlock B2 - immediate | Healthy (Solid State Output) |  | BCV131 |  | 2.18\0.1:2 | BR4-2110-E-00120 | 0
BSR130 | DX02 |  |  | 2 | 18 | 0 | 1 | 3 | Q3 > B1 |  | SDO |  | 4 | [6 empty] | BCV131 |  | 2.18\0.1:3 | BR4-2110-E-00120 | 0
BSR130 | DX02 |  |  | 2 | 18 | 0 | 1 | 4 | Q4 > B2 |  | SDO |  | 4 | [6 empty] | BCV131 |  | 2.18\0.1:4 | BR4-2110-E-00120 | 0
BSR130 | DX02 |  |  | 2 | 18 | 0 | 2 | 1A | 13 / 14 | 4RO | SRO |  | 4 |  | SIL01A |  | FLEXISOFT PWS Bus 1 Statutory immediate circuit 1 healthy | Healthy |  | BCV131 |  | 2.18\0.2:1A | BR4-2110-E-00120 | 0 | wired to stat CCT
BSR130 | DX02 |  |  | 2 | 18 | 0 | 2 | 1B | 23 / 24 | 6026143 | SRO |  | 4 |  | SIL01B |  | FLEXISOFT PWS Bus 1 Statutory immediate circuit 1 healthy | Healthy |  | BCV131 |  | 2.18\0.2:1B | BR4-2110-E-00120 | 0 | monitored
BSR130 | DX02 |  |  | 2 | 18 | 0 | 2 | 1C | Y14 |  | SSDO |  | 4 |  | SIL01C |  | FLEXISOFT PWS Bus 1 Statutory immediate circuit 1 healthy | Healthy (Solid State Output) |  | BCV131 |  | 2.18\0.2:1C | BR4-2110-E-00120 | 0
BSR130 | DX02 |  |  | 2 | 18 | 0 | 2 | 1M | Y1>+ / Y2>I5 |  | SRMO |  | 4 |  | SIL01M |  | Feedback Channel 1A / 1B closed | Healthy Relay (Feedback) |  | BCV131 |  | 2.18\0.2:1M | BR4-2110-E-00120 | 0
BSR130 | DX02 |  |  | 2 | 18 | 0 | 2 | 2A | 33 / 34 |  | SRO |  | 4 |  | SIL02A |  | FLEXISOFT PWS Bus 1 Statutory immediate circuit 2 healthy | Healthy |  | BCV131 |  | 2.18\0.2:2A | BR4-2110-E-00120 | 0 | wired to stat CCT
BSR130 | DX02 |  |  | 2 | 18 | 0 | 2 | 2B | 43 / 44 |  | SRO |  | 4 |  | SIL02B |  | FLEXISOFT PWS Bus 1 Statutory immediate circuit 2 healthy | Healthy |  | BCV131 |  | 2.18\0.2:2B | BR4-2110-E-00120 | 0 | monitored
BSR130 | DX02 |  |  | 2 | 18 | 0 | 2 | 2C | Y24 |  | SSDO |  | 4 |  | SIL02C |  | FLEXISOFT PWS Bus 1 Statutory immediate circuit 2 healthy | Healthy (Solid State Output) |  | BCV131 |  | 2.18\0.2:2C | BR4-2110-E-00120 | 0
BSR130 | DX02 |  |  | 2 | 18 | 0 | 2 | 2M | Y3>+ / Y4>I6 |  | SRMO |  | 4 |  | SIL02M |  | Feedback Channel 2A / 2B closed | Healthy Relay (Feedback) |  | BCV131 |  | 2.18\0.2:2M | BR4-2110-E-00120 | 0
|  |  | 130 | [7 empty] | PNOZs4 | [5 empty] | BCV131 MASTER |  | K155-1 | BCV131 |  |  | BR4-2110-E-00119 | [9 empty] | F32 | 1 | 2 | 3 | 4
|  |  | 130 | [7 empty] | PNOZs4 | [5 empty] | BCV131 MASTER to BCV131PP04 |  | K155-1 | BCV131 |  |  | BR4-2110-E-00119 | [9 empty] | F32 | 5 | 6 | 7 | 8
|  |  | 130 | [7 empty] | PNOZs7.1 | [5 empty] | BCV131 MASTER to BCV131PP05 |  | K155-2 | BCV131 |  |  | BR4-2110-E-00119 | [9 empty] | F32 | 9 | 10 | 11 | 12
[17 empty] | BCV130GB01LCS01 MASTER |  |  | BCV130GB01 | [12 empty] | F32 | 13 | 14 | 15 | 16
|  |  | 130 | [7 empty] | PNOZs4 | [5 empty] | BCV130GB01LCS01 MASTER to BCV130FN02 bucket |  | K??? | BCV130GB01 | [12 empty] | F32 | 17 | 18 | 19 | 20
|  |  | 130 | [7 empty] | PNOZs7.1 | [5 empty] | BCV130GB01LCS01 MASTER to BCV130PP04 bucket |  | K??? | BCV130GB01 | [12 empty] | F32 | 21 | 22 | 23 | 24
|  |  | 130 | [7 empty] | PNOZs4 | [5 empty] | BCV130 MASTER to VSD SAFE TORQUE OFF |  | K305-1 | BCV130 |  |  | BR4-2110-E-00230 | [9 empty] | F32 | 25 | 26 | 27 | 28
|  |  | 130 | [7 empty] | PNOZs4 | [5 empty] | BCV130 MASTER |  | K305-1 | BCV130 | [12 empty] | F32 | 29 | 30 | 31 | 32
|  |  | 130 | [7 empty] | PNOZs7.1 | [5 empty] | BCV130 MASTER to BCV130PP01 (brake) |  | K305-2 | BCV130 | [12 empty] | F32 | 33 | 34 | 35 | 36
|  |  | 130 | [7 empty] | PNOZs4 | [5 empty] | BCV130DX07 summary relay |  | K403 | BCV130 | [12 empty] | F32 | 37 | 38 | 39 | 40
|  |  | 130 | [7 empty] | PNOZs4 | [5 empty] | BCV130MA01 COOLING MASTER from field panel safety relay |  | K355-1 | BCV130MA01 | [12 empty] | F32 | 41 | 42 | 43 | 44
|  |  | 130 | [7 empty] | PNOZs4 | [5 empty] | BCV130 MA01 TROLLEY MASTER from field panel safety relay |  | K375-1 | BCV130MA01 | [12 empty] | F32 | 45 | 46 | 47 | 48
|  |  | 130 | [7 empty] | PNOZs4 | [5 empty] | BCV130DX08 summary relay |  | K425 | BCV130 | [12 empty] | F32 | 49 | 50 | 51 | 52
[17 empty] | BCV130PP03 field LOS to bucket | [15 empty] | F32 | 53 | 54 | 55 | 56
|  |  | 130 | [13 empty] | BCV130MA01 MASTER to BCV130PP02) |  | K355-1 | BCV130MA01 | [12 empty] | F32 | 57 | 58 | 59 | 60
|  |  | 130 | [7 empty] | PNOZs7.1 | [5 empty] | BCV130MA01 MASTER to FN03 bucket |  | K355-2 | BCV130MA01 | [12 empty] | F32 | 61 | 62 | 63 | 64
|  |  | 130 | [7 empty] | PNOZs7.2 | [5 empty] | BCV130MA01 MASTER to FN04 bucket |  | K355-3 | BCV130MA01 | [12 empty] | F32 | 65 | 66 | 67 | 68
|  |  | 130 | [13 empty] | BCV130MA01 MASTER to MT01 bucket |  | K375-1 | BCV130MA01 | [12 empty] | F32 | 69 | 70 | 71 | 72
|  |  | 130 | [7 empty] | PNOZs7.1 | [5 empty] | BCV130MA01 MASTER to MT01EM02 bucket |  | K375-2 | BCV130MA01 | [12 empty] | F32 | 73 | 74 | 75 | 76
|  |  | 130 | [7 empty] | PNOZs4 | [5 empty] | BCV130DX09 summary relay |  | K453 | BCV130 | [12 empty] | F32 | 77 | 78 | 79 | 80
[17 empty] | BCV130FN01 field LOS to bucket |  | field link | [13 empty] | F32 | 81 | 82 | 83 | 84
[17 empty] | BCV130FN02 field LOS to bucket |  | field link | [5 empty] | Removed as has been replaced by F32/17-20 | [7 empty] | F32 | 85 | 86 | 87 | 88
[17 empty] | BTN130PP01 field LOS to bucket |  | field link | [13 empty] | F32 | 89 | 90 | 91 | 92
|  | TeSysT |  |  |  | PR | 1 | 1 | C / I1 | TeSysT | DI |  | 4 |  | CB01 |  | Drive Circuit Breaker | Closed | Q103 | BTN130PP01 |  |  | BR4-2110-E-00213 | A
[6 empty] | PR | 1 | 2 | C / I2 | DX01ES01 | DI |  | 5 |  | TRP02 |  | Drive Circuit Breaker | Tripped | Q103 | BTN130PP01 |  |  | BR4-2110-E-00213 | A
[6 empty] | PR | 1 | 3 | C / I3 |  | DI |  | 5 |  | CAX01 |  | Drive Contactor | Closed | K148 | BTN130PP01 |  |  | BR4-2110-E-00213 | A
[6 empty] | PR | 1 | 4 | C / I4 |  | DI |  | 4 |  | SY01 |  | Safety Interlock Relay | Healthy | K165 | BTN130PP01 |  |  | BR4-2110-E-00213 | A
[6 empty] | PR | 1 | 5 | C / I5 |  | DI | [8 empty] | BTN130PP01 |  |  | BR4-2110-E-00213 | A
[6 empty] | PR | 1 | 6 | C / I6 |  | DI |  | 4 |  | SW01 |  | Remote Mode | Selected |  | BTN130PP01 |  |  | BR4-2110-E-00213 | A
[6 empty] | PR | 1 | 1 | 13 / 14 |  | DO |  | 4 |  | SR01 |  | Start Relay | Closed | K159 | BTN130PP01 |  |  | BR4-2110-E-00213 | A
[6 empty] | PR | 1 | 2 | 23 / 24 |  | DO |  | 5 |  | SHT01 |  | Shunt Trip | Activated | K161 | BTN130PP01 |  |  | BR4-2110-E-00213 | A
[6 empty] | PR | 1 | 3 | 33 / 34 |  | DO |  | 5 | [6 empty] | BTN130PP01 |  |  | BR4-2110-E-00213 | A
[6 empty] | PR | 1 | 4 | 95 / 96 |  | DO |  | 5 |  | TRP01 |  | Drive Circuit Breaker | Trip | Q103 | BTN130PP01 |  |  | BR4-2110-E-00213 | A
|  | TeSysT |  |  |  | PR | 1 | 1 | C / I1 | TeSysT | DI |  | 4 |  | CB01 |  | Drive Circuit Breaker | Closed | Q103 | BCV130PP01 |  |  | BR4-2110-E-00217 | A
[6 empty] | PR | 1 | 2 | C / I2 | DX01ES01 | DI |  | 5 |  | TRP02 |  | Drive Circuit Breaker | Tripped | Q103 | BCV130PP01 |  |  | BR4-2110-E-00217 | A
[6 empty] | PR | 1 | 3 | C / I3 |  | DI |  | 5 |  | CAX01 |  | Drive Contactor | Closed | K148 | BCV130PP01 |  |  | BR4-2110-E-00217 | A
[6 empty] | PR | 1 | 4 | C / I4 |  | DI |  | 4 |  | SY01 |  | Safety Interlock Relay | Healthy | K165 | BCV130PP01 |  |  | BR4-2110-E-00217 | A
[6 empty] | PR | 1 | 5 | C / I5 |  | DI
[6 empty] | PR | 1 | 6 | C / I6 |  | DI |  | 4 |  | SW01 |  | Remote Mode | Selected |  | BCV130PP01 |  |  | BR4-2110-E-00217 | A
[6 empty] | PR | 1 | 1 | 13 / 14 |  | DO |  | 4 |  | SR01 |  | Start Relay | Closed | K159 | BCV130PP01 |  |  | BR4-2110-E-00217 | A
[6 empty] | PR | 1 | 2 | 23 / 24 |  | DO |  | 5 |  | SHT01 |  | Shunt Trip | Activated | K161
[6 empty] | PR | 1 | 3 | 33 / 34 |  | DO |  | 5
[6 empty] | PR | 1 | 4 | 95 / 96 |  | DO |  | 5 |  | TRP01 |  | Drive Circuit Breaker | Trip | Q103
|  | TeSysT |  |  |  | PR | 1 | 1 | C / I1 | TeSysT | DI |  | 4 |  | CB01 |  | Drive Circuit Breaker | Closed | Q103 | BCV130PP03 |  |  | BR4-2110-E-00220 | A
[6 empty] | PR | 1 | 2 | C / I2 | DX01ES01 | DI |  | 5 |  | TRP02 |  | Drive Circuit Breaker | Tripped | Q103 | BCV130PP03 |  |  | BR4-2110-E-00220 | A
[6 empty] | PR | 1 | 3 | C / I3 |  | DI |  | 5 |  | CAX01 |  | Drive Contactor | Closed | K148 | BCV130PP03 |  |  | BR4-2110-E-00220 | A
[6 empty] | PR | 1 | 4 | C / I4 |  | DI |  | 4 |  | SY01 |  | Safety Interlock Relay | Healthy | K165 | BCV130PP03 |  |  | BR4-2110-E-00220 | A
[6 empty] | PR | 1 | 5 | C / I5 |  | DI | [8 empty] | BCV130PP03 |  |  | BR4-2110-E-00220 | A
[6 empty] | PR | 1 | 6 | C / I6 |  | DI |  | 4 |  | SW01 |  | Remote Mode | Selected |  | BCV130PP03 |  |  | BR4-2110-E-00220 | A
[6 empty] | PR | 1 | 1 | 13 / 14 |  | DO |  | 4 |  | SR01 |  | Start Relay | Closed | K159 | BCV130PP03 |  |  | BR4-2110-E-00220 | A
[6 empty] | PR | 1 | 2 | 23 / 24 |  | DO |  | 5 |  | SHT01 |  | Shunt Trip | Activated | K161 | BCV130PP03 |  |  | BR4-2110-E-00220 | A
[6 empty] | PR | 1 | 3 | 33 / 34 |  | DO |  | 5 | [6 empty] | BCV130PP03 |  |  | BR4-2110-E-00220 | A
[6 empty] | PR | 1 | 4 | 95 / 96 |  | DO |  | 5 |  | TRP01 |  | Drive Circuit Breaker | Trip | Q103 | BCV130PP03 |  |  | BR4-2110-E-00220 | A
|  | TeSysT |  |  |  | PR | 1 | 1 | C / I1 | TeSysT | DI |  | 4 |  | CB01 |  | Drive Circuit Breaker | Closed | Q103 | BCV130PP04 |  |  | BR4-2110-E-00221 | A
[6 empty] | PR | 1 | 2 | C / I2 | DX01ES01 | DI |  | 5 |  | TRP02 |  | Drive Circuit Breaker | Tripped | Q103 | BCV130PP04 |  |  | BR4-2110-E-00221 | A
[6 empty] | PR | 1 | 3 | C / I3 |  | DI |  | 5 |  | CAX01 |  | Drive Contactor | Closed | K148 | BCV130PP04 |  |  | BR4-2110-E-00221 | A
[6 empty] | PR | 1 | 4 | C / I4 |  | DI |  | 4 |  | SY01 |  | Safety Interlock Relay | Healthy | K165 | BCV130PP04 |  |  | BR4-2110-E-00221 | A
[6 empty] | PR | 1 | 5 | C / I5 |  | DI | [8 empty] | BCV130PP04 |  |  | BR4-2110-E-00221 | A
[6 empty] | PR | 1 | 6 | C / I6 |  | DI |  | 4 |  | SW01 |  | Remote Mode | Selected |  | BCV130PP04 |  |  | BR4-2110-E-00221 | A
[6 empty] | PR | 1 | 1 | 13 / 14 |  | DO |  | 4 |  | SR01 |  | Start Relay | Closed | K159 | BCV130PP04 |  |  | BR4-2110-E-00221 | A
[6 empty] | PR | 1 | 2 | 23 / 24 |  | DO |  | 5 |  | SHT01 |  | Shunt Trip | Activated | K161 | BCV130PP04 |  |  | BR4-2110-E-00221 | A
[6 empty] | PR | 1 | 3 | 33 / 34 |  | DO |  | 5 | [6 empty] | BCV130PP04 |  |  | BR4-2110-E-00221 | A
[6 empty] | PR | 1 | 4 | 95 / 96 |  | DO |  | 5 |  | TRP01 |  | Drive Circuit Breaker | Trip | Q103 | BCV130PP04 |  |  | BR4-2110-E-00221 | A
|  | TeSysT |  |  |  | PR | 1 | 1 | C / I1 | TeSysT | DI |  | 4 |  | CB01 |  | Drive Circuit Breaker | Closed | Q103 | BCV130FN01 |  |  | BR4-2110-E-00231 | A
[6 empty] | PR | 1 | 2 | C / I2 | DX01ES01 | DI |  | 5 |  | TRP02 |  | Drive Circuit Breaker | Tripped | Q103 | BCV130FN01 |  |  | BR4-2110-E-00231 | A
[6 empty] | PR | 1 | 3 | C / I3 |  | DI |  | 5 |  | CAX01 |  | Drive Contactor | Closed | K148 | BCV130FN01 |  |  | BR4-2110-E-00231 | A
[6 empty] | PR | 1 | 4 | C / I4 |  | DI |  | 4 |  | SY01 |  | Safety Interlock Relay | Healthy | K165 | BCV130FN01 |  |  | BR4-2110-E-00231 | A
[6 empty] | PR | 1 | 5 | C / I5 |  | DI | [8 empty] | BCV130FN01 |  |  | BR4-2110-E-00231 | A
[6 empty] | PR | 1 | 6 | C / I6 |  | DI |  | 4 |  | SW01 |  | Remote Mode | Selected |  | BCV130FN01 |  |  | BR4-2110-E-00231 | A
[6 empty] | PR | 1 | 1 | 13 / 14 |  | DO |  | 4 |  | SR01 |  | Start Relay | Closed | K159 | BCV130FN01 |  |  | BR4-2110-E-00231 | A
[6 empty] | PR | 1 | 2 | 23 / 24 |  | DO |  | 5 |  | SHT01 |  | Shunt Trip | Activated | K161 | BCV130FN01 |  |  | BR4-2110-E-00231 | A
[6 empty] | PR | 1 | 3 | 33 / 34 |  | DO |  | 5 | [6 empty] | BCV130FN01 |  |  | BR4-2110-E-00231 | A
[6 empty] | PR | 1 | 4 | 95 / 96 |  | DO |  | 5 |  | TRP01 |  | Drive Circuit Breaker | Trip | Q103 | BCV130FN01 |  |  | BR4-2110-E-00231 | A
|  | TeSysT |  |  |  | PR | 1 | 1 | C / I1 | TeSysT | DI |  | 4 |  | CB01 |  | Drive Circuit Breaker | Closed | Q103 | BCV130FN02 |  |  | BR4-2110-E-00216 | A
[6 empty] | PR | 1 | 2 | C / I2 | DX01ES01 | DI |  | 5 |  | TRP02 |  | Drive Circuit Breaker | Tripped | Q103 | BCV130FN02 |  |  | BR4-2110-E-00216 | A
[6 empty] | PR | 1 | 3 | C / I3 |  | DI |  | 5 |  | CAX01 |  | Drive Contactor | Closed | K148 | BCV130FN02 |  |  | BR4-2110-E-00216 | A
[6 empty] | PR | 1 | 4 | C / I4 |  | DI |  | 4 |  | SY01 |  | Safety Interlock Relay | Healthy | K165 | BCV130FN02 |  |  | BR4-2110-E-00216 | A
[6 empty] | PR | 1 | 5 | C / I5 |  | DI | [8 empty] | BCV130FN02 |  |  | BR4-2110-E-00216 | A
[6 empty] | PR | 1 | 6 | C / I6 |  | DI |  | 4 |  | SW01 |  | Remote Mode | Selected |  | BCV130FN02 |  |  | BR4-2110-E-00216 | A
[6 empty] | PR | 1 | 1 | 13 / 14 |  | DO |  | 4 |  | SR01 |  | Start Relay | Closed | K159 | BCV130FN02 |  |  | BR4-2110-E-00216 | A
[6 empty] | PR | 1 | 2 | 23 / 24 |  | DO |  | 5 |  | SHT01 |  | Shunt Trip | Activated | K161 | BCV130FN02 |  |  | BR4-2110-E-00216 | A
[6 empty] | PR | 1 | 3 | 33 / 34 |  | DO |  | 5 | [6 empty] | BCV130FN02 |  |  | BR4-2110-E-00216 | A
[6 empty] | PR | 1 | 4 | 95 / 96 |  | DO |  | 5 |  | TRP01 |  | Drive Circuit Breaker | Trip | Q103 | BCV130FN02 |  |  | BR4-2110-E-00216 | A
|  | TeSysT |  |  |  | PR | 1 | 1 | C / I1 | TeSysT | DI |  | 4 |  | CB01 |  | Drive Circuit Breaker | Closed | Q103 | BCV130PP02 |  |  | BR4-2110-E-00233 | A
[6 empty] | PR | 1 | 2 | C / I2 | DX01ES01 | DI |  | 5 |  | TRP02 |  | Drive Circuit Breaker | Tripped | Q103 | BCV130PP02 |  |  | BR4-2110-E-00233 | A
[6 empty] | PR | 1 | 3 | C / I3 |  | DI |  | 5 |  | CAX01 |  | Drive Contactor | Closed | K148 | BCV130PP02 |  |  | BR4-2110-E-00233 | A
[6 empty] | PR | 1 | 4 | C / I4 |  | DI |  | 4 |  | SY01 |  | Safety Interlock Relay | Healthy | K165 | BCV130PP02 |  |  | BR4-2110-E-00233 | A
[6 empty] | PR | 1 | 5 | C / I5 |  | DI | [8 empty] | BCV130PP02
[6 empty] | PR | 1 | 6 | C / I6 |  | DI |  | 4 |  | SW01 |  | Remote Mode | Selected |  | BCV130PP02 |  |  | BR4-2110-E-00233 | A
[6 empty] | PR | 1 | 1 | 13 / 14 |  | DO |  | 4 |  | SR01 |  | Start Relay | Closed | K159 | BCV130PP02 |  |  | BR4-2110-E-00233 | A
[6 empty] | PR | 1 | 2 | 23 / 24 |  | DO |  | 5 |  | SHT01 |  | Shunt Trip | Activated | K161 | BCV130PP02
[6 empty] | PR | 1 | 3 | 33 / 34 |  | DO |  | 5 | [6 empty] | BCV130PP02
[6 empty] | PR | 1 | 4 | 95 / 96 |  | DO |  | 5 |  | TRP01 |  | Drive Circuit Breaker | Trip | Q103 | BCV130PP02
|  | TeSysT |  |  |  | PR | 1 | 1 | C / I1 | TeSysT | DI |  | 4 |  | CB01 |  | Drive Circuit Breaker | Closed | Q103 | BCV130FN03 |  |  | BR4-2110-E-00234 | A
[6 empty] | PR | 1 | 2 | C / I2 | DX01ES01 | DI |  | 5 |  | TRP02 |  | Drive Circuit Breaker | Tripped | Q103 | BCV130FN03 |  |  | BR4-2110-E-00234 | A
[6 empty] | PR | 1 | 3 | C / I3 |  | DI |  | 5 |  | CAX01 |  | Drive Contactor | Closed | K148 | BCV130FN03 |  |  | BR4-2110-E-00234 | A
[6 empty] | PR | 1 | 4 | C / I4 |  | DI |  | 4 |  | SY01 |  | Safety Interlock Relay | Healthy | K165 | BCV130FN03 |  |  | BR4-2110-E-00234 | A
[6 empty] | PR | 1 | 5 | C / I5 |  | DI | [8 empty] | BCV130FN03
[6 empty] | PR | 1 | 6 | C / I6 |  | DI |  | 4 |  | SW01 |  | Remote Mode | Selected |  | BCV130FN03 |  |  | BR4-2110-E-00234 | A
[6 empty] | PR | 1 | 1 | 13 / 14 |  | DO |  | 4 |  | SR01 |  | Start Relay | Closed | K159 | BCV130FN03 |  |  | BR4-2110-E-00234 | A
[6 empty] | PR | 1 | 2 | 23 / 24 |  | DO |  | 5 |  | SHT01 |  | Shunt Trip | Activated | K161 | BCV130FN03
[6 empty] | PR | 1 | 3 | 33 / 34 |  | DO |  | 5 | [6 empty] | BCV130FN03
[6 empty] | PR | 1 | 4 | 95 / 96 |  | DO |  | 5 |  | TRP01 |  | Drive Circuit Breaker | Trip | Q103 | BCV130FN03
|  | TeSysT |  |  |  | PR | 1 | 1 | C / I1 | TeSysT | DI |  | 4 |  | CB01 |  | Drive Circuit Breaker | Closed | Q103 | BCV130FN04 |  |  | BR4-2110-E-00235 | A
[6 empty] | PR | 1 | 2 | C / I2 | DX01ES01 | DI |  | 5 |  | TRP02 |  | Drive Circuit Breaker | Tripped | Q103 | BCV130FN04 |  |  | BR4-2110-E-00235 | A
[6 empty] | PR | 1 | 3 | C / I3 |  | DI |  | 5 |  | CAX01 |  | Drive Contactor | Closed | K148 | BCV130FN04 |  |  | BR4-2110-E-00235 | A
[6 empty] | PR | 1 | 4 | C / I4 |  | DI |  | 4 |  | SY01 |  | Safety Interlock Relay | Healthy | K165 | BCV130FN04 |  |  | BR4-2110-E-00235 | A
[6 empty] | PR | 1 | 5 | C / I5 |  | DI | [8 empty] | BCV130FN04
[6 empty] | PR | 1 | 6 | C / I6 |  | DI |  | 4 |  | SW01 |  | Remote Mode | Selected |  | BCV130FN04 |  |  | BR4-2110-E-00235 | A
[6 empty] | PR | 1 | 1 | 13 / 14 |  | DO |  | 4 |  | SR01 |  | Start Relay | Closed | K159 | BCV130FN04 |  |  | BR4-2110-E-00235 | A
[6 empty] | PR | 1 | 2 | 23 / 24 |  | DO |  | 5 |  | SHT01 |  | Shunt Trip | Activated | K161 | BCV130FN04
[6 empty] | PR | 1 | 3 | 33 / 34 |  | DO |  | 5 | [6 empty] | BCV130FN04
[6 empty] | PR | 1 | 4 | 95 / 96 |  | DO |  | 5 |  | TRP01 |  | Drive Circuit Breaker | Trip | Q103 | BCV130FN04
|  | TeSysT |  |  |  | PR | 1 | 1 | C / I1 | TeSysT | DI |  | 4 |  | CB01 |  | Drive Circuit Breaker | Closed | Q103 | BCV130MT01EM01 |  |  | BR4-2110-E-00236 | A
[6 empty] | PR | 1 | 2 | C / I2 | DX01ES01 | DI |  | 5 |  | TRP02 |  | Drive Circuit Breaker | Tripped | Q103 | BCV130MT01EM01 |  |  | BR4-2110-E-00236 | A
[6 empty] | PR | 1 | 3 | C / I3 |  | DI |  | 5 |  | CAX01 |  | Drive Contactor | Closed | K148 | BCV130MT01EM01 |  |  | BR4-2110-E-00236 | A
[6 empty] | PR | 1 | 4 | C / I4 |  | DI |  | 3 |  | SY01 |  | Safety Interlock Relay | Healthy | K165 | BCV130MT01EM01 |  |  | BR4-2110-E-00236 | A
[6 empty] | PR | 1 | 5 | C / I5 |  | DI | [8 empty] | BCV130MT01EM01 |  |  | BR4-2110-E-00236 | A
[6 empty] | PR | 1 | 6 | C / I6 |  | DI |  | 3 |  | SW01 |  | Remote Mode | Selected |  | BCV130MT01EM01 |  |  | BR4-2110-E-00236 | A
[6 empty] | PR | 1 | 1 | 13 / 14 |  | DO |  | 3 |  | SR01 |  | Run Clean | Closed | K159 | BCV130MT01EM01 |  |  | BR4-2110-E-00236 | A
[6 empty] | PR | 1 | 2 | 23 / 24 |  | DO |  | 5 |  | SR02 |  | Run Maintenance | Closed | K161 | BCV130MT01EM01 |  |  | BR4-2110-E-00236 | A
[6 empty] | PR | 1 | 3 | 33 / 34 |  | DO | [8 empty] | BCV130MT01EM01 |  |  | BR4-2110-E-00236 | A
[6 empty] | PR | 1 | 4 | 95 / 96 |  | DO |  | 5 |  | TRP01 |  | Drive Circuit Breaker | Trip | Q103 | BCV130MT01EM01 |  |  | BR4-2110-E-00236 | A
[6 empty] | PR | 1 | 7 | C / I7 |  | DI |  | 5 |  | CAX02 |  | Drive Contactor | Closed | K149 | BCV130MT01EM01 |  |  | BR4-2110-E-00236 | A
[6 empty] | PR | 1 | 8 | C / I8 |  | DI
[6 empty] | PR | 1 | 9 | C / I9 |  | DI
[6 empty] | PR | 1 | 10 | C / I10 |  | DI
|  | TeSysT |  |  |  | PR | 1 | 1 | C / I1 | TeSysT | DI |  | 4 |  | CB01 |  | Drive Circuit Breaker | Closed | Q103 | BCV130MT01EM02 |  |  | BR4-2110-E-00237 | A
[6 empty] | PR | 1 | 2 | C / I2 | DX01ES01 | DI |  | 5 |  | TRP02 |  | Drive Circuit Breaker | Tripped | Q103 | BCV130MT01EM02 |  |  | BR4-2110-E-00237 | A
[6 empty] | PR | 1 | 3 | C / I3 |  | DI |  | 5 |  | CAX01 |  | Drive Contactor | Closed | K148 | BCV130MT01EM02 |  |  | BR4-2110-E-00237 | A
[6 empty] | PR | 1 | 4 | C / I4 |  | DI |  | 3 |  | SY01 |  | Safety Interlock Relay | Healthy | K165 | BCV130MT01EM02 |  |  | BR4-2110-E-00237 | A
[6 empty] | PR | 1 | 5 | C / I5 |  | DI | [8 empty] | BCV130MT01EM02 |  |  | BR4-2110-E-00237 | A
[6 empty] | PR | 1 | 6 | C / I6 |  | DI |  | 3 |  | SW01 |  | Remote Mode | Selected |  | BCV130MT01EM02 |  |  | BR4-2110-E-00237 | A
[6 empty] | PR | 1 | 1 | 13 / 14 |  | DO |  | 3 |  | SR01 |  | Run Clean | Closed | K159 | BCV130MT01EM02 |  |  | BR4-2110-E-00237 | A
[6 empty] | PR | 1 | 2 | 23 / 24 |  | DO |  | 5 |  | SR02 |  | Run Maintenance | Closed | K161 | BCV130MT01EM02 |  |  | BR4-2110-E-00237 | A
[6 empty] | PR | 1 | 3 | 33 / 34 |  | DO | [8 empty] | BCV130MT01EM02 |  |  | BR4-2110-E-00237 | A
[6 empty] | PR | 1 | 4 | 95 / 96 |  | DO |  | 5 |  | TRP01 |  | Drive Circuit Breaker | Trip | Q103 | BCV130MT01EM02 |  |  | BR4-2110-E-00237 | A
[6 empty] | PR | 1 | 7 | C / I7 |  | DI |  | 5 |  | CAX02 |  | Drive Contactor | Closed | K149 | BCV130MT01EM02 |  |  | BR4-2110-E-00237 | A
[6 empty] | PR | 1 | 8 | C / I8 |  | DI
[6 empty] | PR | 1 | 9 | C / I9 |  | DI
[6 empty] | PR | 1 | 10 | C / I10 |  | DI
|  | TeSysT |  |  |  | PR | 1 | 1 | C / I1 | TeSysT | DI |  | 4 |  | CB01 |  | Drive Circuit Breaker | Closed | Q103 | BBD130PP01 |  |  | BR4-2110-E-00042 | A
[6 empty] | PR | 1 | 2 | C / I2 | DX01ES01 | DI |  | 5 |  | TRP02 |  | Drive Circuit Breaker | Tripped | Q103 | BBD130PP01 |  |  | BR4-2110-E-00042 | A
[6 empty] | PR | 1 | 3 | C / I3 |  | DI |  | 5 |  | CAX01 |  | Drive Contactor | Closed | K148 | BBD130PP01 |  |  | BR4-2110-E-00042 | A
[6 empty] | PR | 1 | 4 | C / I4 |  | DI |  | 4 |  | SY01 |  | Safety Interlock Relay | Healthy | K165 | BBD130PP01 |  |  | BR4-2110-E-00042 | A
[6 empty] | PR | 1 | 5 | C / I5 |  | DI | [8 empty] | BBD130PP01 |  |  | BR4-2110-E-00042 | A
[6 empty] | PR | 1 | 6 | C / I6 |  | DI |  | 4 |  | SW01 |  | Remote Mode | Selected |  | BBD130PP01 |  |  | BR4-2110-E-00042 | A
[6 empty] | PR | 1 | 1 | 13 / 14 |  | DO |  | 4 |  | SR01 |  | Start Relay | Closed | K159 | BBD130PP01 |  |  | BR4-2110-E-00042 | A
[6 empty] | PR | 1 | 2 | 23 / 24 |  | DO |  | 5 |  | SHT01 |  | Shunt Trip | Activated | K161 | BBD130PP01 |  |  | BR4-2110-E-00042 | A
[6 empty] | PR | 1 | 3 | 33 / 34 |  | DO |  | 5 | [6 empty] | BBD130PP01 |  |  | BR4-2110-E-00042 | A
[6 empty] | PR | 1 | 4 | 95 / 96 |  | DO |  | 5 |  | TRP01 |  | Drive Circuit Breaker | Trip | Q103 | BBD130PP01 |  |  | BR4-2110-E-00042 | A
[13 empty] | 5 | [6 empty] | BCV131PP04 |  |  | BR4-2110-E-00218 | A | BPL132 controlled
[20 empty] | BCV131PP05 |  |  | BR4-2110-E-00219 | A | BPL132 controlled
|  | ACS880 |  |  |  |  | 1 | 1 | XDI:1 | ACS880 | DI |  | 4 |  | ENB01 |  | Run |  |  | BCV130 |  |  | BR4-2110-E-00229 | A
[7 empty] | 1 | 2 | XDI:2 |  | DI
[7 empty] | 1 | 3 | XDI:3 |  | DI |  | 4 |  | IS01 |  | Drive Isolator | Closed |  | BCV130 |  |  | BR4-2110-E-00229 | A
[7 empty] | 1 | 6 | XDI:6 |  | DI
[7 empty] | 1 |  | STO |  | DI |  | 4 |  | VS01SY01 |  | STO Relay | Healthy |  | BCV130 |  |  | BR4-2110-E-00229 | A
|  | PR |  |  |  |  | 1 |  |  | MASTERPACT_VAMP |  |  | 4 | [6 empty] | BMC1302INC01 |  |  | BR4-2110-E-00222 | A | Process Bus A Incomer
|  | PR |  |  |  |  | 1 |  | VAMP RJ45 | DX01ES01 |  |  | 4
|  | PR |  |  |  |  | 1 |  | CUB RJ45 | DX01ES01 |  |  | 4
|  | PR |  |  |  |  | 1 |  |  | MASTERPACT |  |  | 4 | [6 empty] | BMC1302INC02 |  |  | BR4-2110-E-00224 | A | Essential Bus Incomer
|  | PR |  |  |  |  | 1 | [5 empty] | 4
|  | PR |  |  |  |  | 1 |  | CUB RJ45 | DX01ES01 |  |  | 4
|  | PR |  |  |  |  | 1 |  |  | MASTERPACT |  |  | 4 | [6 empty] | BMC1302INC03 |  |  | BR4-2110-E-00226 | A | Generator Incomer
|  | PR |  |  |  |  | 1 | [5 empty] | 4
|  | PR |  |  |  |  | 1 |  | CUB RJ45 | DX01ES01 |  |  | 4

## Field IO Assignment
Item | Box | Node | PLC | Bus | Drop | Rack | Slot | Ch | Terminal | Node Type | IO Type | Rev | Instrument Tag | Device | Instrument List Description | Desc2 | State | Location | Drive | Datatype | Address | Drawing | Rev | Notes | FAT | SAT | Raw_Zero | Raw_Full | Eng_Zero | Eng_Full | Format | T S | T1 | T2 | T3 | T4 | Alm_AREA | Alm_PRIV | Alm_HELP | Alm_CATEGORY | Alm_CUSTOM1 | Alm_CUSTOM2 | Alm_CUSTOM3 | Alm_CUSTOM4 | Alm_CUSTOM5 | Alm_CUSTOM6 | Alm_CUSTOM7 | Alm_CUSTOM8
BBD130DX03 - Primary Crusher Building - ROM Bin
EIO node #3 | DX03 | DIO1 | 130 | 2 | 3 | 0
BBD130 | DX03 | DIO1 | 130 | 2 | 3 | 0 |  | Chassis |  | BMEXBP1200
BBD130 | DX03 | DIO1 | 130 | 2 | 3 | 0 |  | Power |  | BMXCPS4022 |  | total |  | spare |  | % spare
BBD130 | DX03 | DIO1 | 130 | 2 | 3 | 0 | 0 | Comms |  | BMECRA31210 | I/O1 | 72 |  | 55 |  | 76.39%
BBD130 | DX03 | DIO1 | 130 | 2 | 3 | 0 | 1 | 0 | BMXFCW303 | BMXDDI3202K | DI | 4 | BBD130DX03 | CB01 |  | 240VAC Dump Lights Circuit Breaker | Closed | Q106 | BBD130DX03 |  | 2.3\0.1:0 | BR4-2110-E-00089 | 0 |  | D | [6 empty] | F1 |  | 1
BBD130 | DX03 | DIO1 | 130 | 2 | 3 | 0 | 1 | 1 |  |  | DI | 4 | BBD130DX03 | VDC01 |  | 24VDC DIO1 Output Control Supply | Healthy | Q143 | BBD130DX03 |  | 2.3\0.1:1 | BR4-2110-E-00089 | 0 |  | D | [6 empty] | F1 |  | 2
BBD130 | DX03 | DIO1 | 130 | 2 | 3 | 0 | 1 | 2 |  |  | DI | 4 | BBD130DX03 | VDC02 |  | 24VDC GW1 Control Supply | Healthy | Q157 | BBD130DX03 |  | 2.3\0.1:2 | BR4-2110-E-00089 | 0 |  | D | [6 empty] | F1 |  | 3
BBD130 | DX03 | DIO1 | 130 | 2 | 3 | 0 | 1 | 3 |  |  | DI | 4 | BBD130DX03 | VDC03 |  | 24VDC Instrument Supply | Healthy | Q164 | BBD130DX03 |  | 2.3\0.1:3 | BR4-2110-E-00089 | 0 |  | D | [6 empty] | F1 |  | 4
BBD130 | DX03 | DIO1 | 130 | 2 | 3 | 0 | 1 | 4 |  |  | DI | 4 | BBD130DX03 | VDC04 |  | 24VDC Transmitter Supply | Healthy | Q168 | BBD130DX03 |  | 2.3\0.1:4 | BR4-2110-E-00089 | 0 |  | D | [6 empty] | F1 |  | 5
BBD130 | DX03 | DIO1 | 130 | 2 | 3 | 0 | 1 | 5 |  |  | DI | 4 | BBD130DX03 | VDC05 |  | 24VDC BBD130DX03 PLC Control Supply | Healthy | Q172 | BBD130DX03 |  | 2.3\0.1:5 | BR4-2110-E-00089 | 0 |  | D | [6 empty] | F1 |  | 6
BBD130 | DX03 | DIO1 | 130 | 2 | 3 | 0 | 1 | 6 |  |  | DI | 4 | BBD130DX03 | VDC06 |  | 24VDC BRB13x Emergency Shutdown Control Supply | Healthy | Q176 | BBD130DX03 |  | 2.3\0.1:6 | BR4-2110-E-00089 | 0 |  | D | [6 empty] | F1 |  | 7
BBD130 | DX03 | DIO1 | 130 | 2 | 3 | 0 | 1 | 7 |  |  | DI | 4 | BBD130DX03 | VDC07 |  | Spare Control Supply | Healthy | Q180 | BBD130DX03 |  | 2.3\0.1:7 | BR4-2110-E-00089 | 0 |  | D | [6 empty] | F1 |  | 8
BBD130 | DX03 | DIO1 | 130 | 2 | 3 | 0 | 1 | 8 |  |  | DI | 4 | BBD130DX03 | VDC08 |  | Spare Control Supply | Healthy | Q184 | BBD130DX03 |  | 2.3\0.1:8 | BR4-2110-E-00089 | 0 |  | D | [6 empty] | F1 |  | 9
BBD130 | DX03 | DIO1 | 130 | 2 | 3 | 0 | 1 | 9 |  |  | DI | 4 | BBD130DX03 | VDC09 |  | Spare Control Supply | Healthy | Q188 | BBD130DX03 |  | 2.3\0.1:9 | BR4-2110-E-00089 | 0 |  | D | [6 empty] | F1 |  | 10
BBD130 | DX03 | DIO1 | 130 | 2 | 3 | 0 | 1 | 10 |  |  | DI | 4 | BBD130DX03 | VDC10 |  | Spare Control Supply | Healthy | Q192 | BBD130DX03 |  | 2.3\0.1:10 | BR4-2110-E-00089 | 0 |  | D | [6 empty] | F1 |  | 11
BBD130 | DX03 | DIO1 | 130 | 2 | 3 | 0 | 1 | 11 |  |  | DI | 4 | BBD130DX03 | VDC11 |  | Spare Control Supply | Healthy | Q196 | BBD130DX03 |  | 2.3\0.1:11 | BR4-2110-E-00089 | 0 |  | D | [6 empty] | F1 |  | 12
BBD130 | DX03 | DIO1 | 130 | 2 | 3 | 0 | 1 | 12 |  |  | DI | [9 empty] | 2.3\0.1:12 |  |  |  | S | [6 empty] | F1 |  | 13
BBD130 | DX03 | DIO1 | 130 | 2 | 3 | 0 | 1 | 13 |  |  | DI | [9 empty] | 2.3\0.1:13 |  |  |  | S | [6 empty] | F1 |  | 14
BBD130 | DX03 | DIO1 | 130 | 2 | 3 | 0 | 1 | 14 |  |  | DI | [9 empty] | 2.3\0.1:14 |  |  |  | S | [6 empty] | F1 |  | 15
BBD130 | DX03 | DIO1 | 130 | 2 | 3 | 0 | 1 | 15 |  |  | DI | [9 empty] | 2.3\0.1:15 |  |  |  | S | [6 empty] | F1 |  | 16
BBD130 | DX03 | DIO1 | 130 | 2 | 3 | 0 | 1 | 16 |  |  | DI | 4 | BBN130LS01 | LS01 | ROM BIN | Level Switch High-High | Healthy |  | BBN130 |  | 2.3\0.1:16 | BR4-2110-E-00090 | 0 |  | S | [6 empty] | F1 | 17 | 18
BBD130 | DX03 | DIO1 | 130 | 2 | 3 | 0 | 1 | 17 |  |  | DI | [9 empty] | 2.3\0.1:17 |  |  |  | S | [6 empty] | F1 | 19 | 20
BBD130 | DX03 | DIO1 | 130 | 2 | 3 | 0 | 1 | 18 |  |  | DI | 4 | BRB13xLCS01 | SY01 | ROM BIN AND PRIMARY CRUSHER ROCKBREAKERS | Emergency Shutdown 1 | Healthy | K253-1 | BRB13x |  | 2.3\0.1:18 | BR4-2110-E-00090 | 0 |  | D | [6 empty] | F1 | 21 | 22
BBD130 | DX03 | DIO1 | 130 | 2 | 3 | 0 | 1 | 19 |  |  | DI | 4 | BRB13xLCS02 | SY02 | ROM BIN AND PRIMARY CRUSHER ROCKBREAKERS | Emergency Shutdown 2 | Healthy | K266-1 | BRB13x |  | 2.3\0.1:19 | BR4-2110-E-00090 | 0 |  | D | [6 empty] | F1 | 23 | 24
BBD130 | DX03 | DIO1 | 130 | 2 | 3 | 0 | 1 | 20 |  |  | DI | [9 empty] | 2.3\0.1:20 |  |  |  | S | [6 empty] | F1 | 25 | 26
BBD130 | DX03 | DIO1 | 130 | 2 | 3 | 0 | 1 | 21 |  |  | DI | [9 empty] | 2.3\0.1:21 |  |  |  | S | [6 empty] | F1 | 27 | 28
BBD130 | DX03 | DIO1 | 130 | 2 | 3 | 0 | 1 | 22 |  |  | DI | [9 empty] | 2.3\0.1:22 |  |  |  | S | [6 empty] | F1 | 29 | 30
BBD130 | DX03 | DIO1 | 130 | 2 | 3 | 0 | 1 | 23 |  |  | DI |  | BRB131 |  | SPARE ROM BIN ROCKBREAKER | [5 empty] | 2.3\0.1:23 |  |  |  | S | [6 empty] | F1 | 31 | 32
BBD130 | DX03 | DIO1 | 130 | 2 | 3 | 0 | 1 | 24 |  |  | DI | 4 | BRB131HP01 | FS03 | ROM BIN ROCKBREAKER HPU | Flow Switch | Healthy |  | BRB131HP01 |  | 2.3\0.1:24 | BR4-2110-E-00090 | 0 |  | S | [6 empty] | F1 | 33 | 34
BBD130 | DX03 | DIO1 | 130 | 2 | 3 | 0 | 1 | 25 |  |  | DI | 4 | BRB131XS01 | XS01 | ROM BIN ROCKBREAKER | HPU | Ready | R327 | BRB131 |  | 2.3\0.1:25 | BR4-2110-E-00090 | 0 |  | S | [6 empty] | F1 | 35 | 36
BBD130 | DX03 | DIO1 | 130 | 2 | 3 | 0 | 1 | 26 |  |  | DI | 4 | BRB131XS02 | XS02 | ROM BIN ROCKBREAKER | HPU | Running | R329 | BRB131 |  | 2.3\0.1:26 | BR4-2110-E-00090 | 0 |  | S | [6 empty] | F1 | 37 | 38
BBD130 | DX03 | DIO1 | 130 | 2 | 3 | 0 | 1 | 27 |  |  | DI | 4 | BRB131XS03 | XS03 | ROM BIN ROCKBREAKER | Safety System | Healthy | R331 | BRB131 |  | 2.3\0.1:27 | BR4-2110-E-00090 | 0 |  | S | [6 empty] | F1 | 39 | 40
BBD130 | DX03 | DIO1 | 130 | 2 | 3 | 0 | 1 | 28 |  |  | DI | 4 | BRB131XS04 | XS04 | ROM BIN ROCKBREAKER | Hpu In Test / Operate Mode |  | R333 | BRB131 |  | 2.3\0.1:28 | BR4-2110-E-00090 | 0 |  | S | [6 empty] | F1 | 41 | 42
BBD130 | DX03 | DIO1 | 130 | 2 | 3 | 0 | 1 | 29 |  |  | DI | 4 | BRB131XS05 | XS05 | ROM BIN ROCKBREAKER | Boomsafe | Ready | R452 | BRB131 |  | 2.3\0.1:29 | BR4-2110-E-00090 | 0 |  | S | [6 empty] | F1 | 43 | 44
BBD130 | DX03 | DIO1 | 130 | 2 | 3 | 0 | 1 | 30 |  |  | DI | 4 | BRB131XS06 | XS06 | ROM BIN ROCKBREAKER | Boomsafe | Parked | R454 | BRB131 |  | 2.3\0.1:30 | BR4-2110-E-00090 | 0 |  | S | [6 empty] | F1 | 45 | 46
BBD130 | DX03 | DIO1 | 130 | 2 | 3 | 0 | 1 | 31 |  |  | DI | 4 | BRB131XS07 | XS07 | ROM BIN ROCKBREAKER | Boomsafe In Remote | Activated | R456 | BRB131 |  | 2.3\0.1:31 | BR4-2110-E-00090 | 0 |  | S | [6 empty] | F1 | 47 | 48
BBD130 | DX03 | DIO1 | 130 | 2 | 3 | 0 | 2 | 0 | BMXFTB2010 | BMXDDO1602 | DO | 4 | BBN130SV01 | SV01 | ROM BIN | Water Addition Solenoid 1 |  |  | BBN130 |  | 2.3\0.2:0 | BR4-2110-E-00091 | 0 |  | S | [6 empty] | F5 | 1 | 2
BBD130 | DX03 | DIO1 | 130 | 2 | 3 | 0 | 2 | 1 |  |  | DO | 4 | BBN130SV02 | SV02 | ROM BIN | Water Addition Solenoid 2 |  |  | BBN130 |  | 2.3\0.2:1 | BR4-2110-E-00091 | 0 |  | S | [6 empty] | F5 | 3 | 4
BBD130 | DX03 | DIO1 | 130 | 2 | 3 | 0 | 2 | 2 |  |  | DO | 4 | BBN130SV03 | SV03 | ROM BIN | Water Addition Solenoid 3 |  |  | BBN130 |  | 2.3\0.2:2 | BR4-2110-E-00091 | 0 |  | S | [6 empty] | F5 | 5 | 6
BBD130 | DX03 | DIO1 | 130 | 2 | 3 | 0 | 2 | 3 |  |  | DO | 4 | BBN130SV04 | SV04 | ROM BIN | Water Addition Solenoid 4 |  |  | BBN130 |  | 2.3\0.2:3 | BR4-2110-E-00091 | 0 |  | S | [6 empty] | F5 | 7 | 8
BBD130 | DX03 | DIO1 | 130 | 2 | 3 | 0 | 2 | 4 |  |  | DO | 4 | BBN130SV05 | SV05 | ROM BIN | Water Addition Solenoid 5 |  |  | BBN130 |  | 2.3\0.2:4 | BR4-2110-E-00091 | 0 |  | S | [6 empty] | F5 | 9 | 10
BBD130 | DX03 | DIO1 | 130 | 2 | 3 | 0 | 2 | 5 |  |  | DO | 4 | BBN130SV06 | SV06 | ROM BIN | Water Addition Solenoid 6 |  |  | BBN130 |  | 2.3\0.2:5 | BR4-2110-E-00091 | 0 |  | S | [6 empty] | F5 | 11 | 12
BBD130 | DX03 | DIO1 | 130 | 2 | 3 | 0 | 2 | 6 |  |  | DO | [9 empty] | 2.3\0.2:6 |  |  |  | S | [6 empty] | F5 | 13 | 14
BBD130 | DX03 | DIO1 | 130 | 2 | 3 | 0 | 2 | 7 |  |  | DO | [9 empty] | 2.3\0.2:7 |  |  |  | S | [6 empty] | F5 | 15 | 16
BBD130 | DX03 | DIO1 | 130 | 2 | 3 | 0 | 2 | 8 |  |  | DO | [9 empty] | 2.3\0.2:8 |  |  |  | S | [6 empty] | F5 | 17 | 18
BBD130 | DX03 | DIO1 | 130 | 2 | 3 | 0 | 2 | 9 |  |  | DO | [9 empty] | 2.3\0.2:9 |  |  |  | S | [6 empty] | F5 | 19 | 20
BBD130 | DX03 | DIO1 | 130 | 2 | 3 | 0 | 2 | 10 |  |  | DO | [9 empty] | 2.3\0.2:10 |  |  |  | S | [6 empty] | F5 | 21 | 22
BBD130 | DX03 | DIO1 | 130 | 2 | 3 | 0 | 2 | 11 |  |  | DO | [9 empty] | 2.3\0.2:11 |  |  |  | S | [6 empty] | F5 | 23 | 24
BBD130 | DX03 | DIO1 | 130 | 2 | 3 | 0 | 2 | 12 |  |  | DO | [9 empty] | 2.3\0.2:12 |  |  |  | S | [6 empty] | F5 | 25 | 26
BBD130 | DX03 | DIO1 | 130 | 2 | 3 | 0 | 2 | 13 |  |  | DO | [9 empty] | 2.3\0.2:13 |  |  |  | S | [6 empty] | F5 | 27 | 28
BBD130 | DX03 | DIO1 | 130 | 2 | 3 | 0 | 2 | 14 |  |  | DO | [9 empty] | 2.3\0.2:14 |  |  |  | S | [6 empty] | F5 | 29 | 30
BBD130 | DX03 | DIO1 | 130 | 2 | 3 | 0 | 2 | 15 |  |  | DO | 4 | BBN130SV14 | SV14 | ROM BIN | Dust Suppression Solenoid |  |  | BBN130 |  | 2.3\0.2:15 | BR4-2110-E-00091 | 0 |  | S | [6 empty] | F5 | 31 | 32
BBD130 | DX03 | DIO1 | 130 | 2 | 3 | 0 | 3 | 0 | BMXFTB2010 | BMXDDO1602 | DO | 4 | BBN130 | SR01 | ROM BIN | Traffic Light Relay | No Dump |  | BBN130 |  | 2.3\0.3:0 | BR4-2110-E-00090 | 0 |  | S | [6 empty] | F6 | 1 | 2
BBD130 | DX03 | DIO1 | 130 | 2 | 3 | 0 | 3 | 1 |  |  | DO | 4 | BBN130 | SR02 | ROM BIN | Traffic Light Relay | Dump Permitted |  | BBN130 |  | 2.3\0.3:1 | BR4-2110-E-00090 | 0 |  | S | [6 empty] | F6 | 3 | 4
BBD130 | DX03 | DIO1 | 130 | 2 | 3 | 0 | 3 | 2 |  |  | DO | 4 | [8 empty] | 2.3\0.3:2 | BR4-2110-E-00462 |  |  | S | [6 empty] | F6 | 5 | 6
BBD130 | DX03 | DIO1 | 130 | 2 | 3 | 0 | 3 | 3 |  |  | DO | 4 | BRB131 | SR01 | ROM BIN | Rockbreaker Start Relay | Ok To Operate |  | BRB131 |  | 2.3\0.3:3 | BR4-2110-E-00091 | 0 |  | S | [6 empty] | F6 | 7 | 8
BBD130 | DX03 | DIO1 | 130 | 2 | 3 | 0 | 3 | 4 |  |  | DO | 4 | BRB131 | SR02 | ROM BIN | Rockbreaker Start Relay | Ok To Deploy |  | BRB131 |  | 2.3\0.3:4 | BR4-2110-E-00091 | 0 |  | S | [6 empty] | F6 | 9 | 10
BBD130 | DX03 | DIO1 | 130 | 2 | 3 | 0 | 3 | 5 |  |  | DO | [9 empty] | 2.3\0.3:5 |  |  |  | S | [6 empty] | F6 | 11 | 12
BBD130 | DX03 | DIO1 | 130 | 2 | 3 | 0 | 3 | 6 |  |  | DO | 4 | BSR130DB02 | SR01 | ROM BIN | Rom Area Lighting Control Relay | Enable |  | BSR130DB02 |  | 2.3\0.3:6 | BR4-2110-E-00091 | 0 |  | S | [6 empty] | F6 | 13 | 14
BBD130 | DX03 | DIO1 | 130 | 2 | 3 | 0 | 3 | 7 |  |  | DO | [9 empty] | 2.3\0.3:7 |  |  |  | S | [6 empty] | F6 | 15 | 16
BBD130 | DX03 | DIO1 | 130 | 2 | 3 | 0 | 3 | 8 |  |  | DO | [9 empty] | 2.3\0.3:8 |  |  |  | S | [6 empty] | F6 | 17 | 18
BBD130 | DX03 | DIO1 | 130 | 2 | 3 | 0 | 3 | 9 |  |  | DO | [9 empty] | 2.3\0.3:9 |  |  |  | S | [6 empty] | F6 | 19 | 20
BBD130 | DX03 | DIO1 | 130 | 2 | 3 | 0 | 3 | 10 |  |  | DO | 4 | BBN130SV07 | SV07 | ROM BIN | Water Addition Solenoid 7 |  |  | BBN130 |  | 2.3\0.3:10 | BR4-2110-E-00091 | 0 |  | S | [6 empty] | F6 | 21 | 22
BBD130 | DX03 | DIO1 | 130 | 2 | 3 | 0 | 3 | 11 |  |  | DO | 4 | BBN130SV08 | SV08 | ROM BIN | Water Addition Solenoid 8 |  |  | BBN130 |  | 2.3\0.3:11 | BR4-2110-E-00091 | 0 |  | S | [6 empty] | F6 | 23 | 24
BBD130 | DX03 | DIO1 | 130 | 2 | 3 | 0 | 3 | 12 |  |  | DO | 4 | BBN130SV09 | SV09 | ROM BIN | Water Addition Solenoid 9 |  |  | BBN130 |  | 2.3\0.3:12 | BR4-2110-E-00091 | 0 |  | S | [6 empty] | F6 | 25 | 26
BBD130 | DX03 | DIO1 | 130 | 2 | 3 | 0 | 3 | 13 |  |  | DO | 4 | BBN130SV10 | SV10 | ROM BIN | Water Addition Solenoid 10 |  |  | BBN130 |  | 2.3\0.3:13 | BR4-2110-E-00091 | 0 |  | S | [6 empty] | F6 | 27 | 28
BBD130 | DX03 | DIO1 | 130 | 2 | 3 | 0 | 3 | 14 |  |  | DO | 4 | BBN130SV11 | SV11 | ROM BIN | Water Addition Solenoid 11 |  |  | BBN130 |  | 2.3\0.3:14 | BR4-2110-E-00091 | 0 |  | S | [6 empty] | F6 | 29 | 30
BBD130 | DX03 | DIO1 | 130 | 2 | 3 | 0 | 3 | 15 |  |  | DO | 4 | BBN130SV12 | SV12 | ROM BIN | Water Addition Solenoid 12 |  |  | BBN130 |  | 2.3\0.3:15 | BR4-2110-E-00091 | 0 |  | S | [6 empty] | F6 | 31 | 32
BBD130 | DX03 | DIO1 | 130 | 2 | 3 | 0 | 4 | 0 | BMXFTW301S | BMEAHI0812 | AI | 4 | BBN130LT01 | LT01 | ROM BIN | Level Transmitter 1 |  | % | BBN130 | REAL | 2.3\0.4:0 | BR4-2110-E-00091 | 0 |  | S |  | 0 | 100 | 0 | 100 | #.# EU | F5 | 33 | 34
BBD130 | DX03 | DIO1 | 130 | 2 | 3 | 0 | 4 | 1 |  |  | AI | 4 | BBN130LT02 | LT02 | ROM BIN | Level Transmitter 2 |  | % | BBN130 | REAL | 2.3\0.4:1 | BR4-2110-E-00091 | 0 |  | S |  | 0 | 100 | 0 | 100 | #.# EU | F5 | 35 | 36
BBD130 | DX03 | DIO1 | 130 | 2 | 3 | 0 | 4 | 2 |  |  | AI | 4 | BBN130ZT01 | ZT01 | ROM BIN | Truck Wheel Position |  | m | BBN130 | REAL | 2.3\0.4:2 | BR4-2110-E-00091 | 0 |  | S |  | 0 | 14.2 | 0 | 14.2 | #.# EU | F5 | 37 | 38
BBD130 | DX03 | DIO1 | 130 | 2 | 3 | 0 | 4 | 3 |  |  | AI | 4 | BBN130ZT02 | ZT02 | ROM BIN | Truck Tray Position |  | m | BBN130 | REAL | 2.3\0.4:3 | BR4-2110-E-00091 | 0 |  | S |  | 0 | 14.2 | 0 | 14.2 | #.# EU | F5 | 39 | 40
BBD130 | DX03 | DIO1 | 130 | 2 | 3 | 0 | 4 | 4 |  |  | AI | [9 empty] | 2.3\0.4:4 |  |  |  | S | [6 empty] | F5 | 41 | 42
BBD130 | DX03 | DIO1 | 130 | 2 | 3 | 0 | 4 | 5 |  |  | AI | [9 empty] | 2.3\0.4:5 |  |  |  | S | [6 empty] | F5 | 43 | 44
BBD130 | DX03 | DIO1 | 130 | 2 | 3 | 0 | 4 | 6 |  |  | AI | [9 empty] | 2.3\0.4:6 |  |  |  | S | [6 empty] | F5 | 45 | 46
BBD130 | DX03 | DIO1 | 130 | 2 | 3 | 0 | 4 | 7 |  |  | AI | [9 empty] | 2.3\0.4:7 |  |  |  | S | [6 empty] | F5 | 47 | 48
BBD130 | DX03 | DIO1 | 130 | 2 | 3 | 0 | 5 |  |  | BMXX0 | [10 empty] | 2.3\0.5:
BBD130 | DX03 | DIO1 | 130 | 2 | 3 | 0 | 5 | [13 empty] | 2.3\0.5:
BBD130 | DX03 | DIO1 | 130 | 2 | 3 | 0 | 5 | [13 empty] | 2.3\0.5:
BBD130 | DX03 | DIO1 | 130 | 2 | 3 | 0 | 5 | [13 empty] | 2.3\0.5:
BBD130 | DX03 | DIO1 | 130 | 2 | 3 | 0 | 6 |  |  | BMXX0 | [10 empty] | 2.3\0.6:
BBD130 | DX03 | DIO1 | 130 | 2 | 3 | 0 | 6 | [13 empty] | 2.3\0.6:
BBD130 | DX03 | DIO1 | 130 | 2 | 3 | 0 | 6 | [13 empty] | 2.3\0.6:
BBD130 | DX03 | DIO1 | 130 | 2 | 3 | 0 | 6 | [13 empty] | 2.3\0.6:
BBD130 | DX03 | DIO1 | 130 | 2 | 3 | 0 | 7 |  |  | BMXX0 | [10 empty] | 2.3\0.7:
BBD130 | DX03 | DIO1 | 130 | 2 | 3 | 0 | 7 | [13 empty] | 2.3\0.7:
BBD130 | DX03 | DIO1 | 130 | 2 | 3 | 0 | 7 | [13 empty] | 2.3\0.7:
BBD130 | DX03 | DIO1 | 130 | 2 | 3 | 0 | 7 | [13 empty] | 2.3\0.7:
BBD130 | DX03 | DIO1 | 130 | 2 | 3 | 0 | 8 |  |  | BMXX0 | [10 empty] | 2.3\0.8:
BBD130 | DX03 | DIO1 | 130 | 2 | 3 | 0 | 8 | [13 empty] | 2.3\0.8:
BBD130 | DX03 | DIO1 | 130 | 2 | 3 | 0 | 8 | [13 empty] | 2.3\0.8:
BBD130 | DX03 | DIO1 | 130 | 2 | 3 | 0 | 8 | [13 empty] | 2.3\0.8:
BBD130 | DX03 | DIO1 | 130 | 2 | 3 | 0 | 9 |  |  | BMXX0 | [10 empty] | 2.3\0.9:
BBD130 | DX03 | DIO1 | 130 | 2 | 3 | 0 | 9 | [13 empty] | 2.3\0.9:
BBD130 | DX03 | DIO1 | 130 | 2 | 3 | 0 | 9 | [13 empty] | 2.3\0.9:
BBD130 | DX03 | DIO1 | 130 | 2 | 3 | 0 | 9 | [13 empty] | 2.3\0.9:
BBD130 | DX03 | DIO1 | 130 | 2 | 3 | 0 | 10 |  |  | BMXX0 | [10 empty] | 2.3\0.10:
BBD130 | DX03 | DIO1 | 130 | 2 | 3 | 0 | 10 | [13 empty] | 2.3\0.10:
BBD130 | DX03 | DIO1 | 130 | 2 | 3 | 0 | 10 | [13 empty] | 2.3\0.10:
BBD130 | DX03 | DIO1 | 130 | 2 | 3 | 0 | 10 | [13 empty] | 2.3\0.10:
BBD130 | DX03 | DIO1 | 130 | 2 | 3 | 0 | 11 |  |  | BMXX0 | [10 empty] | 2.3\0.11:
BBD130 | DX03 | DIO1 | 130 | 2 | 3 | 0 | 11 | [13 empty] | 2.3\0.11:
BBD130 | DX03 | DIO1 | 130 | 2 | 3 | 0 | 11 | [13 empty] | 2.3\0.11:
BBD130 | DX03 | DIO1 | 130 | 2 | 3 | 0 | 11 | [13 empty] | 2.3\0.11:
[10 empty] | PNOZs4 | Safety Relay | 1 | BRB13xLCS01 | LOS01 | ROM BIN AND PRIMARY CRUSHER ROCKBREAKERS | Emergency Shutdown 1 | DEVICE | K253-1 | BRB13x |  |  | BR4-2110-E-00090 | 0 | [8 empty] | F7 | 1 | 2 | 3 | 4
[10 empty] | PNOZs7.1 | Safety Relay | 1 | BRB13x |  |  | Emergency Shutdown |  | K253-2 | BRB13x |  |  | BR4-2110-E-00090 | 0
[10 empty] | PNOZs4 | Safety Relay | 1 | BRB13xLCS02 | LOS01 | ROM BIN AND PRIMARY CRUSHER ROCKBREAKERS | Emergency Shutdown 2 | DEVICE | K266-1 | BRB13x |  |  | BR4-2110-E-00090 | 0 | [8 empty] | F7 | 5 | 6 | 7 | 8
[10 empty] | PNOZs7.1 | Safety Relay | 1 | BRB13x |  |  | Emergency Shutdown |  | K266-2 | BRB13x |  |  | BR4-2110-E-00090 | 0
[10 empty] | * |  | 1 | BRB13x |  | BRB13x MASTER (to BRB131PN01 trip) | Emergency Shutdown | TRIP |  | BRB13x |  |  | BR4-2110-E-00090 | 0 | [8 empty] | F7 | 9 | 10 | 11 | 12
[10 empty] | * |  | 1 | BRB13x |  | BRB13x MASTER (to BRB133PN01 trip) | Emergency Shutdown | TRIP |  | BRB13x |  |  | BR4-2110-E-00090 | 0 | [8 empty] | F7 | 13 | 14 | 15 | 16
[32 empty] | F7 | 17 | 18 | 19 | 20
[32 empty] | F7 | 21 | 22 | 23 | 24
[32 empty] | F7 | 25 | 26 | 27 | 28
[32 empty] | F7 | 29 | 30 | 31 | 32
[32 empty] | F7 | 33 | 34 | 35 | 36
[32 empty] | F7 | 37 | 38 | 39 | 40
[32 empty] | F7 | 41 | 42 | 43 | 44
[32 empty] | F7 | 45 | 46 | 47 | 48
BBD130DX04 - Primary Crusher Building - Apron Feeder
EIO node #4 | DX04 | DIO1 | 130 | 2 | 4 | 0
BBD130 | DX04 | DIO1 | 130 | 2 | 4 | 0 |  | Chassis |  | BMEXBP1200
BBD130 | DX04 | DIO1 | 130 | 2 | 4 | 0 |  | Power |  | BMXCPS4022 |  | total |  | spare |  | % spare
BBD130 | DX04 | DIO1 | 130 | 2 | 4 | 0 | 0 | Comms |  | BMECRA31210 | I/O1 | 152 |  | 65 |  | 42.76%
BBD130 | DX04 | DIO1 | 130 | 2 | 4 | 0 | 1 | 0 | BMXFCW303 | BMXDDI3202K | DI | 5 | BBD130DX04 | CB01 |  | 240VAC Circuit Breaker | Closed | Q106 | BBD130DX04 |  | 2.4\0.1:0 | BR4-2110-E-00093 | 0 |  | D | [6 empty] | F1 |  | 1
BBD130 | DX04 | DIO1 | 130 | 2 | 4 | 0 | 1 | 1 |  |  | DI | 5 | BBD130DX04 | VDC01 |  | 24VDC DIO1 Output Control Supply | Healthy | Q143 | BBD130DX04 |  | 2.4\0.1:1 | BR4-2110-E-00093 | 0 |  | D | [6 empty] | F1 |  | 2
BBD130 | DX04 | DIO1 | 130 | 2 | 4 | 0 | 1 | 2 |  |  | DI | 5 | BBD130DX04 | VDC02 |  | 24VDC GW1 Control Supply | Healthy | Q157 | BBD130DX04 |  | 2.4\0.1:2 | BR4-2110-E-00093 | 0 |  | D | [6 empty] | F1 |  | 3
BBD130 | DX04 | DIO1 | 130 | 2 | 4 | 0 | 1 | 3 |  |  | DI | 5 | BBD130DX04 | VDC03 |  | 24VDC Instrument Supply | Healthy | Q164 | BBD130DX04 |  | 2.4\0.1:3 | BR4-2110-E-00093 | 0 |  | D | [6 empty] | F1 |  | 4
BBD130 | DX04 | DIO1 | 130 | 2 | 4 | 0 | 1 | 4 |  |  | DI | 5 | BBD130DX04 | VDC04 |  | 24VDC Transmitter Supply | Healthy | Q168 | BBD130DX04 |  | 2.4\0.1:4 | BR4-2110-E-00093 | 0 |  | D | [6 empty] | F1 |  | 5
BBD130 | DX04 | DIO1 | 130 | 2 | 4 | 0 | 1 | 5 |  |  | DI | 5 | BBD130DX04 | VDC05 |  | BBD130DX04 24VDC Control Supply | Healthy | Q172 | BBD130DX04 |  | 2.4\0.1:5 | BR4-2110-E-00093 | 0 |  | D | [6 empty] | F1 |  | 6
BBD130 | DX04 | DIO1 | 130 | 2 | 4 | 0 | 1 | 6 |  |  | DI | 5 | BBD130DX04 | VDC06 |  | BVG130 24VDC Control Supply | Healthy | Q176 | BBD130DX04 |  | 2.4\0.1:6 | BR4-2110-E-00093 | 0 |  | D | [6 empty] | F1 |  | 7
BBD130 | DX04 | DIO1 | 130 | 2 | 4 | 0 | 1 | 7 |  |  | DI | 5 | BBD130DX04 | VDC07 |  | BAF130 24VDC Control Supply | Healthy | Q180 | BBD130DX04 |  | 2.4\0.1:7 | BR4-2110-E-00093 | 0 |  | D | [6 empty] | F1 |  | 8
BBD130 | DX04 | DIO1 | 130 | 2 | 4 | 0 | 1 | 8 |  |  | DI | 5 | BBD130DX04 | VDC08 |  | BAF130LU01PP01 24VDC Control Supply | Healthy | Q184 | BBD130DX04 |  | 2.4\0.1:8 | BR4-2110-E-00093 | 0 |  | D | [6 empty] | F1 |  | 9
BBD130 | DX04 | DIO1 | 130 | 2 | 4 | 0 | 1 | 9 |  |  | DI | 5 | BBD130DX04 | VDC09 |  | Spare Control Supply | Healthy | Q188 | BBD130DX04 |  | 2.4\0.1:9 | BR4-2110-E-00093 | 0 |  | D | [6 empty] | F1 |  | 10
BBD130 | DX04 | DIO1 | 130 | 2 | 4 | 0 | 1 | 10 |  |  | DI | 5 | BBD130DX04 | VDC10 |  | Spare Control Supply | Healthy | Q192 | BBD130DX04 |  | 2.4\0.1:10 | BR4-2110-E-00093 | 0 |  | D | [6 empty] | F1 |  | 11
BBD130 | DX04 | DIO1 | 130 | 2 | 4 | 0 | 1 | 11 |  |  | DI | 5 | BBD130DX04 | VDC11 |  | Spare Control Supply | Healthy | Q196 | BBD130DX04 |  | 2.4\0.1:11 | BR4-2110-E-00093 | 0 |  | D | [6 empty] | F1 |  | 12
BBD130 | DX04 | DIO1 | 130 | 2 | 4 | 0 | 1 | 12 |  |  | DI | [9 empty] | 2.4\0.1:12 |  |  |  | S | [6 empty] | F1 |  | 13
BBD130 | DX04 | DIO1 | 130 | 2 | 4 | 0 | 1 | 13 |  |  | DI | [9 empty] | 2.4\0.1:13 |  |  |  | S | [6 empty] | F1 |  | 14
BBD130 | DX04 | DIO1 | 130 | 2 | 4 | 0 | 1 | 14 |  |  | DI | [9 empty] | 2.4\0.1:14 |  |  |  | S | [6 empty] | F1 |  | 15
BBD130 | DX04 | DIO1 | 130 | 2 | 4 | 0 | 1 | 15 |  |  | DI | [9 empty] | 2.4\0.1:15 |  |  |  | S | [6 empty] | F1 |  | 16
BBD130 | DX04 | DIO1 | 130 | 2 | 4 | 0 | 1 | 16 |  |  | DI | 5 | BVG130LCS01 | STT01 | VIBRATING GRIZZLY | Start Pushbutton | Activated | STT01 | BVG130 |  | 2.4\0.1:16 | BR4-2110-E-00061 | A |  | S | [6 empty] | F1 | 17 | 18
BBD130 | DX04 | DIO1 | 130 | 2 | 4 | 0 | 1 | 17 |  |  | DI | 5 | BVG130LCS01 | STP01 | VIBRATING GRIZZLY | Stop Pushbutton | Activated | STP01 | BVG130 |  | 2.4\0.1:17 | BR4-2110-E-00061 | A |  | S | [6 empty] | F1 | 19 | 20
BBD130 | DX04 | DIO1 | 130 | 2 | 4 | 0 | 1 | 18 |  |  | DI | 5 | BVG130CH01BCS01 | BCS01 | VIBRATING GRIZZLY DISCHARGE CHUTE | Blocked Chute Switch | Healthy |  | BVG130 |  | 2.4\0.1:18 | BR4-2110-E-00097 | 0 |  | S | [6 empty] | F1 | 21 | 22
BBD130 | DX04 | DIO1 | 130 | 2 | 4 | 0 | 1 | 19 |  |  | DI | 5 | BBD130FT21 | FQ21 | VIBRATING GRIZZLY DUST SUPPRESSION | Flow Totaliser Pulse | Active |  | BBD130 |  | 2.4\0.1:19 | BR4-2110-E-00097 | 0 |  | S | [6 empty] | F1 | 23 | 24
BBD130 | DX04 | DIO1 | 130 | 2 | 4 | 0 | 1 | 20 |  |  | DI | 5 | BAF130PP01 | THR01 | ROM BIN APRON FEEDER PUMP/MOTOR GROUP 1 MOTOR | PTC Thermistor Relay | Healthy | K187 | BAF130PP01 |  | 2.4\0.1:20 | BR4-2110-E-00051 | 0 |  | S | [6 empty] | F1 | 25 | 26
BBD130 | DX04 | DIO1 | 130 | 2 | 4 | 0 | 1 | 21 |  |  | DI | 5 | BAF130PP02 | THR01 | ROM BIN APRON FEEDER PUMP/MOTOR GROUP 2 MOTOR | PTC Thermistor Relay | Healthy | K187 | BAF130PP02 |  | 2.4\0.1:21 | BR4-2110-E-00052 | 0 |  | S | [6 empty] | F1 | 27 | 28
BBD130 | DX04 | DIO1 | 130 | 2 | 4 | 0 | 1 | 22 |  |  | DI | 5 | BVG130DA01 | THR01 | VIBRATING GRIZZLY DRIVE MOTOR | PTC Thermistor Relay | Healthy | K187 | BVG130 |  | 2.4\0.1:22 | BR4-2110-E-00061 | A |  | S | [6 empty] | F1 | 29 | 30
BBD130 | DX04 | DIO1 | 130 | 2 | 4 | 0 | 1 | 23 |  |  | DI | 5 | BAF130HP01LCS02 | STT01 | ROM BIN APRON FEEDER HPU COOLING FAN 1 | Start Pushbutton | Activated | STT01 | BAF130HP01 |  | 2.4\0.1:23 | BR4-2110-E-00054 | 0 |  | S | [6 empty] | F1 | 31 | 32
BBD130 | DX04 | DIO1 | 130 | 2 | 4 | 0 | 1 | 24 |  |  | DI | 5 | BAF130HP01LCS02 | STP01 | ROM BIN APRON FEEDER HPU COOLING FAN 1 | Stop Pushbutton | Activated | STP01 | BAF130HP01 |  | 2.4\0.1:24 | BR4-2110-E-00054 | 0 |  | S | [6 empty] | F1 | 33 | 34
BBD130 | DX04 | DIO1 | 130 | 2 | 4 | 0 | 1 | 25 |  |  | DI | 5 | BAF130HP01LCS02 | STT02 | ROM BIN APRON FEEDER HPU COOLING FAN 2 | Start Pushbutton | Activated | STT01 | BAF130HP01 |  | 2.4\0.1:25 | BR4-2110-E-00055 | 0 |  | S | [6 empty] | F1 | 35 | 36
BBD130 | DX04 | DIO1 | 130 | 2 | 4 | 0 | 1 | 26 |  |  | DI | 5 | BAF130HP01LCS02 | STP02 | ROM BIN APRON FEEDER HPU COOLING FAN 2 | Stop Pushbutton | Activated | STP01 | BAF130HP01 |  | 2.4\0.1:26 | BR4-2110-E-00055 | 0 |  | S | [6 empty] | F1 | 37 | 38
BBD130 | DX04 | DIO1 | 130 | 2 | 4 | 0 | 1 | 27 |  |  | DI | 5 | BAF130HP01LCS02 | STT03 | ROM BIN APRON FEEDER HPU COOLING FAN 3 | Start Pushbutton | Activated | STT01 | BAF130HP01 |  | 2.4\0.1:27 | BR4-2110-E-00062 | 0 |  | S | [6 empty] | F1 | 39 | 40
BBD130 | DX04 | DIO1 | 130 | 2 | 4 | 0 | 1 | 28 |  |  | DI | 5 | BAF130HP01LCS02 | STP03 | ROM BIN APRON FEEDER HPU COOLING FAN 3 | Stop Pushbutton | Activated | STP01 | BAF130HP01 |  | 2.4\0.1:28 | BR4-2110-E-00062 | 0 |  | S | [6 empty] | F1 | 41 | 42
BBD130 | DX04 | DIO1 | 130 | 2 | 4 | 0 | 1 | 29 |  |  | DI | [9 empty] | 2.4\0.1:29 |  |  |  | S | [6 empty] | F1 | 43 | 44
BBD130 | DX04 | DIO1 | 130 | 2 | 4 | 0 | 1 | 30 |  |  | DI | [9 empty] | 2.4\0.1:30 |  |  |  | S | [6 empty] | F1 | 45 | 46
BBD130 | DX04 | DIO1 | 130 | 2 | 4 | 0 | 1 | 31 |  |  | DI | [9 empty] | 2.4\0.1:31 |  |  |  | S | [6 empty] | F1 | 47 | 48
BBD130 | DX04 | DIO1 | 130 | 2 | 4 | 0 | 2 | 0 | BMXFCW303 | BMXDDI3202K | DI | 5 | BAF130LCS01 | STT01 | ROM BIN APRON FEEDER | Start Pushbutton | Activated | STT01 | BAF130 |  | 2.4\0.2:0 | BR4-2110-E-00094 | 0 |  | S | [6 empty] | F2 | 1 | 2
BBD130 | DX04 | DIO1 | 130 | 2 | 4 | 0 | 2 | 1 |  |  | DI | 5 | BAF130LCS01 | REV01 | ROM BIN APRON FEEDER | Jog Reverse Pushbutton | Activated | REV01 | BAF130 |  | 2.4\0.2:1 | BR4-2110-E-00094 | 0 |  | S | [6 empty] | F2 | 3 | 4
BBD130 | DX04 | DIO1 | 130 | 2 | 4 | 0 | 2 | 2 |  |  | DI | 5 | BAF130LCS01 | STP01 | ROM BIN APRON FEEDER | Stop Pushbutton | Activated | STP01 | BAF130 |  | 2.4\0.2:2 | BR4-2110-E-00094 | 0 |  | S | [6 empty] | F2 | 5 | 6
BBD130 | DX04 | DIO1 | 130 | 2 | 4 | 0 | 2 | 3 |  |  | DI | 5 | BAF130LCS01 | SY01 | ROM BIN APRON FEEDER | Emergency Stop Relay | Healthy | K253 | BAF130 |  | 2.4\0.2:3 | BR4-2110-E-00094 | 0 |  | D | [6 empty] | F2 | 7 | 8
BBD130 | DX04 | DIO1 | 130 | 2 | 4 | 0 | 2 | 4 |  |  | DI | 5 | BAF130PWS01 | PWS01 | ROM BIN APRON FEEDER | Pullwire Switch 1 | Healthy | K203 | BAF130 |  | 2.4\0.2:4 | BR4-2110-E-00094 | 0 |  | D | [6 empty] | F2 | 9 | 10
BBD130 | DX04 | DIO1 | 130 | 2 | 4 | 0 | 2 | 5 |  |  | DI | 5 | BAF130PWS02 | PWS02 | ROM BIN APRON FEEDER | Pullwire Switch 2 | Healthy | K214 | BAF130 |  | 2.4\0.2:5 | BR4-2110-E-00094 | 0 |  | D | [6 empty] | F2 | 11 | 12
BBD130 | DX04 | DIO1 | 130 | 2 | 4 | 0 | 2 | 6 |  |  | DI | 5 | BAF130CH01BCS01 | BCS01 | ROM BIN APRON FEEDER DRIBBLE CHUTE 1 | Blocked Chute Switch | Healthy |  | BAF130CH01 |  | 2.4\0.2:6 | BR4-2110-E-00097 | 0 |  | S | [6 empty] | F2 | 13 | 14
BBD130 | DX04 | DIO1 | 130 | 2 | 4 | 0 | 2 | 7 |  |  | DI | 5 | BAF130CH02BCS01 | BCS01 | ROM BIN APRON FEEDER DRIBBLE CHUTE 2 | Blocked Chute Switch | Healthy |  | BAF130CH02 |  | 2.4\0.2:7 | BR4-2110-E-00097 | 0 |  | S | [6 empty] | F2 | 15 | 16
BBD130 | DX04 | DIO1 | 130 | 2 | 4 | 0 | 2 | 8 |  |  | DI | 5 | BAF130CH03BCS01 | BCS01 | ROM BIN APRON FEEDER DRIBBLE CHUTE 3 | Blocked Chute Switch | Healthy |  | BAF130CH03 |  | 2.4\0.2:8 | BR4-2110-E-00097 | 0 |  | S | [6 empty] | F2 | 17 | 18
BBD130 | DX04 | DIO1 | 130 | 2 | 4 | 0 | 2 | 9 |  |  | DI | [9 empty] | 2.4\0.2:9 |  |  |  | S | [6 empty] | F2 | 19 | 20
BBD130 | DX04 | DIO1 | 130 | 2 | 4 | 0 | 2 | 10 |  |  | DI | 5 | BAF130HP01LCS01 | STT01 | ROM BIN APRON FEEDER HPU | Start Pushbutton | Activated | STT01 | BAF130HP01 |  | 2.4\0.2:10 | BR4-2110-E-00051 | 0 |  | S | [6 empty] | F2 | 21 | 22
BBD130 | DX04 | DIO1 | 130 | 2 | 4 | 0 | 2 | 11 |  |  | DI | 5 | BAF130HP01LCS01 | STP01 | ROM BIN APRON FEEDER HPU | Stop Pushbutton | Activated | STP01 | BAF130HP01 |  | 2.4\0.2:11 | BR4-2110-E-00051 | 0 |  | S | [6 empty] | F2 | 23 | 24
BBD130 | DX04 | DIO1 | 130 | 2 | 4 | 0 | 2 | 12 |  |  | DI | 5 | BAF130HP01LCS01 | SY01 | ROM BIN APRON FEEDER HPU | Emergency Stop Relay | Healthy | K271 | BAF130HP01 |  | 2.4\0.2:12 | BR4-2110-E-00094 | 0 |  | D | [6 empty] | F2 | 25 | 26
BBD130 | DX04 | DIO1 | 130 | 2 | 4 | 0 | 2 | 13 |  |  | DI | 5 | BAF130HP01LCS01 | STT02 | ROM BIN APRON FEEDER HPU CONDITION CIRCULATION PUMP MOTOR | Start Pushbutton | Activated | STT02 | BAF130HP01 |  | 2.4\0.2:13 | BR4-2110-E-00053 | 0 |  | S | [6 empty] | F2 | 27 | 28
BBD130 | DX04 | DIO1 | 130 | 2 | 4 | 0 | 2 | 14 |  |  | DI | 5 | BAF130HP01LCS01 | STP02 | ROM BIN APRON FEEDER HPU CONDITION CIRCULATION PUMP MOTOR | Stop Pushbutton | Activated | STP02 | BAF130HP01 |  | 2.4\0.2:14 | BR4-2110-E-00053 | 0 |  | S | [6 empty] | F2 | 29 | 30
BBD130 | DX04 | DIO1 | 130 | 2 | 4 | 0 | 2 | 15 |  |  | DI | 5 | BAF130PP01 | XS01 | ROM BIN APRON FEEDER PUMP/MOTOR GROUP 1 | Spider Interlock | Healthy |  | BAF130PP01 |  | 2.4\0.2:15 | BR4-2110-E-00092 | 0 |  | S | [6 empty] | F2 | 31 | 32
BBD130 | DX04 | DIO1 | 130 | 2 | 4 | 0 | 2 | 16 |  |  | DI | 5 | BAF130PP02 | XS02 | ROM BIN APRON FEEDER PUMP/MOTOR GROUP 2 | Spider Interlock | Healthy |  | BAF130PP02 |  | 2.4\0.2:16 | BR4-2110-E-00092 | 0 |  | S | [6 empty] | F3 | 1 | 2
BBD130 | DX04 | DIO1 | 130 | 2 | 4 | 0 | 2 | 17 |  |  | DI | 5 | BAF130PP04 | XS03 | ROM BIN APRON FEEDER HPU CONDITION CIRCULATION PUMP MOTOR | Start Interlock | Healthy |  | BAF130PP04 |  | 2.4\0.2:17 | BR4-2110-E-00092 | 0 |  | S | [6 empty] | F3 | 3 | 4
BBD130 | DX04 | DIO1 | 130 | 2 | 4 | 0 | 2 | 18 |  |  | DI | 5 | BAF130ZS01 | ZS01 | ROM BIN APRON FEEDER | Lashing Lug Aft. Maintenance | Healthy |  | BAF130 |  | 2.4\0.2:18 | BR4-2110-E-00095 | 0 |  | S | [6 empty] | F3 | 5 | 6
BBD130 | DX04 | DIO1 | 130 | 2 | 4 | 0 | 2 | 19 |  |  | DI | 5 | BAF130ZS02 | ZS02 | ROM BIN APRON FEEDER | Lashing Lug Fwd. Maintenance | Healthy |  | BAF130 |  | 2.4\0.2:19 | BR4-2110-E-00095 | 0 |  | S | [6 empty] | F3 | 7 | 8
BBD130 | DX04 | DIO1 | 130 | 2 | 4 | 0 | 2 | 20 |  |  | DI | 5 | BAF130ZS03 | ZS03 | ROM BIN APRON FEEDER | Lashing Lug Aft. Maintenance | Healthy |  | BAF130 |  | 2.4\0.2:20 | BR4-2110-E-00095 | 0 |  | S | [6 empty] | F3 | 9 | 10
BBD130 | DX04 | DIO1 | 130 | 2 | 4 | 0 | 2 | 21 |  |  | DI | 5 | BAF130ZS04 | ZS04 | ROM BIN APRON FEEDER | Lashing Lug Fwd. Maintenance | Healthy |  | BAF130 |  | 2.4\0.2:21 | BR4-2110-E-00095 | 0 |  | S | [6 empty] | F3 | 11 | 12
BBD130 | DX04 | DIO1 | 130 | 2 | 4 | 0 | 2 | 22 |  |  | DI | 5 | BAF130ZS05 | ZS05 | ROM BIN APRON FEEDER | Pan Deflection Switch 1 | Healthy |  | BAF130 |  | 2.4\0.2:22 | BR4-2110-E-00095 | 0 |  | S | [6 empty] | F3 | 13 | 14
BBD130 | DX04 | DIO1 | 130 | 2 | 4 | 0 | 2 | 23 |  |  | DI | 5 | BAF130ZS06 | ZS06 | ROM BIN APRON FEEDER | Pan Deflection Switch 2 | Healthy |  | BAF130 |  | 2.4\0.2:23 | BR4-2110-E-00095 | 0 |  | S | [6 empty] | F3 | 15 | 16
BBD130 | DX04 | DIO1 | 130 | 2 | 4 | 0 | 2 | 24 |  |  | DI | 5 | BAF130LU01LCS01 | STT01 | ROM BIN APRON FEEDER LUBRICATION UNIT | Start Pushbutton | Activated | STT01 | BAF130LU01 |  | 2.4\0.2:24 | BR4-2110-E-00050 | 0 |  | S | [6 empty] | F3 | 17 | 18
BBD130 | DX04 | DIO1 | 130 | 2 | 4 | 0 | 2 | 25 |  |  | DI | 5 | BAF130LU01LCS01 | STP01 | ROM BIN APRON FEEDER LUBRICATION UNIT | Stop Pushbutton | Activated | STP01 | BAF130LU01 |  | 2.4\0.2:25 | BR4-2110-E-00050 | 0 |  | S | [6 empty] | F3 | 19 | 20
BBD130 | DX04 | DIO1 | 130 | 2 | 4 | 0 | 2 | 26 |  |  | DI | 5 | BAF130LU01PS01 | PS01 | ROM BIN APRON FEEDER LUBRICATION UNIT | Grease Inlet Filter | Blocked |  | BAF130LU01 |  | 2.4\0.2:26 | BR4-2110-E-00095 | 0 |  | S | [6 empty] | F3 | 21 | 22
BBD130 | DX04 | DIO1 | 130 | 2 | 4 | 0 | 2 | 27 |  |  | DI | 5 | BAF130LU01PS02 | PS02 | ROM BIN APRON FEEDER LUBRICATION UNIT | Grease Outlet Filter | Blocked |  | BAF130LU01 |  | 2.4\0.2:27 | BR4-2110-E-00095 | 0 |  | S | [6 empty] | F3 | 23 | 24
BBD130 | DX04 | DIO1 | 130 | 2 | 4 | 0 | 2 | 28 |  |  | DI | 5 | BAF130LU01ZS01 | ZS01 | ROM BIN APRON FEEDER LUBRICATION UNIT | End Of Line Proximity Switch 1 | Cycled |  | BAF130LU01 |  | 2.4\0.2:28 | BR4-2110-E-00095 | 0 |  | S | [6 empty] | F3 | 25 | 26
BBD130 | DX04 | DIO1 | 130 | 2 | 4 | 0 | 2 | 29 |  |  | DI | 5 | BAF130LU01ZS02 | ZS02 | ROM BIN APRON FEEDER LUBRICATION UNIT | End Of Line Proximity Switch 2 | Cycled |  | BAF130LU01 |  | 2.4\0.2:29 | BR4-2110-E-00095 | 0 |  | S | [6 empty] | F3 | 27 | 28
BBD130 | DX04 | DIO1 | 130 | 2 | 4 | 0 | 2 | 30 |  |  | DI | 5 | BAF130LU01LS01 | LS01 | ROM BIN APRON FEEDER LUBRICATION UNIT | Oil Tank Level Switch | Low |  | BAF130LU01 |  | 2.4\0.2:30 | BR4-2110-E-00095 | 0 |  | S | [6 empty] | F3 | 29 | 30
BBD130 | DX04 | DIO1 | 130 | 2 | 4 | 0 | 2 | 31 |  |  | DI | 5 | BAF130LU01FS01 | FS01 | ROM BIN APRON FEEDER LUBRICATION UNIT | Grease Pulse Meter | Active |  | BAF130LU01 |  | 2.4\0.2:31 | BR4-2110-E-00095 | 0 |  | S | [6 empty] | F3 | 31 | 32
BBD130 | DX04 | DIO1 | 130 | 2 | 4 | 0 | 3 | 0 | BMXFCW303 | BMXDDI3202K | DI | 5 | BVG130ZS01 | ZS01 | VIBRATING GRIZZLY | Metastable Position Switch (B.D.C) | Healthy |  | BVG130 |  | 2.4\0.3:0 | BR4-2110-E-00097 | 0 |  | S | [6 empty] | F6 | 1 | 2
BBD130 | DX04 | DIO1 | 130 | 2 | 4 | 0 | 3 | 1 |  |  | DI | 5 | BAF130HP01FS04 | FS04 | ROM BIN APRON FEEDER HPU FIRE SPRINKLER | Flow Switch | Healthy |  | BAF130HP01 |  | 2.4\0.3:1 | BR4-2110-E-00095 | 0 |  | S | [6 empty] | F6 | 3 | 4
BBD130 | DX04 | DIO1 | 130 | 2 | 4 | 0 | 3 | 2 |  |  | DI | 5 | BVG130DA01 | THR01 | VIBRATING GRIZZLY DRIVE MOTOR | Ptc Thermistor Relay | Healthy | K187 | BVG130 |  | 2.4\0.3:2 | BR4-2110-E-00061 | A | Input moved to (2.4\0.1:22) | S | [6 empty] | F6 | 5 | 6
BBD130 | DX04 | DIO1 | 130 | 2 | 4 | 0 | 3 | 3 |  |  | DI | 5 | BAF130PP01PS06 | PS06 |  | Pump 1A Pressure | Low |  | BAF130PP01 |  | 2.4\0.3:3 | BR4-2110-E-00092 | 0 |  | S | [6 empty] | F6 | 7 | 8
BBD130 | DX04 | DIO1 | 130 | 2 | 4 | 0 | 3 | 4 |  |  | DI | 5 | BAF130PP01PS07 | PS07 |  | Pump 1B Pressure | Low |  | BAF130PP01 |  | 2.4\0.3:4 | BR4-2110-E-00092 | 0 |  | S | [6 empty] | F6 | 9 | 10
BBD130 | DX04 | DIO1 | 130 | 2 | 4 | 0 | 3 | 5 |  |  | DI | 5 | BAF130PP02PS06 | PS06 |  | Pump 2A Pressure | Low |  | BAF130PP02 |  | 2.4\0.3:5 | BR4-2110-E-00092 | 0 |  | S | [6 empty] | F6 | 11 | 12
BBD130 | DX04 | DIO1 | 130 | 2 | 4 | 0 | 3 | 6 |  |  | DI | 5 | BAF130PP02PS07 | PS07 |  | Pump 2B Pressure | Low |  | BAF130PP02 |  | 2.4\0.3:6 | BR4-2110-E-00092 | 0 |  | S | [6 empty] | F6 | 13 | 14
BBD130 | DX04 | DIO1 | 130 | 2 | 4 | 0 | 3 | 7 |  |  | DI | 5 | BAF130HP01TS01 | TS01 |  | Fire Detection Temperature | High |  | BAF130HP01 |  | 2.4\0.3:7 | BR4-2110-E-00092 | 0 |  | S | [6 empty] | F6 | 15 | 16
BBD130 | DX04 | DIO1 | 130 | 2 | 4 | 0 | 3 | 8 |  |  | DI | 5 | BAF130PP01ZS01 | ZS01 |  | Pump 1A Suction Isolation Valve | Closed |  | BAF130PP01 |  | 2.4\0.3:8 | BR4-2110-E-00092 | 0 |  | S | [6 empty] | F6 | 17 | 18
BBD130 | DX04 | DIO1 | 130 | 2 | 4 | 0 | 3 | 9 |  |  | DI | 5 | BAF130PP01ZS02 | ZS02 |  | Pump 1B Suction Isolation Valve | Closed |  | BAF130PP01 |  | 2.4\0.3:9 | BR4-2110-E-00092 | 0 |  | S | [6 empty] | F6 | 19 | 20
BBD130 | DX04 | DIO1 | 130 | 2 | 4 | 0 | 3 | 10 |  |  | DI | 5 | BAF130PP02ZS01 | ZS01 |  | Pump 2A Suction Isolation Valve | Closed |  | BAF130PP02 |  | 2.4\0.3:10 | BR4-2110-E-00092 | 0 |  | S | [6 empty] | F6 | 21 | 22
BBD130 | DX04 | DIO1 | 130 | 2 | 4 | 0 | 3 | 11 |  |  | DI | 5 | BAF130PP02ZS02 | ZS02 |  | Pump 2B Suction Isolation Valve | Closed |  | BAF130PP02 |  | 2.4\0.3:11 | BR4-2110-E-00092 | 0 |  | S | [6 empty] | F6 | 23 | 24
BBD130 | DX04 | DIO1 | 130 | 2 | 4 | 0 | 3 | 12 |  |  | DI | [9 empty] | 2.4\0.3:12 |  |  |  | S | [6 empty] | F6 | 25 | 26
BBD130 | DX04 | DIO1 | 130 | 2 | 4 | 0 | 3 | 13 |  |  | DI | [9 empty] | 2.4\0.3:13 |  |  |  | S | [6 empty] | F6 | 27 | 28
BBD130 | DX04 | DIO1 | 130 | 2 | 4 | 0 | 3 | 14 |  |  | DI | [9 empty] | 2.4\0.3:14 |  |  |  | S | [6 empty] | F6 | 29 | 30
BBD130 | DX04 | DIO1 | 130 | 2 | 4 | 0 | 3 | 15 |  |  | DI | [9 empty] | 2.4\0.3:15 |  |  |  | S | [6 empty] | F6 | 31 | 32
BBD130 | DX04 | DIO1 | 130 | 2 | 4 | 0 | 3 | 16 |  |  | DI | [9 empty] | 2.4\0.3:16 |  |  |  | S | [6 empty] | F4 | 1 | 2
BBD130 | DX04 | DIO1 | 130 | 2 | 4 | 0 | 3 | 17 |  |  | DI | [9 empty] | 2.4\0.3:17 |  |  |  | S | [6 empty] | F4 | 3 | 4
BBD130 | DX04 | DIO1 | 130 | 2 | 4 | 0 | 3 | 18 |  |  | DI | [9 empty] | 2.4\0.3:18 |  |  |  | S | [6 empty] | F4 | 5 | 6
BBD130 | DX04 | DIO1 | 130 | 2 | 4 | 0 | 3 | 19 |  |  | DI | [9 empty] | 2.4\0.3:19 |  |  |  | S | [6 empty] | F4 | 7 | 8
BBD130 | DX04 | DIO1 | 130 | 2 | 4 | 0 | 3 | 20 |  |  | DI | [9 empty] | 2.4\0.3:20 |  |  |  | S | [6 empty] | F4 | 9 | 10
BBD130 | DX04 | DIO1 | 130 | 2 | 4 | 0 | 3 | 21 |  |  | DI | [9 empty] | 2.4\0.3:21 |  |  |  | S | [6 empty] | F4 | 11 | 12
BBD130 | DX04 | DIO1 | 130 | 2 | 4 | 0 | 3 | 22 |  |  | DI | [9 empty] | 2.4\0.3:22 |  |  |  | S | [6 empty] | F4 | 13 | 14
BBD130 | DX04 | DIO1 | 130 | 2 | 4 | 0 | 3 | 23 |  |  | DI | [9 empty] | 2.4\0.3:23 |  |  |  | S | [6 empty] | F4 | 15 | 16
BBD130 | DX04 | DIO1 | 130 | 2 | 4 | 0 | 3 | 24 |  |  | DI | [9 empty] | 2.4\0.3:24 |  |  |  | S | [6 empty] | F4 | 17 | 18
BBD130 | DX04 | DIO1 | 130 | 2 | 4 | 0 | 3 | 25 |  |  | DI | [9 empty] | 2.4\0.3:25 |  |  |  | S | [6 empty] | F4 | 19 | 20
BBD130 | DX04 | DIO1 | 130 | 2 | 4 | 0 | 3 | 26 |  |  | DI | [9 empty] | 2.4\0.3:26 |  |  |  | S | [6 empty] | F4 | 21 | 22
BBD130 | DX04 | DIO1 | 130 | 2 | 4 | 0 | 3 | 27 |  |  | DI | [9 empty] | 2.4\0.3:27 |  |  |  | S | [6 empty] | F4 | 23 | 24
BBD130 | DX04 | DIO1 | 130 | 2 | 4 | 0 | 3 | 28 |  |  | DI | [9 empty] | 2.4\0.3:28 |  |  |  | S | [6 empty] | F4 | 25 | 26
BBD130 | DX04 | DIO1 | 130 | 2 | 4 | 0 | 3 | 29 |  |  | DI | [9 empty] | 2.4\0.3:29 |  |  |  | S | [6 empty] | F4 | 27 | 28
BBD130 | DX04 | DIO1 | 130 | 2 | 4 | 0 | 3 | 30 |  |  | DI | [9 empty] | 2.4\0.3:30 |  |  |  | S | [6 empty] | F4 | 29 | 30
BBD130 | DX04 | DIO1 | 130 | 2 | 4 | 0 | 3 | 31 |  |  | DI | [9 empty] | 2.4\0.3:31 |  |  |  | S | [6 empty] | F4 | 31 | 32
BBD130 | DX04 | DIO1 | 130 | 2 | 4 | 0 | 4 | 0 | BMXFTB2010 | BMXDDO1602 | DO | 5 | BAF130YA01 | YA01 | ROM BIN APRON FEEDER | Start Up Warning Siren 1 |  |  | BAF130 |  | 2.4\0.4:0 | BR4-2110-E-00095 | 0 |  | S | [6 empty] | F5 | 1 | 2
BBD130 | DX04 | DIO1 | 130 | 2 | 4 | 0 | 4 | 1 |  |  | DO | 5 | BAF130 | SR01 | ROM BIN APRON FEEDER | Hpu Pump 1 Running Relay |  |  | BAF130 |  | 2.4\0.4:1 | BR4-2110-E-00095 | 0 |  | S | [6 empty] | F5 | 3 | 4
BBD130 | DX04 | DIO1 | 130 | 2 | 4 | 0 | 4 | 2 |  |  | DO | 5 | BAF130 | SR02 | ROM BIN APRON FEEDER | Hpu Pump 2 Running Relay |  |  | BAF130 |  | 2.4\0.4:2 | BR4-2110-E-00095 | 0 |  | S | [6 empty] | F5 | 5 | 6
BBD130 | DX04 | DIO1 | 130 | 2 | 4 | 0 | 4 | 3 |  |  | DO | 5 | BAF130 | SR03 | ROM BIN APRON FEEDER | Hpu Stop Interlock |  |  | BAF130 |  | 2.4\0.4:3 | BR4-2110-E-00095 | 0 |  | S | [6 empty] | F5 | 7 | 8
BBD130 | DX04 | DIO1 | 130 | 2 | 4 | 0 | 4 | 4 |  |  | DO | [9 empty] | 2.4\0.4:4 |  |  |  | S | [6 empty] | F5 | 9 | 10
BBD130 | DX04 | DIO1 | 130 | 2 | 4 | 0 | 4 | 5 |  |  | DO | [9 empty] | 2.4\0.4:5 |  |  |  | S | [6 empty] | F5 | 11 | 12
BBD130 | DX04 | DIO1 | 130 | 2 | 4 | 0 | 4 | 6 |  |  | DO | [9 empty] | 2.4\0.4:6 |  |  |  | S | [6 empty] | F5 | 13 | 14
BBD130 | DX04 | DIO1 | 130 | 2 | 4 | 0 | 4 | 7 |  |  | DO | [9 empty] | 2.4\0.4:7 |  |  |  | S | [6 empty] | F5 | 15 | 16
BBD130 | DX04 | DIO1 | 130 | 2 | 4 | 0 | 4 | 8 |  |  | DO | [9 empty] | 2.4\0.4:8 |  |  |  | S | [6 empty] | F5 | 17 | 18
BBD130 | DX04 | DIO1 | 130 | 2 | 4 | 0 | 4 | 9 |  |  | DO | [9 empty] | 2.4\0.4:9 |  |  |  | S | [6 empty] | F5 | 19 | 20
BBD130 | DX04 | DIO1 | 130 | 2 | 4 | 0 | 4 | 10 |  |  | DO | [9 empty] | 2.4\0.4:10 |  |  |  | S | [6 empty] | F5 | 21 | 22
BBD130 | DX04 | DIO1 | 130 | 2 | 4 | 0 | 4 | 11 |  |  | DO | [9 empty] | 2.4\0.4:11 |  |  |  | S | [6 empty] | F5 | 23 | 24
BBD130 | DX04 | DIO1 | 130 | 2 | 4 | 0 | 4 | 12 |  |  | DO | [9 empty] | 2.4\0.4:12 |  |  |  | S | [6 empty] | F5 | 25 | 26
BBD130 | DX04 | DIO1 | 130 | 2 | 4 | 0 | 4 | 13 |  |  | DO | [9 empty] | 2.4\0.4:13 |  |  |  | S | [6 empty] | F5 | 27 | 28
BBD130 | DX04 | DIO1 | 130 | 2 | 4 | 0 | 4 | 14 |  |  | DO | 5 | BVG130YA02 | YA02 | VIBRATING GRIZZLY | Start Up Warning Siren |  |  | BVG130 |  | 2.4\0.4:14 | BR4-2110-E-00095 | 0 |  | S | [6 empty] | F5 | 29 | 30
BBD130 | DX04 | DIO1 | 130 | 2 | 4 | 0 | 4 | 15 |  |  | DO | 5 | BBD130SV13 | SV13 | VIBRATING GRIZZLY | Dust Suppression Solenoid Valve |  |  | BBD130 |  | 2.4\0.4:15 | BR4-2110-E-00095 | 0 |  | S | [6 empty] | F5 | 31 | 32
BBD130 | DX04 | DIO1 | 130 | 2 | 4 | 0 | 5 | 0 | BMXFTB2010 | BMXDDO1602 | DO | 5 | BAF130LU01SV01 | SV01 | ROM BIN APRON FEEDER LUBRICATION UNIT | Oil Pump Solenoid Valve |  |  | BAF130LU01 |  | 2.4\0.5:0 | BR4-2110-E-00095 | 0 |  | S | [6 empty] | F6 | 33 | 34
BBD130 | DX04 | DIO1 | 130 | 2 | 4 | 0 | 5 | 1 |  |  | DO | 5 | BAF130LU01SV02 | SV02 | ROM BIN APRON FEEDER LUBRICATION UNIT | Grease Line 1 Solenoid Valve |  |  | BAF130LU01 |  | 2.4\0.5:1 | BR4-2110-E-00095 | 0 |  | S | [6 empty] | F6 | 35 | 36
BBD130 | DX04 | DIO1 | 130 | 2 | 4 | 0 | 5 | 2 |  |  | DO | 5 | BAF130LU01SV03 | SV03 | ROM BIN APRON FEEDER LUBRICATION UNIT | Grease Line 2 Solenoid Valve |  |  | BAF130LU01 |  | 2.4\0.5:2 | BR4-2110-E-00095 | 0 |  | S | [6 empty] | F6 | 37 | 38
BBD130 | DX04 | DIO1 | 130 | 2 | 4 | 0 | 5 | 3 |  |  | DO | 5 | BAF130LU01SV04 | SV04 | ROM BIN APRON FEEDER LUBRICATION UNIT | Grease Inlet Shut Off Valve |  |  | BAF130LU01 |  | 2.4\0.5:3 | BR4-2110-E-00095 | 0 |  | S | [6 empty] | F6 | 39 | 40
BBD130 | DX04 | DIO1 | 130 | 2 | 4 | 0 | 5 | 4 |  |  | DO | 5 | BAF130LU01YL01 | YL01 | ROM BIN APRON FEEDER LUBRICATION UNIT | Grease End Of Line 1 Cycle Complete |  |  | BAF130LU01 |  | 2.4\0.5:4 | BR4-2110-E-00095 | 0 |  | S | [6 empty] | F6 | 41 | 42
BBD130 | DX04 | DIO1 | 130 | 2 | 4 | 0 | 5 | 5 |  |  | DO | 5 | BAF130LU01YL02 | YL02 | ROM BIN APRON FEEDER LUBRICATION UNIT | Grease End Of Line 2 Cycle Complete |  |  | BAF130LU01 |  | 2.4\0.5:5 | BR4-2110-E-00095 | 0 |  | S | [6 empty] | F6 | 43 | 44
BBD130 | DX04 | DIO1 | 130 | 2 | 4 | 0 | 5 | 6 |  |  | DO | [9 empty] | 2.4\0.5:6 |  |  |  | S | [6 empty] | F6 | 45 | 46
BBD130 | DX04 | DIO1 | 130 | 2 | 4 | 0 | 5 | 7 |  |  | DO | [9 empty] | 2.4\0.5:7 |  |  |  | S | [6 empty] | F6 | 47 | 48
BBD130 | DX04 | DIO1 | 130 | 2 | 4 | 0 | 5 | 8 |  |  | DO | [9 empty] | 2.4\0.5:8 |  |  |  | S | [6 empty] | F3 | 33 | 34
BBD130 | DX04 | DIO1 | 130 | 2 | 4 | 0 | 5 | 9 |  |  | DO | [9 empty] | 2.4\0.5:9 |  |  |  | S | [6 empty] | F3 | 35 | 36
BBD130 | DX04 | DIO1 | 130 | 2 | 4 | 0 | 5 | 10 |  |  | DO | [9 empty] | 2.4\0.5:10 |  |  |  | S | [6 empty] | F3 | 37 | 38
BBD130 | DX04 | DIO1 | 130 | 2 | 4 | 0 | 5 | 11 |  |  | DO | [9 empty] | 2.4\0.5:11 |  |  |  | S | [6 empty] | F3 | 39 | 40
BBD130 | DX04 | DIO1 | 130 | 2 | 4 | 0 | 5 | 12 |  |  | DO | [9 empty] | 2.4\0.5:12 |  |  |  | S | [6 empty] | F3 | 41 | 42
BBD130 | DX04 | DIO1 | 130 | 2 | 4 | 0 | 5 | 13 |  |  | DO | [9 empty] | 2.4\0.5:13 |  |  |  | S | [6 empty] | F3 | 43 | 44
BBD130 | DX04 | DIO1 | 130 | 2 | 4 | 0 | 5 | 14 |  |  | DO | [9 empty] | 2.4\0.5:14 |  |  |  | S | [6 empty] | F3 | 45 | 46
BBD130 | DX04 | DIO1 | 130 | 2 | 4 | 0 | 5 | 15 |  |  | DO | 5 | BSR130DB03 | SR01 |  | Lighting Control Relay | Enable |  | BSR130DB03 |  | 2.4\0.5:15 | BR4-2110-E-00095 | 0 |  | S | [6 empty] | F3 | 47 | 48
BBD130 | DX04 | DIO1 | 130 | 2 | 4 | 0 | 6 | 0 | BMXFTW301S | BMEAHI0812 | AI | 5 | BAF130LU01PT01 | PT01 | ROM BIN APRON FEEDER LUBRICATION UNIT | Grease Line 1 Pressure Transducer |  | PSI | BAF130LU01 | REAL | 2.4\0.6:0 | BR4-2110-E-00096 | 0 |  | S |  | 0 | 5000 | 0 | 5000 | # EU | F4 | 33 | 34
BBD130 | DX04 | DIO1 | 130 | 2 | 4 | 0 | 6 | 1 |  |  | AI | 5 | BAF130LU01PT02 | PT02 | ROM BIN APRON FEEDER LUBRICATION UNIT | Grease Line 2 Pressure Transducer |  | PSI | BAF130LU01 | REAL | 2.4\0.6:1 | BR4-2110-E-00096 | 0 |  | S |  | 0 | 5000 | 0 | 5000 | # EU | F4 | 35 | 36
BBD130 | DX04 | DIO1 | 130 | 2 | 4 | 0 | 6 | 2 |  |  | AI | 5 | BAF130LU01PT03 | PT03 | ROM BIN APRON FEEDER LUBRICATION UNIT | Oil Pressure Transducer |  | PSI | BAF130LU01 | REAL | 2.4\0.6:2 | BR4-2110-E-00096 | 0 |  | S |  | 0 | 500 | 0 | 500 | # EU | F4 | 37 | 38
BBD130 | DX04 | DIO1 | 130 | 2 | 4 | 0 | 6 | 3 |  |  | AI | 5 | BAF130LU01PT04 | PT04 | ROM BIN APRON FEEDER LUBRICATION UNIT | End Of Line 1 Pressure Transducer |  | PSI | BAF130LU01 | REAL | 2.4\0.6:3 | BR4-2110-E-00096 | 0 |  | S |  | 0 | 5000 | 0 | 5000 | # EU | F4 | 39 | 40
BBD130 | DX04 | DIO1 | 130 | 2 | 4 | 0 | 6 | 4 |  |  | AI | 5 | BAF130LU01PT05 | PT05 | ROM BIN APRON FEEDER LUBRICATION UNIT | End Of Line 2 Pressure Transducer |  | PSI | BAF130LU01 | REAL | 2.4\0.6:4 | BR4-2110-E-00096 | 0 |  | S |  | 0 | 5000 | 0 | 5000 | # EU | F4 | 41 | 42
BBD130 | DX04 | DIO1 | 130 | 2 | 4 | 0 | 6 | 5 |  |  | AI | 5 | BAF130LU01LT01 | LT01 | ROM BIN APRON FEEDER LUBRICATION UNIT | Grease Level Transducer |  | % | BAF130LU01 | REAL | 2.4\0.6:5 | BR4-2110-E-00096 | 0 |  | S |  | 0 | 100 | 0 | 100 | # EU | F4 | 43 | 44
BBD130 | DX04 | DIO1 | 130 | 2 | 4 | 0 | 6 | 6 |  |  | AI | 5 | BAF130HP01TT02 | TT02 | ROM BIN APRON FEEDER HPU | Oil Cooler Inlet Temperature |  | C | BAF130 | REAL | 2.4\0.6:6 | BR4-2110-E-00092 | 0 |  | S |  | 0 | 100 | 0 | 100 | # EU | F4 | 45 | 46
BBD130 | DX04 | DIO1 | 130 | 2 | 4 | 0 | 6 | 7 |  |  | AI | 5 | BAF130HP01TT03 | TT03 | ROM BIN APRON FEEDER HPU | Oil Cooler Outlet Temperature |  | C | BAF130 | REAL | 2.4\0.6:7 | BR4-2110-E-00092 | 0 |  | S |  | 0 | 100 | 0 | 100 | # EU | F4 | 47 | 48
BBD130 | DX04 | DIO1 | 130 | 2 | 4 | 0 | 7 | 0 | BMXFTW301S | BMEAHI0812 | AI | 5 | BAF130LT01 | LT01 | ROM BIN APRON FEEDER | Level Indicating Transmitter 1 |  | % | BAF130 | REAL | 2.4\0.7:0 | BR4-2110-E-00096 | 0 |  | S |  | 0 | 100 | 0 | 100 | # EU | F5 | 33 | 34
BBD130 | DX04 | DIO1 | 130 | 2 | 4 | 0 | 7 | 1 |  |  | AI | 5 | BAF130LT02 | LT02 | ROM BIN APRON FEEDER | Level Indicating Transmitter 2 |  | % | BAF130 | REAL | 2.4\0.7:1 | BR4-2110-E-00096 | 0 |  | S |  | 0 | 100 | 0 | 100 | # EU | F5 | 35 | 36
BBD130 | DX04 | DIO1 | 130 | 2 | 4 | 0 | 7 | 2 |  |  | AI | [9 empty] | 2.4\0.7:2 |  |  |  | S | [6 empty] | F5 | 37 | 38
BBD130 | DX04 | DIO1 | 130 | 2 | 4 | 0 | 7 | 3 |  |  | AI | [9 empty] | 2.4\0.7:3 |  |  |  | S | [6 empty] | F5 | 39 | 40
BBD130 | DX04 | DIO1 | 130 | 2 | 4 | 0 | 7 | 4 |  |  | AI | 5 | BBD130FT21 | FT21 | VIBRATING GRIZZLY DUST SUPPRESSION | Flow Transmitter |  | m3/h | BBD130 | REAL | 2.4\0.7:4 | BR4-2110-E-00097 | 0 |  | S |  | 0 | 3.9 | 0 | 3.9 | #.# EU | F5 | 41 | 42
BBD130 | DX04 | DIO1 | 130 | 2 | 4 | 0 | 7 | 5 |  |  | AI | 5 | BAF130HP01FT01 | FT01 | ROM BIN APRON FEEDER HPU | Hydraulic Motor Drain Flow |  | m3/h | BAF130HP01 | REAL | 2.4\0.7:5 | BR4-2110-E-00092 | 0 |  | S |  | 0 |  | 0 |  | #.# EU | F5 | 43 | 44
BBD130 | DX04 | DIO1 | 130 | 2 | 4 | 0 | 7 | 6 |  |  | AI | 5 | BAF130HP01FT02 | FT02 | ROM BIN APRON FEEDER HPU | Pump Group 1 Case Drain Flow |  | m3/h | BAF130HP01 | REAL | 2.4\0.7:6 | BR4-2110-E-00092 | 0 |  | S |  | 0 |  | 0 |  | #.# EU | F5 | 45 | 46
BBD130 | DX04 | DIO1 | 130 | 2 | 4 | 0 | 7 | 7 |  |  | AI | 5 | BAF130HP01FT03 | FT03 | ROM BIN APRON FEEDER HPU | Pump Group 2 Case Drain Flow |  | m3/h | BAF130HP01 | REAL | 2.4\0.7:7 | BR4-2110-E-00092 | 0 |  | S |  | 0 |  | 0 |  | #.# EU | F5 | 47 | 48
BBD130 | DX04 | DIO1 | 130 | 2 | 4 | 0 | 8 | 0 | BMXFTB2010 | BMXEHC0800 | HSCI | 5 | BAF130SS01 | SS01 | ROM BIN APRON FEEDER | Underspeed Pulse |  | SS01 | BAF130 |  | 2.4\0.8:0 | BR4-2110-E-00095 | 0 |  | S | [6 empty] | F2 | 37 | 38
BBD130 | DX04 | DIO1 | 130 | 2 | 4 | 0 | 8 | 1 |  |  | HSCI | 5 | BAF130SS01 | ZQ01 | ROM BIN APRON FEEDER | Distance Pulse |  | SS01 | BAF130 |  | 2.4\0.8:1 | BR4-2110-E-00095 | 0 |  | S | [6 empty] | F2 | 39 | 40
BBD130 | DX04 | DIO1 | 130 | 2 | 4 | 0 | 8 | 2 |  |  | HSCI | 5 | BVG130SS01 | SS01 | VIBRATING GRIZZLY | Underspeed Pulse |  | SS01 | BVG130 |  | 2.4\0.8:2 | BR4-2110-E-00095 | 0 |  | S | [6 empty] | F2 | 41 | 42
BBD130 | DX04 | DIO1 | 130 | 2 | 4 | 0 | 8 | 3 |  |  | HSCI | 5 | BVG130SS01 | ZQ01 | VIBRATING GRIZZLY | Distance Pulse |  | SS01 | BVG130 |  | 2.4\0.8:3 | BR4-2110-E-00095 | 0 |  | S | [6 empty] | F2 | 43 | 44
BBD130 | DX04 | DIO1 | 130 | 2 | 4 | 0 | 8 | 4 |  |  | HSCI | [9 empty] | 2.4\0.8:4 |  |  |  | S | [6 empty] | F2 | 45 | 46
BBD130 | DX04 | DIO1 | 130 | 2 | 4 | 0 | 8 | 5 |  |  | HSCI | [9 empty] | 2.4\0.8:5 |  |  |  | S | [6 empty] | F2 | 47 | 48
BBD130 | DX04 | DIO1 | 130 | 2 | 4 | 0 | 8 | 6 |  |  | HSCI | [9 empty] | 2.4\0.8:6 |  |  |  | S | [6 empty] | F2 | 49 | 50
BBD130 | DX04 | DIO1 | 130 | 2 | 4 | 0 | 8 | 7 |  |  | HSCI | [9 empty] | 2.4\0.8:7 |  |  |  | S | [6 empty] | F2 | 51 | 52
BBD130 | DX04 | DIO1 | 130 | 2 | 4 | 0 | 9 |  |  | BMXX0 | [10 empty] | 2.4\0.9:
BBD130 | DX04 | DIO1 | 130 | 2 | 4 | 0 | 9 | [13 empty] | 2.4\0.9:
BBD130 | DX04 | DIO1 | 130 | 2 | 4 | 0 | 9 | [13 empty] | 2.4\0.9:
BBD130 | DX04 | DIO1 | 130 | 2 | 4 | 0 | 9 | [13 empty] | 2.4\0.9:
BBD130 | DX04 | DIO1 | 130 | 2 | 4 | 0 | 10 |  |  | BMXX0 | [10 empty] | 2.4\0.10:
BBD130 | DX04 | DIO1 | 130 | 2 | 4 | 0 | 10 | [13 empty] | 2.4\0.10:
BBD130 | DX04 | DIO1 | 130 | 2 | 4 | 0 | 10 | [13 empty] | 2.4\0.10:
BBD130 | DX04 | DIO1 | 130 | 2 | 4 | 0 | 10 | [13 empty] | 2.4\0.10:
BBD130 | DX04 | DIO1 | 130 | 2 | 4 | 0 | 11 |  |  | BMXX0 | [10 empty] | 2.4\0.11:
BBD130 | DX04 | DIO1 | 130 | 2 | 4 | 0 | 11 | [13 empty] | 2.4\0.11:
BBD130 | DX04 | DIO1 | 130 | 2 | 4 | 0 | 11 | [13 empty] | 2.4\0.11:
BBD130 | DX04 | DIO1 | 130 | 2 | 4 | 0 | 11 | [13 empty] | 2.4\0.11:
[10 empty] | * |  | 4 | BAF130 |  | ROM BIN APRON FEEDER HPU | ROM Bin Apron Feeder To BSR130DX01 Master Relay |  | SUB LINK | BAF130HP01 |  |  | BR4-2110-E-00174 | 0 | [8 empty] | F7 | 1 | 2 | 3 | 4
[10 empty] | * |  | 4 | BAF130HP01LCS02 | LOS01 | ROM BIN APRON FEEDER HPU COOLING FANS | LOS To Master Relay BSR130DX01 |  | DEVICE | BAF130HP01 |  |  | BR4-2110-E-00174 | 0 | [8 empty] | F7 | 5 | 6 | 7 | 8
[10 empty] | * |  | 4 | BAF130LU01LCS01 | LOS01 | ROM BIN APRON FEEDER LUBRICATION UNIT | Emergency Stop Relay |  | SUB LINK | BAF130PP07 |  |  | BR4-2110-E-00050 | 0 | [8 empty] | F7 | 9 | 10 | 11 | 12
[10 empty] | * |  | 4 | BVG130LCS01 | LOS01 | VIBRATING GRIZZLY | Emergency Stop Relay |  | SUB LINK | BVG130 |  |  | BR4-2110-E-00061 | 0 | [8 empty] | F7 | 13 | 14 | 15 | 16
[10 empty] | PNOZs4 | Safety Relay | 4 | BAF130PWS01 | PWS01 | ROM BIN APRON FEEDER | Pullwire Switch 1 |  | K203 | BAF130 |  |  | BR4-2110-E-00094 | 0 | [8 empty] | F7 | 17 | 18 | 19 | 20
[10 empty] | PNOZs4 | Safety Relay | 4 | BAF130PWS02 | PWS02 | ROM BIN APRON FEEDER | Pullwire Switch 2 |  | K214 | BAF130 |  |  | BR4-2110-E-00094 | 0 | [8 empty] | F7 | 21 | 22 | 23 | 24
[10 empty] | PNOZs4 | Safety Relay | 4 | BAF130LCS01 | LOS01 | ROM BIN APRON FEEDER | Emergency Stop Relay |  | K253 | BAF130 |  |  | BR4-2110-E-00094 | 0 | [8 empty] | F7 | 25 | 26 | 27 | 28
[10 empty] | PNOZs4 | Safety Relay | 4 | BAF130HP01LCS01 | LOS01 | ROM BIN APRON FEEDER HPU | Emergency Stop Relay |  | K271 | BAF130HP01 |  |  | BR4-2110-E-00094 | 0 | [8 empty] | F7 | 29 | 30 | 31 | 32
[32 empty] | F7 | 33 | 34 | 35 | 36
[32 empty] | F7 | 37 | 38 | 39 | 40
[32 empty] | F7 | 41 | 42 | 43 | 44
[32 empty] | F7 | 45 | 46 | 47 | 48
BBD130DX05 - Primary Crusher Building - Primary Crusher
EIO node #5 | DX05 | DIO1 | 130 | 2 | 5 | 0
BBD130 | DX05 | DIO1 | 130 | 2 | 5 | 0 |  | Chassis |  | BMEXBP1200
BBD130 | DX05 | DIO1 | 130 | 2 | 5 | 0 |  | Power |  | BMXCPS4022 |  | total |  | spare |  | % spare
BBD130 | DX05 | DIO1 | 130 | 2 | 5 | 0 | 0 | Comms |  | BMECRA31210 | I/O1 | 112 |  | 61 |  | 54.46%
BBD130 | DX05 | DIO1 | 130 | 2 | 5 | 0 | 1 | 0 | BMXFCW303 | BMXDDI3202K | DI | 4 | BBD130DX05 | CB01 |  | 240VAC Circuit Breaker | Closed | Q106 | BBD130DX05 |  | 2.5\0.1:0 | BR4-2110-E-00098 | 0 |  | D | [6 empty] | F1 |  | 1
BBD130 | DX05 | DIO1 | 130 | 2 | 5 | 0 | 1 | 1 |  |  | DI | 4 | BBD130DX05 | VDC01 |  | 24VDC DIO1 Output Control Supply | Healthy | Q143 | BBD130DX05 |  | 2.5\0.1:1 | BR4-2110-E-00098 | 0 |  | D | [6 empty] | F1 |  | 2
BBD130 | DX05 | DIO1 | 130 | 2 | 5 | 0 | 1 | 2 |  |  | DI | 4 | BBD130DX05 | VDC02 |  | 24VDC GW1 Control Supply | Healthy | Q157 | BBD130DX05 |  | 2.5\0.1:2 | BR4-2110-E-00098 | 0 |  | D | [6 empty] | F1 |  | 3
BBD130 | DX05 | DIO1 | 130 | 2 | 5 | 0 | 1 | 3 |  |  | DI | 4 | BBD130DX05 | VDC03 |  | 24VDC Instrument Supply | Healthy | Q164 | BBD130DX05 |  | 2.5\0.1:3 | BR4-2110-E-00098 | 0 |  | D | [6 empty] | F1 |  | 4
BBD130 | DX05 | DIO1 | 130 | 2 | 5 | 0 | 1 | 4 |  |  | DI | 4 | BBD130DX05 | VDC04 |  | 24VDC Transmitter Supply | Healthy | Q168 | BBD130DX05 |  | 2.5\0.1:4 | BR4-2110-E-00098 | 0 |  | D | [6 empty] | F1 |  | 5
BBD130 | DX05 | DIO1 | 130 | 2 | 5 | 0 | 1 | 5 |  |  | DI | 4 | BBD130DX05 | VDC05 |  | 24VDC BJC130 Control Supply | Healthy | Q172 | BBD130DX05 |  | 2.5\0.1:5 | BR4-2110-E-00098 | 0 |  | D | [6 empty] | F1 |  | 6
BBD130 | DX05 | DIO1 | 130 | 2 | 5 | 0 | 1 | 6 |  |  | DI | 5 | BBD130DX05 | VDC06 |  | 24VDC BRB13x Instrument Control Supply | Healthy | Q176 | BBD130DX05 |  | 2.5\0.1:6 | BR4-2110-E-00098 | 0 |  | D | [6 empty] | F1 |  | 7
BBD130 | DX05 | DIO1 | 130 | 2 | 5 | 0 | 1 | 7 |  |  | DI | 5 | BBD130DX05 | VDC07 |  | 24VDC BJC130ZT01 Gap Setting Control Supply | Healthy | Q180 | BBD130DX05 |  | 2.5\0.1:7 | BR4-2110-E-00098 | 0 |  | D | [6 empty] | F1 |  | 8
BBD130 | DX05 | DIO1 | 130 | 2 | 5 | 0 | 1 | 8 |  |  | DI | 5 | BBD130DX05 | VDC08 |  | 24VDC BJC130HP01 Control Supply | Healthy | Q184 | BBD130DX05 |  | 2.5\0.1:8 | BR4-2110-E-00098 | 0 |  | D | [6 empty] | F1 |  | 9
BBD130 | DX05 | DIO1 | 130 | 2 | 5 | 0 | 1 | 9 |  |  | DI | 5 | BBD130DX05 | VDC09 |  | 24VDC BJC130LU01 Control Supply | Healthy | Q188 | BBD130DX05 |  | 2.5\0.1:9 | BR4-2110-E-00098 | 0 |  | D | [6 empty] | F1 |  | 10
BBD130 | DX05 | DIO1 | 130 | 2 | 5 | 0 | 1 | 10 |  |  | DI | 4 | BBD130DX05 | VDC10 |  | Spare Control Supply | Healthy | Q192 | BBD130DX05 |  | 2.5\0.1:10 | BR4-2110-E-00098 | 0 |  | D | [6 empty] | F1 |  | 11
BBD130 | DX05 | DIO1 | 130 | 2 | 5 | 0 | 1 | 11 |  |  | DI | 4 | BBD130DX05 | VDC11 |  | Spare Control Supply | Healthy | Q196 | BBD130DX05 |  | 2.5\0.1:11 | BR4-2110-E-00098 | 0 |  | D | [6 empty] | F1 |  | 12
BBD130 | DX05 | DIO1 | 130 | 2 | 5 | 0 | 1 | 12 |  |  | DI | [9 empty] | 2.5\0.1:12 |  |  |  | S | [6 empty] | F1 |  | 13
BBD130 | DX05 | DIO1 | 130 | 2 | 5 | 0 | 1 | 13 |  |  | DI | [9 empty] | 2.5\0.1:13 |  |  |  | S | [6 empty] | F1 |  | 14
BBD130 | DX05 | DIO1 | 130 | 2 | 5 | 0 | 1 | 14 |  |  | DI | [9 empty] | 2.5\0.1:14 |  |  |  | S | [6 empty] | F1 |  | 15
BBD130 | DX05 | DIO1 | 130 | 2 | 5 | 0 | 1 | 15 |  |  | DI | [9 empty] | 2.5\0.1:15 |  |  |  | S | [6 empty] | F1 |  | 16
BBD130 | DX05 | DIO1 | 130 | 2 | 5 | 0 | 1 | 16 |  |  | DI | 4 | BJC130LCS01 | STT01 | PRIMARY JAW CRUSHER | Start Pushbutton | Activated | STT01 | BJC130 |  | 2.5\0.1:16 | BR4-2110-E-00099 | 0 |  | S | [6 empty] | F1 | 17 | 18
BBD130 | DX05 | DIO1 | 130 | 2 | 5 | 0 | 1 | 17 |  |  | DI | 4 | BJC130LCS01 | STP01 | PRIMARY JAW CRUSHER | Stop Pushbutton | Activated | STP01 | BJC130 |  | 2.5\0.1:17 | BR4-2110-E-00099 | 0 |  | S | [6 empty] | F1 | 19 | 20
BBD130 | DX05 | DIO1 | 130 | 2 | 5 | 0 | 1 | 18 |  |  | DI | 4 | BJC130LCS01 | SY01 | PRIMARY JAW CRUSHER | Emergency Stop Relay | Healthy | K202 | BJC130 |  | 2.5\0.1:18 | BR4-2110-E-00099 | 0 |  | D | [6 empty] | F1 | 21 | 22
BBD130 | DX05 | DIO1 | 130 | 2 | 5 | 0 | 1 | 19 |  |  | DI | 4 | BJC130LCS02 | STT01 | PRIMARY JAW CRUSHER | Start Pushbutton | Activated | STT01 | BJC130 |  | 2.5\0.1:19 | BR4-2110-E-00099 | 0 |  | S | [6 empty] | F1 | 23 | 24
BBD130 | DX05 | DIO1 | 130 | 2 | 5 | 0 | 1 | 20 |  |  | DI | 4 | BJC130LCS02 | STP01 | PRIMARY JAW CRUSHER | Stop Pushbutton | Activated | STP01 | BJC130 |  | 2.5\0.1:20 | BR4-2110-E-00099 | 0 |  | S | [6 empty] | F1 | 25 | 26
BBD130 | DX05 | DIO1 | 130 | 2 | 5 | 0 | 1 | 21 |  |  | DI | 4 | BJC130LCS02 | SY01 | PRIMARY JAW CRUSHER | Emergency Stop Relay | Healthy | K218 | BJC130 |  | 2.5\0.1:21 | BR4-2110-E-00099 | 0 |  | D | [6 empty] | F1 | 27 | 28
BBD130 | DX05 | DIO1 | 130 | 2 | 5 | 0 | 1 | 22 |  |  | DI | [13 empty] | S | [6 empty] | F1 | 29 | 30
BBD130 | DX05 | DIO1 | 130 | 2 | 5 | 0 | 1 | 23 |  |  | DI | 4 | BJC130CH02BCS01 | BCS01 | PRIMARY JAW CRUSHER DISCHARGE CHUTE | Blocked Chute Switch 1 | Healthy |  | BJC130 |  | 2.5\0.1:23 | BR4-2110-E-00102 | 0 |  | S | [6 empty] | F1 | 31 | 32
BBD130 | DX05 | DIO1 | 130 | 2 | 5 | 0 | 1 | 24 |  |  | DI | 5 | BJC130 | THR01 | PRIMARY JAW CRUSHER | Thermistor | Healthy | K293 | BJC130 |  | 2.5\0.1:24 | BR4-2110-E-00099 | 1 |  | S | [6 empty] | F1 | 33 | 34
BBD130 | DX05 | DIO1 | 130 | 2 | 5 | 0 | 1 | 25 |  |  | DI | [9 empty] | 2.5\0.1:25 |  |  |  | S | [6 empty] | F1 | 35 | 36
BBD130 | DX05 | DIO1 | 130 | 2 | 5 | 0 | 1 | 26 |  |  | DI | [9 empty] | 2.5\0.1:26 |  |  |  | S | [6 empty] | F1 | 37 | 38
BBD130 | DX05 | DIO1 | 130 | 2 | 5 | 0 | 1 | 27 |  |  | DI | [9 empty] | 2.5\0.1:27 |  |  |  | S | [6 empty] | F1 | 39 | 40
BBD130 | DX05 | DIO1 | 130 | 2 | 5 | 0 | 1 | 28 |  |  | DI | [9 empty] | 2.5\0.1:28 |  |  |  | S | [6 empty] | F1 | 41 | 42
BBD130 | DX05 | DIO1 | 130 | 2 | 5 | 0 | 1 | 29 |  |  | DI | [9 empty] | 2.5\0.1:29 |  |  |  | S | [6 empty] | F1 | 43 | 44
BBD130 | DX05 | DIO1 | 130 | 2 | 5 | 0 | 1 | 30 |  |  | DI | 4 | BRB13xLCS03 | SY03 | ROM BIN AND PRIMARY CRUSHER ROCKBREAKERS | Emergency Shutdown 3 | Healthy | K253-1 | BRB13x |  | 2.5\0.1:30 | BR4-2110-E-00099 | 0 |  | D | [6 empty] | F1 | 45 | 46
BBD130 | DX05 | DIO1 | 130 | 2 | 5 | 0 | 1 | 31 |  |  | DI | 4 | BRB13xLCS04 | SY04 | ROM BIN AND PRIMARY CRUSHER ROCKBREAKERS | Emergency Shutdown 4 | Healthy | K266-1 | BRB13x |  | 2.5\0.1:31 | BR4-2110-E-00099 | 0 |  | D | [6 empty] | F1 | 47 | 48
BBD130 | DX05 | DIO1 | 130 | 2 | 5 | 0 | 2 | 0 | BMXFCW303 | BMXDDI3202K | DI | 5 | BJC130HP01PN01 | SW01 | PRIMARY JAW CRUSHER HPU | Main Switch | Closed | Q1 | BJC130HP01 |  | 2.5\0.2:0 | BR4-2110-E-00100 | 0 |  | S | [6 empty] | F2 | 1 | 2
BBD130 | DX05 | DIO1 | 130 | 2 | 5 | 0 | 2 | 1 |  |  | DI | 5 | BJC130HP01PN01 | CAX01 | PRIMARY JAW CRUSHER HPU | HPU Pump | Running | Q9 | BJC130HP01 |  | 2.5\0.2:1 | BR4-2110-E-00100 | 0 |  | S | [6 empty] | F2 | 3 | 4
BBD130 | DX05 | DIO1 | 130 | 2 | 5 | 0 | 2 | 2 |  |  | DI | 5 | BJC130HP01PN01 | SY01 | PRIMARY JAW CRUSHER HPU | Emergency Stop Relay | Healthy | K234 | BJC130HP01 |  | 2.5\0.2:2 | BR4-2110-E-00100 | 0 |  | S | [6 empty] | F2 | 5 | 6
BBD130 | DX05 | DIO1 | 130 | 2 | 5 | 0 | 2 | 3 |  |  | DI | 5 | BJC130HP01PN01 | XS01 | PRIMARY JAW CRUSHER HPU | Setting Lightening | Activated | XS01 | BJC130HP01 |  | 2.5\0.2:3 | BR4-2110-E-00100 | 0 |  | S | [6 empty] | F2 | 7 | 8
BBD130 | DX05 | DIO1 | 130 | 2 | 5 | 0 | 2 | 4 |  |  | DI | 5 | BJC130HP01PN01 | PIT01 | PRIMARY JAW CRUSHER HPU | Toggle Cylinder Pressure | Low | PIT01 | BJC130HP01 |  | 2.5\0.2:4 | BR4-2110-E-00100 | 1 |  | S | [6 empty] | F2 | 9 | 10
BBD130 | DX05 | DIO1 | 130 | 2 | 5 | 0 | 2 | 5 |  |  | DI | 4 | BJC130HP01PDSH01 | PDSH01 | PRIMARY JAW CRUSHER HPU | Oil Return Filter | Blocked |  | BJC130HP01 |  | 2.5\0.2:5 | BR4-2110-E-00100 | 0 |  | S | [6 empty] | F2 | 11 | 12
BBD130 | DX05 | DIO1 | 130 | 2 | 5 | 0 | 2 | 6 |  |  | DI | 4 | BJC130HP01UE01 | LS01 | PRIMARY JAW CRUSHER HPU | Oil Tank Level | Low |  | BJC130HP01 |  | 2.5\0.2:6 | BR4-2110-E-00100 | 0 |  | S | [6 empty] | F2 | 13 | 14
BBD130 | DX05 | DIO1 | 130 | 2 | 5 | 0 | 2 | 7 |  |  | DI | 4 | BJC130HP01UE01 | TS01 | PRIMARY JAW CRUSHER HPU | Oil Tank Temperature | Healthy |  | BJC130HP01 |  | 2.5\0.2:7 | BR4-2110-E-00100 | 0 |  | S | [6 empty] | F2 | 15 | 16
BBD130 | DX05 | DIO1 | 130 | 2 | 5 | 0 | 2 | 8 |  |  | DI | 4 | BJC130HP01PS01 | PS01 | PRIMARY JAW CRUSHER HPU | Pressure Switch Clamping Low Limit | Healthy |  | BJC130HP01 |  | 2.5\0.2:8 | BR4-2110-E-00100 | 0 |  | S | [6 empty] | F2 | 17 | 18
BBD130 | DX05 | DIO1 | 130 | 2 | 5 | 0 | 2 | 9 |  |  | DI | 5 | BJC130ZS01 | ZS01 | PRIMARY JAW CRUSHER HPU | Toggle Plate Switch | Healthy |  | BJC130 |  | 2.5\0.2:9 | BR4-2110-E-00100 | 0 |  | S | [6 empty] | F2 | 19 | 20
BBD130 | DX05 | DIO1 | 130 | 2 | 5 | 0 | 2 | 10 |  |  | DI | [9 empty] | 2.5\0.2:10 |  |  |  | S | [6 empty] | F2 | 21 | 22
BBD130 | DX05 | DIO1 | 130 | 2 | 5 | 0 | 2 | 11 |  |  | DI | [9 empty] | 2.5\0.2:11 |  |  |  | S | [6 empty] | F2 | 23 | 24
BBD130 | DX05 | DIO1 | 130 | 2 | 5 | 0 | 2 | 12 |  |  | DI | [9 empty] | 2.5\0.2:12 |  |  |  | S | [6 empty] | F2 | 25 | 26
BBD130 | DX05 | DIO1 | 130 | 2 | 5 | 0 | 2 | 13 |  |  | DI | [9 empty] | 2.5\0.2:13 |  |  |  | S | [6 empty] | F2 | 27 | 28
BBD130 | DX05 | DIO1 | 130 | 2 | 5 | 0 | 2 | 14 |  |  | DI | [9 empty] | 2.5\0.2:14 |  |  |  | S | [6 empty] | F2 | 29 | 30
BBD130 | DX05 | DIO1 | 130 | 2 | 5 | 0 | 2 | 15 |  |  | DI | [9 empty] | 2.5\0.2:15 |  |  |  | S | [6 empty] | F2 | 31 | 32
BBD130 | DX05 | DIO1 | 130 | 2 | 5 | 0 | 2 | 16 |  |  | DI | [9 empty] | 2.5\0.2:16 |  |  |  | S | [6 empty] | F3 | 1 | 2
BBD130 | DX05 | DIO1 | 130 | 2 | 5 | 0 | 2 | 17 |  |  | DI | [9 empty] | 2.5\0.2:17 |  |  |  | S | [6 empty] | F3 | 3 | 4
BBD130 | DX05 | DIO1 | 130 | 2 | 5 | 0 | 2 | 18 |  |  | DI | [9 empty] | 2.5\0.2:18 |  |  |  | S | [6 empty] | F3 | 5 | 6
BBD130 | DX05 | DIO1 | 130 | 2 | 5 | 0 | 2 | 19 |  |  | DI | [9 empty] | 2.5\0.2:19 |  |  |  | S | [6 empty] | F3 | 7 | 8
BBD130 | DX05 | DIO1 | 130 | 2 | 5 | 0 | 2 | 20 |  |  | DI | [9 empty] | 2.5\0.2:20 |  |  |  | S | [6 empty] | F3 | 9 | 10
BBD130 | DX05 | DIO1 | 130 | 2 | 5 | 0 | 2 | 21 |  |  | DI | 4 | BJC130LU01LCS01 | STT01 | PRIMARY JAW CRUSHER LUBRICATION UNIT | Start Pushbutton | Activated | STT01 | BJC130LU01 |  | 2.5\0.2:21 | BR4-2110-E-00067 | 0 |  | S | [6 empty] | F3 | 11 | 12
BBD130 | DX05 | DIO1 | 130 | 2 | 5 | 0 | 2 | 22 |  |  | DI | 4 | BJC130LU01LCS01 | STP01 | PRIMARY JAW CRUSHER LUBRICATION UNIT | Stop Pushbutton | Activated | STP01 | BJC130LU01 |  | 2.5\0.2:22 | BR4-2110-E-00067 | 0 |  | S | [6 empty] | F3 | 13 | 14
BBD130 | DX05 | DIO1 | 130 | 2 | 5 | 0 | 2 | 23 |  |  | DI | [9 empty] | 2.5\0.2:23 |  |  |  | S | [6 empty] | F3 | 15 | 16
BBD130 | DX05 | DIO1 | 130 | 2 | 5 | 0 | 2 | 24 |  |  | DI | 4 | BJC130LU01ZS01 | ZS01 | PRIMARY JAW CRUSHER LUBRICATION UNIT | Grease End Of Line 1,2 | Cycled |  | BJC130LU01 |  | 2.5\0.2:24 | BR4-2110-E-00100 | 0 |  | S | [6 empty] | F3 | 17 | 18
BBD130 | DX05 | DIO1 | 130 | 2 | 5 | 0 | 2 | 25 |  |  | DI | 4 | BJC130LU01ZS02 | ZS02 | PRIMARY JAW CRUSHER LUBRICATION UNIT | Grease End Of Line 3,4 | Cycled |  | BJC130LU01 |  | 2.5\0.2:25 | BR4-2110-E-00100 | 0 |  | S | [6 empty] | F3 | 19 | 20
BBD130 | DX05 | DIO1 | 130 | 2 | 5 | 0 | 2 | 26 |  |  | DI | 4 | BJC130LU01ZS03 | ZS03 | PRIMARY JAW CRUSHER LUBRICATION UNIT | Grease End Of Line 5,6 | Cycled |  | BJC130LU01 |  | 2.5\0.2:26 | BR4-2110-E-00100 | 0 |  | S | [6 empty] | F3 | 21 | 22
BBD130 | DX05 | DIO1 | 130 | 2 | 5 | 0 | 2 | 27 |  |  | DI | 4 | BJC130LU01ZS04 | ZS04 | PRIMARY JAW CRUSHER LUBRICATION UNIT | Grease End Of Line 7,8 | Cycled |  | BJC130LU01 |  | 2.5\0.2:27 | BR4-2110-E-00100 | 0 |  | S | [6 empty] | F3 | 23 | 24
BBD130 | DX05 | DIO1 | 130 | 2 | 5 | 0 | 2 | 28 |  |  | DI | 4 | BJC130LU01ZS05 | ZS05 | PRIMARY JAW CRUSHER LUBRICATION UNIT | Grease End Of Line 9,10 | Cycled |  | BJC130LU01 |  | 2.5\0.2:28 | BR4-2110-E-00100 | 0 |  | S | [6 empty] | F3 | 25 | 26
BBD130 | DX05 | DIO1 | 130 | 2 | 5 | 0 | 2 | 29 |  |  | DI | 4 | BJC130LU01LS01 | LS01 | PRIMARY JAW CRUSHER LUBRICATION UNIT | Oil Level | Low |  | BJC130LU01 |  | 2.5\0.2:29 | BR4-2110-E-00100 | 0 |  | S | [6 empty] | F3 | 27 | 28
BBD130 | DX05 | DIO1 | 130 | 2 | 5 | 0 | 2 | 30 |  |  | DI | 4 | BJC130LU01PS01 | PS01 | PRIMARY JAW CRUSHER LUBRICATION UNIT | Inlet Filter | Blocked |  | BJC130LU01 |  | 2.5\0.2:30 | BR4-2110-E-00100 | 0 |  | S | [6 empty] | F3 | 29 | 30
BBD130 | DX05 | DIO1 | 130 | 2 | 5 | 0 | 2 | 31 |  |  | DI | 4 | BJC130LU01PS02 | PS02 | PRIMARY JAW CRUSHER LUBRICATION UNIT | Outlet Filter | Blocked |  | BJC130LU01 |  | 2.5\0.2:31 | BR4-2110-E-00100 | 0 |  | S | [6 empty] | F3 | 31 | 32
BBD130 | DX05 | DIO1 | 130 | 2 | 5 | 0 | 3 | 0 | BMXFTB2010 | BMXDDO1602 | DO | 4 | BJC130YA01 | YA01 | PRIMARY JAW CRUSHER | Start Up Warning Siren |  |  | BJC130 |  | 2.5\0.3:0 | BR4-2110-E-00100 | 0 |  | S | [6 empty] | F5 | 1 | 2
BBD130 | DX05 | DIO1 | 130 | 2 | 5 | 0 | 3 | 1 |  |  | DO | [9 empty] | 2.5\0.3:1 |  |  |  | S | [6 empty] | F5 | 3 | 4
BBD130 | DX05 | DIO1 | 130 | 2 | 5 | 0 | 3 | 2 |  |  | DO | [9 empty] | 2.5\0.3:2 |  |  |  | S | [6 empty] | F5 | 5 | 6
BBD130 | DX05 | DIO1 | 130 | 2 | 5 | 0 | 3 | 3 |  |  | DO | [9 empty] | 2.5\0.3:3 |  |  |  | S | [6 empty] | F5 | 7 | 8
BBD130 | DX05 | DIO1 | 130 | 2 | 5 | 0 | 3 | 4 |  |  | DO | 4 | BJC130HP01PN01 | K343 | PRIMARY JAW CRUSHER HPU | Setting Increase |  | K343 | BJC130HP01 |  | 2.5\0.3:4 | BR4-2110-E-00100 | 0 |  | S | [6 empty] | F5 | 9 | 10
BBD130 | DX05 | DIO1 | 130 | 2 | 5 | 0 | 3 | 5 |  |  | DO | 4 | BJC130HP01PN01 | K345 | PRIMARY JAW CRUSHER HPU | Setting Mode |  | K345 | BJC130HP01 |  | 2.5\0.3:5 | BR4-2110-E-00100 | 0 |  | S | [6 empty] | F5 | 11 | 12
BBD130 | DX05 | DIO1 | 130 | 2 | 5 | 0 | 3 | 6 |  |  | DO | 4 | BJC130HP01PN01 | K347 | PRIMARY JAW CRUSHER HPU | Crusher Running |  | K347 | BJC130HP01 |  | 2.5\0.3:6 | BR4-2110-E-00100 | 0 |  | S | [6 empty] | F5 | 13 | 14
BBD130 | DX05 | DIO1 | 130 | 2 | 5 | 0 | 3 | 7 |  |  | DO | 4 | BJC130HP01PN01 | K349 | PRIMARY JAW CRUSHER HPU | Setting Decrease |  | K349 | BJC130HP01 |  | 2.5\0.3:7 | BR4-2110-E-00100 | 0 |  | S | [6 empty] | F5 | 15 | 16
BBD130 | DX05 | DIO1 | 130 | 2 | 5 | 0 | 3 | 8 |  |  | DO | [9 empty] | 2.5\0.3:8 |  |  |  | S | [6 empty] | F5 | 17 | 18
BBD130 | DX05 | DIO1 | 130 | 2 | 5 | 0 | 3 | 9 |  |  | DO | [9 empty] | 2.5\0.3:9 |  |  |  | S | [6 empty] | F5 | 19 | 20
BBD130 | DX05 | DIO1 | 130 | 2 | 5 | 0 | 3 | 10 |  |  | DO | [9 empty] | 2.5\0.3:10 |  |  |  | S | [6 empty] | F5 | 21 | 22
BBD130 | DX05 | DIO1 | 130 | 2 | 5 | 0 | 3 | 11 |  |  | DO | 4 | BJC130LU01SV01 | SV01 | PRIMARY JAW CRUSHER LUBRICATION UNIT | Pump Solenoid Valve |  | K395 | BJC130LU01 |  | 2.5\0.3:11 | BR4-2110-E-00100 | 0 |  | S | [6 empty] | F5 | 23 | 24
BBD130 | DX05 | DIO1 | 130 | 2 | 5 | 0 | 3 | 12 |  |  | DO | 4 | BJC130LU01SV02 | SV02 | PRIMARY JAW CRUSHER LUBRICATION UNIT | Grease Line 1 Solenoid Valve |  | K397 | BJC130LU01 |  | 2.5\0.3:12 | BR4-2110-E-00100 | 0 |  | S | [6 empty] | F5 | 25 | 26
BBD130 | DX05 | DIO1 | 130 | 2 | 5 | 0 | 3 | 13 |  |  | DO | 4 | BJC130LU01SV03 | SV03 | PRIMARY JAW CRUSHER LUBRICATION UNIT | Grease Line 2 Solenoid Valve |  | K399 | BJC130LU01 |  | 2.5\0.3:13 | BR4-2110-E-00100 | 0 |  | S | [6 empty] | F5 | 27 | 28
BBD130 | DX05 | DIO1 | 130 | 2 | 5 | 0 | 3 | 14 |  |  | DO | 4 | BJC130LU01YL01 | YL01 | PRIMARY JAW CRUSHER LUBRICATION UNIT | End Of Line 1 Cycle Complete Indicator Light |  |  | BJC130LU01 |  | 2.5\0.3:14 | BR4-2110-E-00100 | 0 |  | S | [6 empty] | F5 | 29 | 30
BBD130 | DX05 | DIO1 | 130 | 2 | 5 | 0 | 3 | 15 |  |  | DO | 4 | BJC130LU01YL02 | YL02 | PRIMARY JAW CRUSHER LUBRICATION UNIT | End Of Line 2 Cycle Complete Indicator Light |  |  | BJC130LU01 |  | 2.5\0.3:15 | BR4-2110-E-00100 | 0 |  | S | [6 empty] | F5 | 31 | 32
BBD130 | DX05 | DIO1 | 130 | 2 | 5 | 0 | 4 | 0 | BMXFTW301S | BMEAHI0812 | AI | 4 | BJC130LT01 | LT01 | PRIMARY JAW CRUSHER | Chute Level |  | % | BJC130 | REAL | 2.5\0.4:0 | BR4-2110-E-00102 | 0 |  | S |  | 0 | 100 | 0 | 100 | #.# EU | F5 | 33 | 34
BBD130 | DX05 | DIO1 | 130 | 2 | 5 | 0 | 4 | 1 |  |  | AI | 4 | BJC130ZT01 | ZT01 | PRIMARY JAW CRUSHER | Gap Setting Measurement |  | mm | BJC130 | REAL | 2.5\0.4:1 | BR4-2110-E-00101 | 0 |  | S |  | 0 | 200 | 0 | 200 | # EU | F5 | 35 | 36
BBD130 | DX05 | DIO1 | 130 | 2 | 5 | 0 | 4 | 2 |  |  | AI | 5 | BBD130PT20 | PT20 | PRIMARY CRUSHING BUILDING | Pressure Transmitter |  | kPa | BBD130 | REAL | 2.5\0.4:2 | BR4-2110-E-00101 | 1 |  | S |  | 0 | 1600 | 0 | 1600 | #.# EU | F5 | 37 | 38
BBD130 | DX05 | DIO1 | 130 | 2 | 5 | 0 | 4 | 3 |  |  | AI | 5 | BJC130HP01TT01 | TT01 | PRIMARY JAW CRUSHER HPU | TEMPERATURE TRANSMITTER |  | C | BJC130HP01 | REAL | 2.5\0.4:3 | BR4-2110-E-00101 | 1 |  | S | [6 empty] | F5 | 39 | 40
BBD130 | DX05 | DIO1 | 130 | 2 | 5 | 0 | 4 | 4 |  |  | AI | [9 empty] | 2.5\0.4:4 |  |  |  | S | [6 empty] | F5 | 41 | 42
BBD130 | DX05 | DIO1 | 130 | 2 | 5 | 0 | 4 | 5 |  |  | AI | [9 empty] | 2.5\0.4:5 |  |  |  | S | [6 empty] | F5 | 43 | 44
BBD130 | DX05 | DIO1 | 130 | 2 | 5 | 0 | 4 | 6 |  |  | AI | [9 empty] | 2.5\0.4:6 |  |  |  | S | [6 empty] | F5 | 45 | 46
BBD130 | DX05 | DIO1 | 130 | 2 | 5 | 0 | 4 | 7 |  |  | AI | [9 empty] | 2.5\0.4:7 |  |  |  | S | [6 empty] | F5 | 47 | 48
BBD130 | DX05 | DIO1 | 130 | 2 | 5 | 0 | 5 | 0 | BMXFTW301S | BMEAHI0812 | AI | 4 | BJC130LU01PT01 | PT01 | PRIMARY JAW CRUSHER LUBRICATION UNIT | Grease Line 1 Start Of Line Pressure |  | PSI | BJC130LU01 | REAL | 2.5\0.5:0 | BR4-2110-E-00101 | 0 |  | S |  | 0 | 5000 | 0 | 5000 | # EU | F3 | 33 | 34
BBD130 | DX05 | DIO1 | 130 | 2 | 5 | 0 | 5 | 1 |  |  | AI | 4 | BJC130LU01PT02 | PT02 | PRIMARY JAW CRUSHER LUBRICATION UNIT | Grease Line 2 Start Of Line Pressure |  | PSI | BJC130LU01 | REAL | 2.5\0.5:1 | BR4-2110-E-00101 | 0 |  | S |  | 0 | 5000 | 0 | 5000 | # EU | F3 | 35 | 36
BBD130 | DX05 | DIO1 | 130 | 2 | 5 | 0 | 5 | 2 |  |  | AI | 4 | BJC130LU01PT03 | PT03 | PRIMARY JAW CRUSHER LUBRICATION UNIT | Oil Pressure |  | PSI | BJC130LU01 | REAL | 2.5\0.5:2 | BR4-2110-E-00101 | 0 |  | S |  | 0 | 500 | 0 | 500 | # EU | F3 | 37 | 38
BBD130 | DX05 | DIO1 | 130 | 2 | 5 | 0 | 5 | 3 |  |  | AI | 4 | BJC130LU01PT04 | PT04 | PRIMARY JAW CRUSHER LUBRICATION UNIT | Grease Line 1 End Of Line Pressure |  | PSI | BJC130LU01 | REAL | 2.5\0.5:3 | BR4-2110-E-00101 | 0 |  | S |  | 0 | 5000 | 0 | 5000 | # EU | F3 | 39 | 40
BBD130 | DX05 | DIO1 | 130 | 2 | 5 | 0 | 5 | 4 |  |  | AI | 4 | BJC130LU01PT05 | PT05 | PRIMARY JAW CRUSHER LUBRICATION UNIT | Grease Line 2 End Of Line Pressure |  | PSI | BJC130LU01 | REAL | 2.5\0.5:4 | BR4-2110-E-00101 | 0 |  | S |  | 0 | 5000 | 0 | 5000 | # EU | F3 | 41 | 42
BBD130 | DX05 | DIO1 | 130 | 2 | 5 | 0 | 5 | 5 |  |  | AI | 4 | BJC130LU01LT01 | LT01 | PRIMARY JAW CRUSHER LUBRICATION UNIT | Grease Level |  | % | BJC130LU01 | REAL | 2.5\0.5:5 | BR4-2110-E-00101 | 0 |  | S |  | 0 | 100 | 0 | 100 | #.# EU | F3 | 43 | 44
BBD130 | DX05 | DIO1 | 130 | 2 | 5 | 0 | 5 | 6 |  |  | AI | [9 empty] | 2.5\0.5:6 |  |  |  | S | [6 empty] | F3 | 45 | 46
BBD130 | DX05 | DIO1 | 130 | 2 | 5 | 0 | 5 | 7 |  |  | AI | [9 empty] | 2.5\0.5:7 |  |  |  | S | [6 empty] | F3 | 47 | 48
BBD130 | DX05 | DIO1 | 130 | 2 | 5 | 0 | 6 | 0 | BMXFCW301S | BMXART0814 | RTDI | 4 | BJC130TT01 | TT01 | PRIMARY JAW CRUSHER | Frame Left Bearing Temperature |  | C | BJC130 | REAL | 2.5\0.6:0 | BR4-2110-E-00102 | 0 |  | S |  | 0 | 200 | 0 | 200 | # EU | F6 | 1 | 2
BBD130 | DX05 | DIO1 | 130 | 2 | 5 | 0 | 6 | 1 | BMXFCW301S |  | RTDI | 4 | BJC130TT02 | TT02 | PRIMARY JAW CRUSHER | Frame Right Bearing Temperature |  | C | BJC130 | REAL | 2.5\0.6:1 | BR4-2110-E-00102 | 0 |  | S |  | 0 | 200 | 0 | 200 | # EU | F6 | 3 | 4
BBD130 | DX05 | DIO1 | 130 | 2 | 5 | 0 | 6 | 2 |  |  | RTDI | 4 | BJC130TT03 | TT03 | PRIMARY JAW CRUSHER | Pitman Left Bearing Temperature |  | C | BJC130 | REAL | 2.5\0.6:2 | BR4-2110-E-00102 | 0 |  | S |  | 0 | 200 | 0 | 200 | # EU | F6 | 5 | 6
BBD130 | DX05 | DIO1 | 130 | 2 | 5 | 0 | 6 | 3 |  |  | RTDI | 4 | BJC130TT04 | TT04 | PRIMARY JAW CRUSHER | Pitman Right Bearing Temperature |  | C | BJC130 | REAL | 2.5\0.6:3 | BR4-2110-E-00102 | 0 |  | S |  | 0 | 200 | 0 | 200 | # EU | F6 | 7 | 8
BBD130 | DX05 | DIO1 | 130 | 2 | 5 | 0 | 6 | 4 |  |  | RTDI | [9 empty] | 2.5\0.6:4 |  |  |  | S | [6 empty] | F6 | 9 | 10
BBD130 | DX05 | DIO1 | 130 | 2 | 5 | 0 | 6 | 5 |  |  | RTDI | [9 empty] | 2.5\0.6:5 |  |  |  | S | [6 empty] | F6 | 11 | 12
BBD130 | DX05 | DIO1 | 130 | 2 | 5 | 0 | 6 | 6 |  |  | RTDI | [9 empty] | 2.5\0.6:6 |  |  |  | S | [6 empty] | F6 | 13 | 14
BBD130 | DX05 | DIO1 | 130 | 2 | 5 | 0 | 6 | 7 |  |  | RTDI | [9 empty] | 2.5\0.6:7 |  |  |  | S | [6 empty] | F6 | 15 | 16
BBD130 | DX05 | DIO1 | 130 | 2 | 5 | 0 | 7 | 0 | BMXFTB2010 | BMXEHC0800 | HSCI | 4 | BJC130SS01 | SS01 | PRIMARY JAW CRUSHER | Underspeed Pulse |  |  | BJC130 |  | 2.5\0.7:0 | BR4-2110-E-00099 | 0 |  | S | [6 empty] | F2 | 33 | 34
BBD130 | DX05 | DIO1 | 130 | 2 | 5 | 0 | 7 | 1 |  |  | HSCI | [9 empty] | 2.5\0.7:1 |  |  |  | S | [6 empty] | F2 | 35 | 36
BBD130 | DX05 | DIO1 | 130 | 2 | 5 | 0 | 7 | 2 |  |  | HSCI | [9 empty] | 2.5\0.7:2 |  |  |  | S | [6 empty] | F2 | 37 | 38
BBD130 | DX05 | DIO1 | 130 | 2 | 5 | 0 | 7 | 3 |  |  | HSCI | [9 empty] | 2.5\0.7:3 |  |  |  | S | [6 empty] | F2 | 39 | 40
BBD130 | DX05 | DIO1 | 130 | 2 | 5 | 0 | 7 | 4 |  |  | HSCI | [9 empty] | 2.5\0.7:4 |  |  |  | S | [6 empty] | F2 | 41 | 42
BBD130 | DX05 | DIO1 | 130 | 2 | 5 | 0 | 7 | 5 |  |  | HSCI | [9 empty] | 2.5\0.7:5 |  |  |  | S | [6 empty] | F2 | 43 | 44
BBD130 | DX05 | DIO1 | 130 | 2 | 5 | 0 | 7 | 6 |  |  | HSCI | [9 empty] | 2.5\0.7:6 |  |  |  | S | [6 empty] | F2 | 45 | 46
BBD130 | DX05 | DIO1 | 130 | 2 | 5 | 0 | 7 | 7 |  |  | HSCI | [9 empty] | 2.5\0.7:7 |  |  |  | S | [6 empty] | F2 | 47 | 48
BBD130 | DX05 | DIO1 | 130 | 2 | 5 | 0 | 8 |  |  | BMXX0 | [10 empty] | 2.5\0.8:
BBD130 | DX05 | DIO1 | 130 | 2 | 5 | 0 | 8 | [13 empty] | 2.5\0.8:
BBD130 | DX05 | DIO1 | 130 | 2 | 5 | 0 | 8 | [13 empty] | 2.5\0.8:
BBD130 | DX05 | DIO1 | 130 | 2 | 5 | 0 | 8 | [13 empty] | 2.5\0.8:
BBD130 | DX05 | DIO1 | 130 | 2 | 5 | 0 | 9 |  |  | BMXX0 | [10 empty] | 2.5\0.9:
BBD130 | DX05 | DIO1 | 130 | 2 | 5 | 0 | 9 | [13 empty] | 2.5\0.9:
BBD130 | DX05 | DIO1 | 130 | 2 | 5 | 0 | 9 | [13 empty] | 2.5\0.9:
BBD130 | DX05 | DIO1 | 130 | 2 | 5 | 0 | 9 | [13 empty] | 2.5\0.9:
BBD130 | DX05 | DIO1 | 130 | 2 | 5 | 0 | 10 |  |  | BMXX0 | [10 empty] | 2.5\0.10:
BBD130 | DX05 | DIO1 | 130 | 2 | 5 | 0 | 10 | [13 empty] | 2.5\0.10:
BBD130 | DX05 | DIO1 | 130 | 2 | 5 | 0 | 10 | [13 empty] | 2.5\0.10:
BBD130 | DX05 | DIO1 | 130 | 2 | 5 | 0 | 10 | [13 empty] | 2.5\0.10:
BBD130 | DX05 | DIO1 | 130 | 2 | 5 | 0 | 11 |  |  | BMXX0 | [10 empty] | 2.5\0.11:
BBD130 | DX05 | DIO1 | 130 | 2 | 5 | 0 | 11 | [13 empty] | 2.5\0.11:
BBD130 | DX05 | DIO1 | 130 | 2 | 5 | 0 | 11 | [13 empty] | 2.5\0.11:
BBD130 | DX05 | DIO1 | 130 | 2 | 5 | 0 | 11 | [13 empty] | 2.5\0.11:
[10 empty] | * |  | 4 | BJC130 |  | ROM BIN APRON FEEDER HPU | Rom Bin Apron Feeder To Bsr130Dx01 Master Relay |  | Sub Link | BJC130HP01 | [12 empty] | F7 | 1 | 2 | 3 | 4
[10 empty] | * |  | 4 | BJC130LU01LCS01 | LOS01 | PRIMARY JAW CRUSHER LUBRICATION UNIT | Emergency Stop Relay |  | Sub Link | BJC130PP01 |  |  | BR4-2110-E-00067 | 0 | [8 empty] | F7 | 5 | 6 | 7 | 8
[10 empty] | PNOZs4 | Safety Relay | 4 | BJC130LCS01 | LOS01 | PRIMARY JAW CRUSHER | Emergency Stop Relay |  | K202 | BJC130 |  |  | BR4-2110-E-00099 | 0 | [8 empty] | F7 | 9 | 10 | 11 | 12
[10 empty] | PNOZs4 | Safety Relay | 4 | BJC130LCS02 | LOS01 | PRIMARY JAW CRUSHER | Emergency Stop Relay |  | K218 | BJC130 |  |  | BR4-2110-E-00099 | 0 | [8 empty] | F7 | 13 | 14 | 15 | 16
[10 empty] | PNOZs4 | Safety Relay | 4 | BJC130HP01LCS01 | LOS01 | PRIMARY JAW CRUSHER HPU | Emergency Stop Relay |  | K303 | BJC130HP01 |  |  | BR4-2110-E-00100 | 0 | [8 empty] | F7 | 17 | 18 | 19 | 20
[10 empty] | PNOZs4 | Safety Relay | 4 | BRB13xLCS03 | LOS01 | ROM BIN AND PRIMARY CRUSHER ROCKBREAKERS | Emergency Shutdown 3 |  | K253-1 | BRB13x |  |  | BR4-2110-E-00099 | 0 | [8 empty] | F7 | 21 | 22 | 23 | 24
[10 empty] | PNOZs7.1 | Safety Relay | 4 | BRB13x |  |  | Emergency Shutdown |  | K253-2 | BRB13x |  |  | BR4-2110-E-00099 | 0
[10 empty] | PNOZs4 | Safety Relay | 4 | BRB13xLCS04 | LOS01 | ROM BIN AND PRIMARY CRUSHER ROCKBREAKERS | Emergency Shutdown 4 |  | K266-1 | BRB13x |  |  | BR4-2110-E-00099 | 0 | [8 empty] | F7 | 25 | 26 | 27 | 28
[10 empty] | PNOZs7.1 | Safety Relay | 4 | BRB13x |  |  | Emergency Shutdown |  | K266-2 | BRB13x |  |  | BR4-2110-E-00099 | 0
[10 empty] | * |  | 4 |  |  | BRB13x MASTER (to BRB131PN01 trip) | Emergency Shutdown | Trip | K253 | BRB13x |  |  | BR4-2110-E-00099 | 0 | [8 empty] | F7 | 29 | 30 | 31 | 32
[10 empty] | * |  | 4 |  |  | BRB13x MASTER (to BRB132PN01 trip) | Emergency Shutdown | Trip | K266 | BRB13x |  |  | BR4-2110-E-00099 | 0 | [8 empty] | F7 | 33 | 34 | 35 | 36
[32 empty] | F7 | 37 | 38 | 39 | 40
[32 empty] | F7 | 41 | 42 | 43 | 44
[32 empty] | F7 | 45 | 46 | 47 | 48
BBD130DX06 - Primary Crusher Building - Building
EIO node #6 | DX06 | DIO1 | 130 | 2 | 6 | 0
BBD130 | DX06 | DIO1 | 130 | 2 | 6 | 0 |  | Chassis |  | BMEXBP1200
BBD130 | DX06 | DIO1 | 130 | 2 | 6 | 0 |  | Power |  | BMXCPS4022 |  | total |  | spare |  | % spare | [7 empty] | there's enough room for 40 terminals including earthss
BBD130 | DX06 | DIO1 | 130 | 2 | 6 | 0 | 0 | Comms |  | BMECRA31210 | I/O1 | 120 |  | 71 |  | 59.17% | [7 empty] | mm
BBD130 | DX06 | DIO1 | 130 | 2 | 6 | 0 | 1 | 0 | BMXFCW303 | BMXDDI3202K | DI | 4 | BBD130DX06 | CB01 | 240VAC CIRCUIT BREAKER | 240VAC Circuit Breaker | Closed | Q106 | BBD130DX06 |  | 2.6\0.1:0 | BR4-2110-E-00103 | 0 |  | D | [6 empty] | F1 |  | 1
BBD130 | DX06 | DIO1 | 130 | 2 | 6 | 0 | 1 | 1 |  |  | DI | 4 | BBD130DX06 | VDC01 | 24VDC DIO1 OUTPUT CONTROL SUPPLY | 24VDC DIO1 Output Control Supply | Healthy | Q143 | BBD130DX06 |  | 2.6\0.1:1 | BR4-2110-E-00103 | 0 |  | D | [6 empty] | F1 |  | 2
BBD130 | DX06 | DIO1 | 130 | 2 | 6 | 0 | 1 | 2 |  |  | DI | 4 | BBD130DX06 | VDC02 | 24VDC GW1 CONTROL SUPPLY | 24VDC GW1 Control Supply | Healthy | Q157 | BBD130DX06 |  | 2.6\0.1:2 | BR4-2110-E-00103 | 0 |  | D | [6 empty] | F1 |  | 3
BBD130 | DX06 | DIO1 | 130 | 2 | 6 | 0 | 1 | 3 |  |  | DI | 4 | BBD130DX06 | VDC03 | 24VDC INSTRUMENT SUPPLY | 24VDC Instrument Supply | Healthy | Q164 | BBD130DX06 |  | 2.6\0.1:3 | BR4-2110-E-00103 | 0 |  | D | [6 empty] | F1 |  | 4
BBD130 | DX06 | DIO1 | 130 | 2 | 6 | 0 | 1 | 4 |  |  | DI | 4 | BBD130DX06 | VDC04 | 24VDC TRANSMITTER SUPPLY | 24VDC Transmitter Supply | Healthy | Q168 | BBD130DX06 |  | 2.6\0.1:4 | BR4-2110-E-00103 | 0 |  | D | [6 empty] | F1 |  | 5
BBD130 | DX06 | DIO1 | 130 | 2 | 6 | 0 | 1 | 5 |  |  | DI | 4 | BBD130DX06 | VDC05 | 24VDC APRON FEEDER ISOLATION GATE CONTROL SUPPLY | 24VDC Apron Feeder Isolation Gate Control Supply | Healthy | Q172 | BBD130DX06 |  | 2.6\0.1:5 | BR4-2110-E-00103 | 0 |  | D | [6 empty] | F1 |  | 6
BBD130 | DX06 | DIO1 | 130 | 2 | 6 | 0 | 1 | 6 |  |  | DI | 4 | BBD130DX06 | VDC06 | 24VDC ROCKBREAKER CONTROL SUPPLY | 24VDC Rockbreakers Control Supply | Healthy | Q176 | BBD130DX06 |  | 2.6\0.1:6 | BR4-2110-E-00103 | 0 |  | D | [6 empty] | F1 |  | 7
BBD130 | DX06 | DIO1 | 130 | 2 | 6 | 0 | 1 | 7 |  |  | DI | 4 | BBD130DX06 | VDC07 | 24VDC DUST COLLETOR CONTROL SUPPLY | 24VDC Dust Collector Control Supply | Healthy | Q180 | BBD130DX06 |  | 2.6\0.1:7 | BR4-2110-E-00103 | 0 |  | D | [6 empty] | F1 |  | 8
BBD130 | DX06 | DIO1 | 130 | 2 | 6 | 0 | 1 | 8 |  |  | DI | 4 | BBD130DX06 | VDC08 | Spare 24VDC Control Supply | Spare Control Supply | Healthy | Q184 | BBD130DX06 |  | 2.6\0.1:8 | BR4-2110-E-00103 | 0 |  | D | [6 empty] | F1 |  | 9
BBD130 | DX06 | DIO1 | 130 | 2 | 6 | 0 | 1 | 9 |  |  | DI | 4 | BBD130DX06 | VDC09 | Spare 24VDC Control Supply | Spare Control Supply | Healthy | Q188 | BBD130DX06 |  | 2.6\0.1:9 | BR4-2110-E-00103 | 0 |  | D | [6 empty] | F1 |  | 10
BBD130 | DX06 | DIO1 | 130 | 2 | 6 | 0 | 1 | 10 |  |  | DI | 4 | BBD130DX06 | VDC10 | Spare 24VDC Control Supply | Spare Control Supply | Healthy | Q192 | BBD130DX06 |  | 2.6\0.1:10 | BR4-2110-E-00103 | 0 |  | D | [6 empty] | F1 |  | 11
BBD130 | DX06 | DIO1 | 130 | 2 | 6 | 0 | 1 | 11 |  |  | DI | 4 | BBD130DX06 | VDC11 | Spare 24VDC Control Supply | Spare Control Supply | Healthy | Q196 | BBD130DX06 |  | 2.6\0.1:11 | BR4-2110-E-00103 | 0 |  | D | [6 empty] | F1 |  | 12
BBD130 | DX06 | DIO1 | 130 | 2 | 6 | 0 | 1 | 12 |  |  | DI | [9 empty] | 2.6\0.1:12 |  |  |  | S | [6 empty] | F1 |  | 13
BBD130 | DX06 | DIO1 | 130 | 2 | 6 | 0 | 1 | 13 |  |  | DI | [9 empty] | 2.6\0.1:13 |  |  |  | S | [6 empty] | F1 |  | 14
BBD130 | DX06 | DIO1 | 130 | 2 | 6 | 0 | 1 | 14 |  |  | DI | [9 empty] | 2.6\0.1:14 |  |  |  | S | [6 empty] | F1 |  | 15
BBD130 | DX06 | DIO1 | 130 | 2 | 6 | 0 | 1 | 15 |  |  | DI | [9 empty] | 2.6\0.1:15 |  |  |  | S | [6 empty] | F1 |  | 16
BBD130 | DX06 | DIO1 | 130 | 2 | 6 | 0 | 1 | 16 |  |  | DI | 4 | BDU130FN01LCS01 | STT01 | DUST COLLECTOR FAN | Start Pushbutton | Activated | STT01 | BDU130FN01 |  | 2.6\0.1:16 | BR4-2110-E-00058 | 0 |  | S | [6 empty] | F1 | 17 | 18
BBD130 | DX06 | DIO1 | 130 | 2 | 6 | 0 | 1 | 17 |  |  | DI | 4 | BDU130FN01LCS01 | STP01 | DUST COLLECTOR FAN | Stop Pushbutton | Activated | STP01 | BDU130FN01 |  | 2.6\0.1:17 | BR4-2110-E-00058 | 0 |  | S | [6 empty] | F1 | 19 | 20
BBD130 | DX06 | DIO1 | 130 | 2 | 6 | 0 | 1 | 18 |  |  | DI | [9 empty] | 2.6\0.1:18 |  |  |  | S | [6 empty] | F1 | 21 | 22
BBD130 | DX06 | DIO1 | 130 | 2 | 6 | 0 | 1 | 19 |  |  | DI | 4 | BDU130HOP01LS01 | LS01 | DUST COLLECTOR HOPPER | Hopper Level | High |  | BDU130HOP01 |  | 2.6\0.1:19 | BR4-2110-E-00105 | 0 |  | S | [6 empty] | F1 | 23 | 24
BBD130 | DX06 | DIO1 | 130 | 2 | 6 | 0 | 1 | 20 |  |  | DI | 4 | BDU130HOP01LS02 | LS02 | DUST COLLECTOR HOPPER | Hopper Level | Low |  | BDU130HOP01 |  | 2.6\0.1:20 | BR4-2110-E-00105 | 0 |  | S | [6 empty] | F1 | 25 | 26
BBD130 | DX06 | DIO1 | 130 | 2 | 6 | 0 | 1 | 21 |  |  | DI | 4 | BDU130RV01LCS01 | STT01 | DUST COLLECTOR ROTARY VALVE | Start Pushbutton | Activated | STT01 | BDU130RV01 |  | 2.6\0.1:21 | BR4-2110-E-00059 | 0 |  | S | [6 empty] | F1 | 27 | 28
BBD130 | DX06 | DIO1 | 130 | 2 | 6 | 0 | 1 | 22 |  |  | DI | 4 | BDU130RV01LCS01 | STP01 | DUST COLLECTOR ROTARY VALVE | Stop Pushbutton | Activated | STP01 | BDU130RV01 |  | 2.6\0.1:22 | BR4-2110-E-00059 | 0 |  | S | [6 empty] | F1 | 29 | 30
BBD130 | DX06 | DIO1 | 130 | 2 | 6 | 0 | 1 | 23 |  |  | DI | [9 empty] | 2.6\0.1:23 |  |  |  | S | [6 empty] | F1 | 31 | 32
BBD130 | DX06 | DIO1 | 130 | 2 | 6 | 0 | 1 | 24 |  |  | DI | 5 | BDU130RV01LCS01 | IS01 | DUST COLLECTOR ROTARY VALVE | Local Isolator | Closed | IS01 | BDU130RV01 |  | 2.6\0.1:24 |  |  |  | S | [6 empty] | F1 | 33 | 34
BBD130 | DX06 | DIO1 | 130 | 2 | 6 | 0 | 1 | 25 |  |  | DI | 4 | BDU130RV01SS01 | SS01 | DUST COLLECTOR ROTARY VALVE | Underspeed Pulse | Activated |  | BDU130RV01 |  | 2.6\0.1:25 | BR4-2110-E-00105 | 0 |  | S | [6 empty] | F1 | 35 | 36
BBD130 | DX06 | DIO1 | 130 | 2 | 6 | 0 | 1 | 26 |  |  | DI | [9 empty] | 2.6\0.1:26 |  |  |  | S | [6 empty] | F1 | 37 | 38
BBD130 | DX06 | DIO1 | 130 | 2 | 6 | 0 | 1 | 27 |  |  | DI | 4 | BDU130FN01 | THR01 | DUST COLLECTOR FAN MOTOR | PTC Thermistor Relay | Healthy | K187 | BDU130FN01 |  | 2.6\0.1:27 | BR4-2110-E-00058 | 0 |  | S | [6 empty] | F1 | 39 | 40
BBD130 | DX06 | DIO1 | 130 | 2 | 6 | 0 | 1 | 28 |  |  | DI | [9 empty] | 2.6\0.1:28 |  |  |  | S | [6 empty] | F1 | 41 | 42
BBD130 | DX06 | DIO1 | 130 | 2 | 6 | 0 | 1 | 29 |  |  | DI | [9 empty] | 2.6\0.1:29 |  |  |  | S | [6 empty] | F1 | 43 | 44
BBD130 | DX06 | DIO1 | 130 | 2 | 6 | 0 | 1 | 30 |  |  | DI | [9 empty] | 2.6\0.1:30 |  |  |  | S | [6 empty] | F1 | 45 | 46
BBD130 | DX06 | DIO1 | 130 | 2 | 6 | 0 | 1 | 31 |  |  | DI | [9 empty] | 2.6\0.1:31 |  |  |  | S | [6 empty] | F1 | 47 | 48
BBD130 | DX06 | DIO1 | 130 | 2 | 6 | 0 | 2 | 0 | BMXFCW303 | BMXDDI3202K | DI | 4 | BDU130CP01 | ZS01 | DUST COLLECTOR COMPRESSOR | Power | Healthy |  | BDU130CP01 |  | 2.6\0.2:0 | BR4-2110-E-00105 | 0 |  | S | [6 empty] | F2 | 1 | 2
BBD130 | DX06 | DIO1 | 130 | 2 | 6 | 0 | 2 | 1 |  |  | DI | 4 | BDU130CP01 | XS01 | DUST COLLECTOR COMPRESSOR | General | Healthy |  | BDU130CP01 |  | 2.6\0.2:1 | BR4-2110-E-00105 | 0 |  | S | [6 empty] | F2 | 3 | 4
BBD130 | DX06 | DIO1 | 130 | 2 | 6 | 0 | 2 | 2 |  |  | DI | 4 | BDU130CP01 | XS02 | DUST COLLECTOR COMPRESSOR | Running Contactor | Closed |  | BDU130CP01 |  | 2.6\0.2:2 | BR4-2110-E-00105 | 0 |  | S | [6 empty] | F2 | 5 | 6
BBD130 | DX06 | DIO1 | 130 | 2 | 6 | 0 | 2 | 3 |  |  | DI | 4 | BDU130DY01 | XS01 | DUST COLLECTOR DRYER | General | Healthy |  | BDU130DY01 |  | 2.6\0.2:3 | BR4-2110-E-00105 | 0 |  | S | [6 empty] | F2 | 7 | 8
BBD130 | DX06 | DIO1 | 130 | 2 | 6 | 0 | 2 | 4 |  |  | DI | [9 empty] | 2.6\0.2:4 |  |  |  | S | [6 empty] | F2 | 9 | 10
BBD130 | DX06 | DIO1 | 130 | 2 | 6 | 0 | 2 | 5 |  |  | DI | [9 empty] | 2.6\0.2:5 |  |  |  | S | [6 empty] | F2 | 11 | 12
BBD130 | DX06 | DIO1 | 130 | 2 | 6 | 0 | 2 | 6 |  |  | DI | 4 | BBD130PP01LCS03 | STT01 | PRIMARY CRUSHER AREA SUMP PUMP | Start Pushbutton | Activated | STT01 | BBD130PP01 |  | 2.6\0.2:6 | BR4-2110-E-00042 | 0 |  | S | [6 empty] | F2 | 13 | 14
BBD130 | DX06 | DIO1 | 130 | 2 | 6 | 0 | 2 | 7 |  |  | DI | 4 | BBD130PP01LCS03 | STP01 | PRIMARY CRUSHER AREA SUMP PUMP | Stop Pushbutton | Activated | STP01 | BBD130PP01 |  | 2.6\0.2:7 | BR4-2110-E-00042 | 0 |  | S | [6 empty] | F2 | 15 | 16
BBD130 | DX06 | DIO1 | 130 | 2 | 6 | 0 | 2 | 8 |  |  | DI | 5 | BBD130PP01LCS03 | IS01 | PRIMARY CRUSHER AREA SUMP PUMP | Isolator | Closed | IS01 | BBD130PP01 |  | 2.6\0.2:8 | BR4-2110-E-00042 | 0 |  | S | [6 empty] | F2 | 17 | 18
BBD130 | DX06 | DIO1 | 130 | 2 | 6 | 0 | 2 | 9 |  |  | DI | [9 empty] | 2.6\0.2:9 |  |  |  | S | [6 empty] | F2 | 19 | 20
BBD130 | DX06 | DIO1 | 130 | 2 | 6 | 0 | 2 | 10 |  |  | DI | 5 | BAF130PP05LCS01 | IS01 | APRON FEEDER ISOLATION GATE HPU | Isolator | Closed | IS01 | BAF130PP05 |  | 2.6\0.2:10 | BR4-2110-E-00056 | 0 |  | S | [6 empty] | F2 | 21 | 22
BBD130 | DX06 | DIO1 | 130 | 2 | 6 | 0 | 2 | 11 |  |  | DI | 5 | BAF130PP05LCS01 | STT01 | APRON FEEDER ISOLATION GATE HPU | Start Pushbutton | Activated | STT01 | BAF130PP05 |  | 2.6\0.2:11 | BR4-2110-E-00056 | 0 |  | S | [6 empty] | F2 | 23 | 24
BBD130 | DX06 | DIO1 | 130 | 2 | 6 | 0 | 2 | 12 |  |  | DI | 5 | BAF130PP05LCS01 | STP01 | APRON FEEDER ISOLATION GATE HPU | Stop Pushbutton | Activated | STP01 | BAF130PP05 |  | 2.6\0.2:12 | BR4-2110-E-00056 | 0 |  | S | [6 empty] | F2 | 25 | 26
BBD130 | DX06 | DIO1 | 130 | 2 | 6 | 0 | 2 | 13 |  |  | DI | 4 | BAF130PP05LCS01 | SY01 | APRON FEEDER ISOLATION GATE HPU | Emergency Stop Relay | Healthy | K202 | BAF130PP05 |  | 2.6\0.2:13 | BR4-2110-E-00104 | 0 |  | D | [6 empty] | F2 | 27 | 28
BBD130 | DX06 | DIO1 | 130 | 2 | 6 | 0 | 2 | 14 |  |  | DI | 5 | BAF130HP02PS06 | PS06 | APRON FEEDER ISOLATION GATE HPU | Pressure Filter 2 | Healthy |  | BAF130HP02 |  | 2.6\0.2:14 | BR4-2110-E-00125 | 0 |  | S | [6 empty] | F2 | 29 | 30
BBD130 | DX06 | DIO1 | 130 | 2 | 6 | 0 | 2 | 15 |  |  | DI | 5 | BAF130HP02FS01 | FS01 | APRON FEEDER ISOLATION GATE HPU | Flow Switch | Healthy |  | BAF130HP02 |  | 2.6\0.2:15 | BR4-2110-E-00125 | 0 |  | S | [6 empty] | F2 | 31 | 32
BBD130 | DX06 | DIO1 | 130 | 2 | 6 | 0 | 2 | 16 |  |  | DI | 4 | BAF130HP02LS01 | LS01 | APRON FEEDER ISOLATION GATE HPU | Oil Level Low | Healthy |  | BAF130HP02 |  | 2.6\0.2:16 | BR4-2110-E-00125 | 0 |  | S | [6 empty] | F3 | 1 | 2
BBD130 | DX06 | DIO1 | 130 | 2 | 6 | 0 | 2 | 17 |  |  | DI | 4 | BAF130HP02PS01 | PS01 | APRON FEEDER ISOLATION GATE HPU | Supply Line Pressure | Healthy |  | BAF130HP02 |  | 2.6\0.2:17 | BR4-2110-E-00125 | 0 |  | S | [6 empty] | F3 | 3 | 4
BBD130 | DX06 | DIO1 | 130 | 2 | 6 | 0 | 2 | 18 |  |  | DI | 5 | BAF130HP02PS03 | PS03 | APRON FEEDER ISOLATION GATE HPU | Return Filter 1 | Healthy |  | BAF130HP02 |  | 2.6\0.2:18 | BR4-2110-E-00125 | 0 |  | S | [6 empty] | F3 | 5 | 6
BBD130 | DX06 | DIO1 | 130 | 2 | 6 | 0 | 2 | 19 |  |  | DI | 5 | BAF130HP02PS04 | PS04 | APRON FEEDER ISOLATION GATE HPU | Return Filter 2 | Healthy |  | BAF130HP02 |  | 2.6\0.2:19 | BR4-2110-E-00125 | 0 |  | S | [6 empty] | F3 | 7 | 8
BBD130 | DX06 | DIO1 | 130 | 2 | 6 | 0 | 2 | 20 |  |  | DI | 5 | BAF130HP02PS05 | PS05 | APRON FEEDER ISOLATION GATE HPU | Pressure Filter 1 | Healthy |  | BAF130HP02 |  | 2.6\0.2:20 | BR4-2110-E-00125 | 0 |  | S | [6 empty] | F3 | 9 | 10
BBD130 | DX06 | DIO1 | 130 | 2 | 6 | 0 | 2 | 21 |  |  | DI | 4 | BAF130GA01LCS01 | PB01 | ROM BIN APRON FEEDER ISOLATION GATE | Open Pushbutton | Activated | PB01 | BAF130GA01 |  | 2.6\0.2:21 | BR4-2110-E-00104 | 0 |  | S | [6 empty] | F3 | 11 | 12
BBD130 | DX06 | DIO1 | 130 | 2 | 6 | 0 | 2 | 22 |  |  | DI | 4 | BAF130GA01LCS01 | PB02 | ROM BIN APRON FEEDER ISOLATION GATE | Close Pushbutton | Activated | PB02 | BAF130GA01 |  | 2.6\0.2:22 | BR4-2110-E-00104 | 0 |  | S | [6 empty] | F3 | 13 | 14
BBD130 | DX06 | DIO1 | 130 | 2 | 6 | 0 | 2 | 23 |  |  | DI | 4 | BAF130GA01LCS01 | SY01 | ROM BIN APRON FEEDER ISOLATION GATE | Emergency Stop Relay | Healthy | K220 | BAF130GA01 |  | 2.6\0.2:23 | BR4-2110-E-00104 | 0 |  | D | [6 empty] | F3 | 15 | 16
BBD130 | DX06 | DIO1 | 130 | 2 | 6 | 0 | 2 | 24 |  |  | DI | 4 | BAF130GA01ZS01 | ZS01 | ROM BIN APRON FEEDER ISOLATION GATE | Actuator 1 | Open |  | BAF130GA01 |  | 2.6\0.2:24 | BR4-2110-E-00125 | 0 |  | S | [6 empty] | F3 | 17 | 18
BBD130 | DX06 | DIO1 | 130 | 2 | 6 | 0 | 2 | 25 |  |  | DI | 4 | BAF130GA01ZS02 | ZS02 | ROM BIN APRON FEEDER ISOLATION GATE | Actuator 1 | Closed |  | BAF130GA01 |  | 2.6\0.2:25 | BR4-2110-E-00125 | 0 |  | S | [6 empty] | F3 | 19 | 20
BBD130 | DX06 | DIO1 | 130 | 2 | 6 | 0 | 2 | 26 |  |  | DI | 4 | BAF130GA01ZS03 | ZS03 | ROM BIN APRON FEEDER ISOLATION GATE | Actuator 2 | Open |  | BAF130GA01 |  | 2.6\0.2:26 | BR4-2110-E-00125 | 0 |  | S | [6 empty] | F3 | 21 | 22
BBD130 | DX06 | DIO1 | 130 | 2 | 6 | 0 | 2 | 27 |  |  | DI | 4 | BAF130GA01ZS04 | ZS04 | ROM BIN APRON FEEDER ISOLATION GATE | Actuator 2 | Closed |  | BAF130GA01 |  | 2.6\0.2:27 | BR4-2110-E-00125 | 0 |  | S | [6 empty] | F3 | 23 | 24
BBD130 | DX06 | DIO1 | 130 | 2 | 6 | 0 | 2 | 28 |  |  | DI | 4 | BAF130GA01ZS05 | ZS05 | ROM BIN APRON FEEDER ISOLATION GATE | Locking Pin 1A | Engaged |  | BAF130GA01 |  | 2.6\0.2:28 | BR4-2110-E-00125 | 0 |  | S | [6 empty] | F3 | 25 | 26
BBD130 | DX06 | DIO1 | 130 | 2 | 6 | 0 | 2 | 29 |  |  | DI | 4 | BAF130GA01ZS06 | ZS06 | ROM BIN APRON FEEDER ISOLATION GATE | Locking Pin 1B | Engaged |  | BAF130GA01 |  | 2.6\0.2:29 | BR4-2110-E-00125 | 0 |  | S | [6 empty] | F3 | 27 | 28
BBD130 | DX06 | DIO1 | 130 | 2 | 6 | 0 | 2 | 30 |  |  | DI | 4 | BAF130GA01ZS07 | ZS07 | ROM BIN APRON FEEDER ISOLATION GATE | Locking Pin 2A | Engaged |  | BAF130GA01 |  | 2.6\0.2:30 | BR4-2110-E-00125 | 0 |  | S | [6 empty] | F3 | 29 | 30
BBD130 | DX06 | DIO1 | 130 | 2 | 6 | 0 | 2 | 31 |  |  | DI | 4 | BAF130GA01ZS08 | ZS08 | ROM BIN APRON FEEDER ISOLATION GATE | Locking Pin 2B | Engaged |  | BAF130GA01 |  | 2.6\0.2:31 | BR4-2110-E-00125 | 0 |  | S | [6 empty] | F3 | 31 | 32
BBD130 | DX06 | DIO1 | 130 | 2 | 6 | 0 | 3 | 0 | BMXFCW303 | BMXDDI3202K | DI | [9 empty] | 2.6\0.3:0 |  |  |  | S | [6 empty] | F4 | 1 | 2
BBD130 | DX06 | DIO1 | 130 | 2 | 6 | 0 | 3 | 1 |  |  | DI | [9 empty] | 2.6\0.3:1 |  |  |  | S | [6 empty] | F4 | 3 | 4
BBD130 | DX06 | DIO1 | 130 | 2 | 6 | 0 | 3 | 2 |  |  | DI | 4 | BRB132XS01 | XS01 | PRIMARY JAW CRUSHER ROCKBREAKER | HPU | Running |  | BRB132 |  | 2.6\0.3:2 | BR4-2110-E-00105 | 0 |  | S | [6 empty] | F4 | 5 | 6
BBD130 | DX06 | DIO1 | 130 | 2 | 6 | 0 | 3 | 3 |  |  | DI | 4 | BRB132XS02 | XS02 | PRIMARY JAW CRUSHER ROCKBREAKER | HPU | Healthy |  | BRB132 |  | 2.6\0.3:3 | BR4-2110-E-00105 | 0 |  | S | [6 empty] | F4 | 7 | 8
BBD130 | DX06 | DIO1 | 130 | 2 | 6 | 0 | 3 | 4 |  |  | DI | 4 | BRB132XS03 | XS03 | PRIMARY JAW CRUSHER ROCKBREAKER | Safety System | Healthy |  | BRB132 |  | 2.6\0.3:4 | BR4-2110-E-00105 | 0 |  | S | [6 empty] | F4 | 9 | 10
BBD130 | DX06 | DIO1 | 130 | 2 | 6 | 0 | 3 | 5 |  |  | DI | 4 | BRB132XS04 | XS04 | PRIMARY JAW CRUSHER ROCKBREAKER | HPU In Test/Operate Mode |  |  | BRB132 |  | 2.6\0.3:5 | BR4-2110-E-00105 | 0 |  | S | [6 empty] | F4 | 11 | 12
BBD130 | DX06 | DIO1 | 130 | 2 | 6 | 0 | 3 | 6 |  |  | DI | 4 | BRB132XS05 | XS05 | PRIMARY JAW CRUSHER ROCKBREAKER | Boomsafe | Healthy |  | BRB132 |  | 2.6\0.3:6 | BR4-2110-E-00105 | 0 |  | S | [6 empty] | F4 | 13 | 14
BBD130 | DX06 | DIO1 | 130 | 2 | 6 | 0 | 3 | 7 |  |  | DI | 4 | BRB132XS06 | XS06 | PRIMARY JAW CRUSHER ROCKBREAKER | Boomsafe | Parked |  | BRB132 |  | 2.6\0.3:7 | BR4-2110-E-00105 | 0 |  | S | [6 empty] | F4 | 15 | 16
BBD130 | DX06 | DIO1 | 130 | 2 | 6 | 0 | 3 | 8 |  |  | DI | 4 | BRB132XS07 | XS07 | PRIMARY JAW CRUSHER ROCKBREAKER | Boomsafe In Remote Mode | Activated |  | BRB132 |  | 2.6\0.3:8 | BR4-2110-E-00105 | 0 |  | S | [6 empty] | F4 | 17 | 18
BBD130 | DX06 | DIO1 | 130 | 2 | 6 | 0 | 3 | 9 |  |  | DI | [9 empty] | 2.6\0.3:9 |  |  | This Isnt shown on the Termination or Schematics? 00149/00104 | S | [6 empty] | F4 | 19 | 20
BBD130 | DX06 | DIO1 | 130 | 2 | 6 | 0 | 3 | 10 |  |  | DI | 4 | BRB13xLCS05 | SY05 | ROM BIN AND PRIMARY CRUSHER ROCKBREAKERS | Emergency Shutdown 5 | Healthy | K253-1 | BRB13x |  | 2.6\0.3:10 | BR4-2110-E-00104 | 0 |  | D | [6 empty] | F4 | 21 | 22
BBD130 | DX06 | DIO1 | 130 | 2 | 6 | 0 | 3 | 11 |  |  | DI | 4 | BRB132HP01FS02 | FS02 | PRIMARY JAW CRUSHER ROCKBREAKER HPU FIRE SPRINKLER | Flow Switch | Healthy |  | BRB132HP01 |  | 2.6\0.3:11 | BR4-2110-E-00105 | 0 |  | S | [6 empty] | F4 | 23 | 24
BBD130 | DX06 | DIO1 | 130 | 2 | 6 | 0 | 3 | 12 |  |  | DI | [9 empty] | 2.6\0.3:12 |  |  |  | S | [6 empty] | F4 | 25 | 26
BBD130 | DX06 | DIO1 | 130 | 2 | 6 | 0 | 3 | 13 |  |  | DI | [9 empty] | 2.6\0.3:13 |  |  |  | S | [6 empty] | F4 | 27 | 28
BBD130 | DX06 | DIO1 | 130 | 2 | 6 | 0 | 3 | 14 |  |  | DI | [9 empty] | 2.6\0.3:14 |  |  |  | S | [6 empty] | F4 | 29 | 30
BBD130 | DX06 | DIO1 | 130 | 2 | 6 | 0 | 3 | 15 |  |  | DI | [9 empty] | 2.6\0.3:15 |  |  |  | S | [6 empty] | F4 | 31 | 32
BBD130 | DX06 | DIO1 | 130 | 2 | 6 | 0 | 3 | 16 |  |  | DI | [5 empty] | \ |  |  |  | 2.6\0.3:16 |  |  |  | S | [6 empty] | F6 | 1 | 2
BBD130 | DX06 | DIO1 | 130 | 2 | 6 | 0 | 3 | 17 |  |  | DI | [9 empty] | 2.6\0.3:17 |  |  |  | S | [6 empty] | F6 | 3 | 4
BBD130 | DX06 | DIO1 | 130 | 2 | 6 | 0 | 3 | 18 |  |  | DI | [9 empty] | 2.6\0.3:18 |  |  |  | S | [6 empty] | F6 | 5 | 6
BBD130 | DX06 | DIO1 | 130 | 2 | 6 | 0 | 3 | 19 |  |  | DI | [9 empty] | 2.6\0.3:19 |  |  |  | S | [6 empty] | F6 | 7 | 8
BBD130 | DX06 | DIO1 | 130 | 2 | 6 | 0 | 3 | 20 |  |  | DI | [9 empty] | 2.6\0.3:20 |  |  |  | S | [6 empty] | F6 | 9 | 10
BBD130 | DX06 | DIO1 | 130 | 2 | 6 | 0 | 3 | 21 |  |  | DI | [9 empty] | 2.6\0.3:21 |  |  |  | S | [6 empty] | F6 | 11 | 12
BBD130 | DX06 | DIO1 | 130 | 2 | 6 | 0 | 3 | 22 |  |  | DI | [9 empty] | 2.6\0.3:22 |  |  |  | S | [6 empty] | F6 | 13 | 14
BBD130 | DX06 | DIO1 | 130 | 2 | 6 | 0 | 3 | 23 |  |  | DI | [9 empty] | 2.6\0.3:23 |  |  |  | S | [6 empty] | F6 | 15 | 16
BBD130 | DX06 | DIO1 | 130 | 2 | 6 | 0 | 3 | 24 |  |  | DI | [9 empty] | 2.6\0.3:24 |  |  |  | S | [6 empty] | F6 | 17 | 18
BBD130 | DX06 | DIO1 | 130 | 2 | 6 | 0 | 3 | 25 |  |  | DI | [9 empty] | 2.6\0.3:25 |  |  |  | S | [6 empty] | F6 | 19 | 20
BBD130 | DX06 | DIO1 | 130 | 2 | 6 | 0 | 3 | 26 |  |  | DI | [9 empty] | 2.6\0.3:26 |  |  |  | S | [6 empty] | F6 | 21 | 22
BBD130 | DX06 | DIO1 | 130 | 2 | 6 | 0 | 3 | 27 |  |  | DI | [9 empty] | 2.6\0.3:27 |  |  |  | S | [6 empty] | F6 | 23 | 24
BBD130 | DX06 | DIO1 | 130 | 2 | 6 | 0 | 3 | 28 |  |  | DI | [9 empty] | 2.6\0.3:28 |  |  |  | S | [6 empty] | F6 | 25 | 26
BBD130 | DX06 | DIO1 | 130 | 2 | 6 | 0 | 3 | 29 |  |  | DI | [9 empty] | 2.6\0.3:29 |  |  |  | S | [6 empty] | F6 | 27 | 28
BBD130 | DX06 | DIO1 | 130 | 2 | 6 | 0 | 3 | 30 |  |  | DI | [9 empty] | 2.6\0.3:30 |  |  |  | S | [6 empty] | F6 | 29 | 30
BBD130 | DX06 | DIO1 | 130 | 2 | 6 | 0 | 3 | 31 |  |  | DI | [9 empty] | 2.6\0.3:31 |  |  |  | S | [6 empty] | F6 | 31 | 32
BBD130 | DX06 | DIO1 | 130 | 2 | 6 | 0 | 4 | 0 | BMXFTB2010 | BMXDDO1602 | DO | 4 | BBD130PP01SV02 | SV02 | PRIMARY CRUSHER AREA SUMP PUMP | Agitator Solenoid Valve |  |  | BBD130PP01 |  | 2.6\0.4:0 | BR4-2110-E-00105 | 0 |  | S | [6 empty] | F5 | 1 | 2
BBD130 | DX06 | DIO1 | 130 | 2 | 6 | 0 | 4 | 1 |  |  | DO | 4 | BDU130CP01SR01 | SR01 | DUST COLLECTOR COMPRESSOR | Compressor Enable |  | SR01 | BDU130CP01 |  | 2.6\0.4:1 | BR4-2110-E-00105 | 0 |  | S | [6 empty] | F5 | 3 | 4
BBD130 | DX06 | DIO1 | 130 | 2 | 6 | 0 | 4 | 2 |  |  | DO | [9 empty] | 2.6\0.4:2 |  |  |  | S | [6 empty] | F5 | 5 | 6
BBD130 | DX06 | DIO1 | 130 | 2 | 6 | 0 | 4 | 3 |  |  | DO | [9 empty] | 2.6\0.4:3 |  |  |  | S | [6 empty] | F5 | 7 | 8
BBD130 | DX06 | DIO1 | 130 | 2 | 6 | 0 | 4 | 4 |  |  | DO | 4 | BRB132SR01 | SR01 | PRIMARY JAW CRUSHER ROCKBREAKER | Ok To Operate |  | SR01 | BRB132 |  | 2.6\0.4:4 | BR4-2110-E-00105 | 0 |  | S | [6 empty] | F5 | 9 | 10
BBD130 | DX06 | DIO1 | 130 | 2 | 6 | 0 | 4 | 5 |  |  | DO | 4 | BRB132SR02 | SR02 | PRIMARY JAW CRUSHER ROCKBREAKER | Ok To Deploy |  | SR02 | BRB132 |  | 2.6\0.4:5 | BR4-2110-E-00105 | 0 |  | S | [6 empty] | F5 | 11 | 12
BBD130 | DX06 | DIO1 | 130 | 2 | 6 | 0 | 4 | 6 |  |  | DO | [9 empty] | 2.6\0.4:6 |  |  |  | S | [6 empty] | F5 | 13 | 14
BBD130 | DX06 | DIO1 | 130 | 2 | 6 | 0 | 4 | 7 |  |  | DO | [9 empty] | 2.6\0.4:7 |  |  |  | S | [6 empty] | F5 | 15 | 16
BBD130 | DX06 | DIO1 | 130 | 2 | 6 | 0 | 4 | 8 |  |  | DO | [9 empty] | 2.6\0.4:8 |  |  |  | S | [6 empty] | F5 | 17 | 18
BBD130 | DX06 | DIO1 | 130 | 2 | 6 | 0 | 4 | 9 |  |  | DO | [9 empty] | 2.6\0.4:9 |  |  |  | S | [6 empty] | F5 | 19 | 20
BBD130 | DX06 | DIO1 | 130 | 2 | 6 | 0 | 4 | 10 |  |  | DO | 4 | BAF130HP02 | SR01 | ROM BIN APRON FEEDER ISOLATION GATE HPU | Hydraulic Pump Running |  |  | BAF130HP02 |  | 2.6\0.4:10 | BR4-2110-E-00125 | 0 |  | S | [6 empty] | F5 | 21 | 22
BBD130 | DX06 | DIO1 | 130 | 2 | 6 | 0 | 4 | 11 |  |  | DO | 4 | BAF130GA01YA01 | YA01 | ROM BIN APRON FEEDER ISOLATION GATE | Start Up Warning Siren |  |  | BAF130GA01 |  | 2.6\0.4:11 | BR4-2110-E-00125 | 0 |  | S | [6 empty] | F5 | 23 | 24
BBD130 | DX06 | DIO1 | 130 | 2 | 6 | 0 | 4 | 12 |  |  | DO | 4 | BAF130GA01SV01 | SV01 | ROM BIN APRON FEEDER ISOLATION GATE | Open Solenoid |  |  | BAF130GA01 |  | 2.6\0.4:12 | BR4-2110-E-00125 | 0 |  | S | [6 empty] | F5 | 25 | 26
BBD130 | DX06 | DIO1 | 130 | 2 | 6 | 0 | 4 | 13 |  |  | DO | 4 | BAF130GA01SV02 | SV02 | ROM BIN APRON FEEDER ISOLATION GATE | Close Solenoid |  |  | BAF130GA01 |  | 2.6\0.4:13 | BR4-2110-E-00125 | 0 |  | S | [6 empty] | F5 | 27 | 28
BBD130 | DX06 | DIO1 | 130 | 2 | 6 | 0 | 4 | 14 |  |  | DO | 4 | BAF130GA01YL01 | YL01 | ROM BIN APRON FEEDER ISOLATION GATE | Open Indicator Light |  |  | BAF130GA01 |  | 2.6\0.4:14 | BR4-2110-E-00125 | 0 |  | S | [6 empty] | F5 | 29 | 30
BBD130 | DX06 | DIO1 | 130 | 2 | 6 | 0 | 4 | 15 |  |  | DO | 4 | BAF130GA01YL02 | YL02 | ROM BIN APRON FEEDER ISOLATION GATE | Closed Indicator Light |  |  | BAF130GA01 |  | 2.6\0.4:15 | BR4-2110-E-00125 | 0 |  | S | [6 empty] | F5 | 31 | 32
BBD130 | DX06 | DIO1 | 130 | 2 | 6 | 0 | 5 | 0 | BMXFTW301S | BMEAHI0812 | AI | 4 | BBD130SM01LT01 | LT01 | PRIMARY CRUSHER AREA SUMP | Level |  | % | BBD130SM01 | REAL | 2.6\0.5:0 | BR4-2110-E-00125 | 0 |  | S |  | 0 | 100 | 0 | 100 | #.# EU | F5 | 33 | 34
BBD130 | DX06 | DIO1 | 130 | 2 | 6 | 0 | 5 | 1 |  |  | AI | 4 | BDU130CP01PT01 | PT01 | DUST COLLECTOR COMPRESSOR | Filter Air Pressure |  | kPa | BDU130CP01 | REAL | 2.6\0.5:1 | BR4-2110-E-00125 | 0 |  | S |  | 0 | 10 | 0 | 10 | #.# EU | F5 | 35 | 36
BBD130 | DX06 | DIO1 | 130 | 2 | 6 | 0 | 5 | 2 |  |  | AI | 4 | BDU130PDIT01 | XT01 | DUST COLLECTOR | Differential Pressure |  | kPa | BDU130 | REAL | 2.6\0.5:2 | BR4-2110-E-00125 | 0 |  | S |  | 0 | 10 | 0 | 10 | #.# EU | F5 | 37 | 38
BBD130 | DX06 | DIO1 | 130 | 2 | 6 | 0 | 5 | 3 |  |  | AI | 5 | BAF130HP02TT01 | TT01 | ROM BIN APRON FEEDER ISOLATION GATE HPU | Temperature |  | C | BAF130HP02 | REAL | 2.6\0.5:3 | BR4-2110-E-00125 | 0 |  | S | [6 empty] | F5 | 39 | 40
BBD130 | DX06 | DIO1 | 130 | 2 | 6 | 0 | 5 | 4 |  |  | AI | [9 empty] | 2.6\0.5:4 |  |  |  | S | [6 empty] | F5 | 41 | 42
BBD130 | DX06 | DIO1 | 130 | 2 | 6 | 0 | 5 | 5 |  |  | AI | [9 empty] | 2.6\0.5:5 |  |  |  | S | [6 empty] | F5 | 43 | 44
BBD130 | DX06 | DIO1 | 130 | 2 | 6 | 0 | 5 | 6 |  |  | AI | [9 empty] | 2.6\0.5:6 |  |  |  | S | [6 empty] | F5 | 45 | 46
BBD130 | DX06 | DIO1 | 130 | 2 | 6 | 0 | 5 | 7 |  |  | AI | [9 empty] | 2.6\0.5:7 |  |  |  | S | [6 empty] | F5 | 47 | 48
BBD130 | DX06 | DIO1 | 130 | 2 | 6 | 0 | 6 |  |  | BMXX0 | [10 empty] | 2.6\0.6:
BBD130 | DX06 | DIO1 | 130 | 2 | 6 | 0 | 6 | [13 empty] | 2.6\0.6:
BBD130 | DX06 | DIO1 | 130 | 2 | 6 | 0 | 6 | [13 empty] | 2.6\0.6:
BBD130 | DX06 | DIO1 | 130 | 2 | 6 | 0 | 6 | [13 empty] | 2.6\0.6:
BBD130 | DX06 | DIO1 | 130 | 2 | 6 | 0 | 7 |  |  | BMXX0 | [10 empty] | 2.6\0.7:
BBD130 | DX06 | DIO1 | 130 | 2 | 6 | 0 | 7 | [13 empty] | 2.6\0.7:
BBD130 | DX06 | DIO1 | 130 | 2 | 6 | 0 | 7 | [13 empty] | 2.6\0.7:
BBD130 | DX06 | DIO1 | 130 | 2 | 6 | 0 | 7 | [13 empty] | 2.6\0.7:
BBD130 | DX06 | DIO1 | 130 | 2 | 6 | 0 | 8 |  |  | BMXX0 | [10 empty] | 2.6\0.8:
BBD130 | DX06 | DIO1 | 130 | 2 | 6 | 0 | 8 | [13 empty] | 2.6\0.8:
BBD130 | DX06 | DIO1 | 130 | 2 | 6 | 0 | 8 | [13 empty] | 2.6\0.8:
BBD130 | DX06 | DIO1 | 130 | 2 | 6 | 0 | 8 | [13 empty] | 2.6\0.8:
BBD130 | DX06 | DIO1 | 130 | 2 | 6 | 0 | 9 |  |  | BMXX0 | [10 empty] | 2.6\0.9:
BBD130 | DX06 | DIO1 | 130 | 2 | 6 | 0 | 9 | [13 empty] | 2.6\0.9:
BBD130 | DX06 | DIO1 | 130 | 2 | 6 | 0 | 9 | [13 empty] | 2.6\0.9:
BBD130 | DX06 | DIO1 | 130 | 2 | 6 | 0 | 9 | [13 empty] | 2.6\0.9:
BBD130 | DX06 | DIO1 | 130 | 2 | 6 | 0 | 10 |  |  | BMXX0 | [10 empty] | 2.6\0.10:
BBD130 | DX06 | DIO1 | 130 | 2 | 6 | 0 | 10 | [13 empty] | 2.6\0.10:
BBD130 | DX06 | DIO1 | 130 | 2 | 6 | 0 | 10 | [13 empty] | 2.6\0.10:
BBD130 | DX06 | DIO1 | 130 | 2 | 6 | 0 | 10 | [13 empty] | 2.6\0.10:
BBD130 | DX06 | DIO1 | 130 | 2 | 6 | 0 | 11 |  |  | BMXX0 | [10 empty] | 2.6\0.11:
BBD130 | DX06 | DIO1 | 130 | 2 | 6 | 0 | 11 | [13 empty] | 2.6\0.11:
BBD130 | DX06 | DIO1 | 130 | 2 | 6 | 0 | 11 | [13 empty] | 2.6\0.11:
BBD130 | DX06 | DIO1 | 130 | 2 | 6 | 0 | 11 | [13 empty] | 2.6\0.11:
[10 empty] | * |  |  | BAF130GA01 |  | ROM BIN APRON APRON FEEDER ISOLATION GATE HPU | ROM Bin Apron Feeder Iso. Gate To BSR130DX01 Master Relay |  | SUB LINK | BAF130GA01 |  |  | BR4-2110-E-00176 | 0 | BBDDX06-C1 FROM BSR130DX01 | [7 empty] | F7 | 1 | 2 | 3 | 4
[10 empty] | * |  |  | BDU130FN01LCS01 | SY01 | DUST COLLECTOR FAN | Emergency Stop Relay |  | SUB LINK | BDU130FN01 |  |  | BR4-2110-E-00058 | 0 | [8 empty] | F7 | 5 | 6 | 7 | 8
[10 empty] | * |  |  | BDU130RV01LCS01 | SY01 | DUST COLLECTOR ROTARY VALVE | Emergency Stop Relay |  | SUB LINK | BDU130RV01 |  |  | BR4-2110-E-00059 | 0 | [8 empty] | F7 | 9 | 10 | 11 | 12
[10 empty] | * |  |  | BBD130PP01LCS01 | SY01 | PRIMARY CRUSHER AREA SUMP PUMP | Emergency Stop Relay |  | SUB LINK | BBD130PP01 |  |  | BR4-2110-E-00042 | 0 | BBDDX06-C2 FROM BSR130DX02 | [7 empty] | F7 | 13 | 14 | 15 | 16
[32 empty] | F7 | 17 | 18 | 19 | 20
[32 empty] | F7 | 21 | 22 | 23 | 24
[32 empty] | F7 | 25 | 26 | 27 | 28
[10 empty] | PNOZs4 | Safety Relay |  | BAF130PP05LCS01 | SY01 | ROM BIN APRON APRON FEEDER ISOLATION GATE HPU | Emergency Stop Relay |  | K202 | BAF130PP05 |  |  | BR4-2110-E-00104 | 0 | [8 empty] | F7 | 29 | 30 | 31 | 32
[10 empty] | PNOZs4 | Safety Relay |  | BAF130GA01LCS01 | SY01 | ROM BIN APRON FEEDER ISOLATION GATE | Emergency Stop Relay |  | K220 | BAF130GA01 |  |  | BR4-2110-E-00104 | 0 | [8 empty] | F7 | 33 | 34 | 35 | 36
[10 empty] | * |  |  | BRB13xSY05 | SY05 | ROM BIN AND PRIMARY CRUSHER ROCKBREAKERS | Emergency Shutdown 5 |  |  | BRB13X |  |  | BR4-2110-E-00104 | 0 | [8 empty] | F7 | 37 | 38 | 39 | 40
[10 empty] | PNOZs4 | Safety Relay |  |  |  | BRB13x MASTER (to BRB131PN01 trip) | Emergency Shutdown |  | K253-1 | BRB13x |  |  | BR4-2110-E-00104 | 0 | [8 empty] | F7 | 41 | 42 | 43 | 44
[10 empty] | PNOZs4.1 | Safety Relay |  |  |  | BRB13x MASTER (to BRB133PN01 trip) | Emergency Shutdown |  | K253-2 | BRB13x |  |  | BR4-2110-E-00104 | 0 | [8 empty] | F7 | 45 | 46 | 47 | 48
BCV130DX07 - Primary Crusher Discharge Conveyor - Tail End
EIO node #7 | DX07 | DIO1 | 130 | 2 | 7 | 0
BCV130 | DX07 | DIO1 | 130 | 2 | 7 | 0 |  | Chassis |  | BMEXBP1200
BCV130 | DX07 | DIO1 | 130 | 2 | 7 | 0 |  | Power |  | BMXCPS4022 |  | total |  | spare |  | % spare
BCV130 | DX07 | DIO1 | 130 | 2 | 7 | 0 | 0 | Comms |  | BMECRA31210 | I/O1 | 96 |  | 78 |  | 81.25%
BCV130 | DX07 | DIO1 | 130 | 2 | 7 | 0 | 1 | 0 | BMXFCW303 | BMXDDI3202K | DI | 4 | BCV130DX07 | CB01 |  | 240VAC MD01 Circuit Breaker | Closed | Q106 | BCV130DX07 |  | 2.7\0.1:0 | BR4-2110-E-00106 | 0 |  | D | [6 empty] | F1 |  | 1
BCV130 | DX07 | DIO1 | 130 | 2 | 7 | 0 | 1 | 1 |  |  | DI | 4 | BCV130DX07 | VDC01 |  | 24VDC DIO1 Output Control Supply | Healthy | Q143 | BCV130DX07 |  | 2.7\0.1:1 | BR4-2110-E-00106 | 0 |  | D | [6 empty] | F1 |  | 2
BCV130 | DX07 | DIO1 | 130 | 2 | 7 | 0 | 1 | 2 |  |  | DI | 4 | BCV130DX07 | VDC02 |  | 24VDC GW1 Control Supply | Healthy | Q157 | BCV130DX07 |  | 2.7\0.1:2 | BR4-2110-E-00106 | 0 |  | D | [6 empty] | F1 |  | 3
BCV130 | DX07 | DIO1 | 130 | 2 | 7 | 0 | 1 | 3 |  |  | DI | 4 | BCV130DX07 | VDC03 |  | 24VDC Instrument Supply | Healthy | Q164 | BCV130DX07 |  | 2.7\0.1:3 | BR4-2110-E-00106 | 0 |  | D | [6 empty] | F1 |  | 4
BCV130 | DX07 | DIO1 | 130 | 2 | 7 | 0 | 1 | 4 |  |  | DI | 4 | BCV130DX07 | VDC04 |  | 24VDC Transmitter Supply | Healthy | Q168 | BCV130DX07 |  | 2.7\0.1:4 | BR4-2110-E-00106 | 0 |  | D | [6 empty] | F1 |  | 5
BCV130 | DX07 | DIO1 | 130 | 2 | 7 | 0 | 1 | 5 |  |  | DI | 4 | BCV130DX07 | VDC05 |  | 24VDC BCV1310DX07 PLC Control Supply | Healthy | Q172 | BCV130DX07 |  | 2.7\0.1:5 | BR4-2110-E-00106 | 0 |  | D | [6 empty] | F1 |  | 6
BCV130 | DX07 | DIO1 | 130 | 2 | 7 | 0 | 1 | 6 |  |  | DI | 4 | BCV130DX07 | VDC06 |  | BCV130WM01 Control Supply | Healthy | Q176 | BCV130DX07 |  | 2.7\0.1:6 | BR4-2110-E-00106 | 0 |  | D | [6 empty] | F1 |  | 7
BCV130 | DX07 | DIO1 | 130 | 2 | 7 | 0 | 1 | 7 |  |  | DI | 4 | BCV130DX07 | VDC07 |  | BCV130MD01 Control Supply | Healthy | Q180 | BCV130DX07 |  | 2.7\0.1:7 | BR4-2110-E-00106 | 0 |  | D | [6 empty] | F1 |  | 8
BCV130 | DX07 | DIO1 | 130 | 2 | 7 | 0 | 1 | 8 |  |  | DI | 4 | BCV130DX07 | VDC08 |  | BCV130MO01AX01 Control Supply | Healthy | Q184 | BCV130DX07 |  | 2.7\0.1:8 | BR4-2110-E-00106 | 0 |  | D | [6 empty] | F1 |  | 9
BCV130 | DX07 | DIO1 | 130 | 2 | 7 | 0 | 1 | 9 |  |  | DI | 4 | BCV130DX07 | VDC09 |  | BCV130XT01PN01 Control Supply | Healthy | Q188 | BCV130DX07 |  | 2.7\0.1:9 | BR4-2110-E-00106 | 0 |  | D | [6 empty] | F1 |  | 10
BCV130 | DX07 | DIO1 | 130 | 2 | 7 | 0 | 1 | 10 |  |  | DI | 4 | BCV130DX07 | VDC10 |  | BCV130AIT01 Control Supply | Healthy | Q192 | BCV130DX07 |  | 2.7\0.1:10 | BR4-2110-E-00106 | 0 |  | D | [6 empty] | F1 |  | 11
BCV130 | DX07 | DIO1 | 130 | 2 | 7 | 0 | 1 | 11 |  |  | DI | 4 | BCV130DX07 | VDC11 |  | Spare Control Supply | Healthy | Q196 | BCV130DX07 |  | 2.7\0.1:11 | BR4-2110-E-00106 | 0 |  | D | [6 empty] | F1 |  | 12
BCV130 | DX07 | DIO1 | 130 | 2 | 7 | 0 | 1 | 12 |  |  | DI | 7 | BCV130DX07 | CB02 |  | 240VAC XT01 Circuit Breaker | Closed | Q108 | BCV130DX07 |  | 2.7\0.1:12 | BR4-2110-E-00106 | 0 |  | S | [6 empty] | F1 |  | 13
BCV130 | DX07 | DIO1 | 130 | 2 | 7 | 0 | 1 | 13 |  |  | DI | [9 empty] | 2.7\0.1:13 |  |  |  | S | [6 empty] | F1 |  | 14
BCV130 | DX07 | DIO1 | 130 | 2 | 7 | 0 | 1 | 14 |  |  | DI | [9 empty] | 2.7\0.1:14 |  |  |  | S | [6 empty] | F1 |  | 15
BCV130 | DX07 | DIO1 | 130 | 2 | 7 | 0 | 1 | 15 |  |  | DI | [9 empty] | 2.7\0.1:15 |  |  |  | S | [6 empty] | F1 |  | 16
BCV130 | DX07 | DIO1 | 130 | 2 | 7 | 0 | 1 | 16 |  |  | DI | 4 | BCV130PWS09 | PWS09 | PRIMARY CRUSHING DISCHARGE CONVEYOR | Pullwire Switch 9 | Healthy | K206 | BCV130 |  | 2.7\0.1:16 | BR4-2110-E-00107 | 0 |  | D | [6 empty] | F1 | 17 | 18
BCV130 | DX07 | DIO1 | 130 | 2 | 7 | 0 | 1 | 17 |  |  | DI | 4 | BCV130PWS10 | PWS10 | PRIMARY CRUSHING DISCHARGE CONVEYOR | Pullwire Switch 10 | Healthy | K214 | BCV130 |  | 2.7\0.1:17 | BR4-2110-E-00107 | 0 |  | D | [6 empty] | F1 | 19 | 20
BCV130 | DX07 | DIO1 | 130 | 2 | 7 | 0 | 1 | 18 |  |  | DI | 4 | BCV130PWS11 | PWS11 | PRIMARY CRUSHING DISCHARGE CONVEYOR | Pullwire Switch 11 | Healthy | K225 | BCV130 |  | 2.7\0.1:18 | BR4-2110-E-00107 | 0 |  | D | [6 empty] | F1 | 21 | 22
BCV130 | DX07 | DIO1 | 130 | 2 | 7 | 0 | 1 | 19 |  |  | DI | 4 | BCV130PWS12 | PWS12 | PRIMARY CRUSHING DISCHARGE CONVEYOR | Pullwire Switch 12 | Healthy | K236 | BCV130 |  | 2.7\0.1:19 | BR4-2110-E-00107 | 0 |  | D | [6 empty] | F1 | 23 | 24
BCV130 | DX07 | DIO1 | 130 | 2 | 7 | 0 | 1 | 20 |  |  | DI | 4 | BCV130PWS13 | PWS13 | PRIMARY CRUSHING DISCHARGE CONVEYOR | Pullwire Switch 13 | Healthy | K253 | BCV130 |  | 2.7\0.1:20 | BR4-2110-E-00107 | 0 |  | D | [6 empty] | F1 | 25 | 26
BCV130 | DX07 | DIO1 | 130 | 2 | 7 | 0 | 1 | 21 |  |  | DI | 4 | BCV130PWS14 | PWS14 | PRIMARY CRUSHING DISCHARGE CONVEYOR | Pullwire Switch 14 | Healthy | K264 | BCV130 |  | 2.7\0.1:21 | BR4-2110-E-00107 | 0 |  | D | [6 empty] | F1 | 27 | 28
BCV130 | DX07 | DIO1 | 130 | 2 | 7 | 0 | 1 | 22 |  |  | DI | 4 | BCV130BDS05 | BDS05 | PRIMARY CRUSHING DISCHARGE CONVEYOR | Belt Drift Switch 5 | Healthy |  | BCV130 |  | 2.7\0.1:22 | BR4-2110-E-00108 | 0 |  | S | [6 empty] | F1 | 29 | 30
BCV130 | DX07 | DIO1 | 130 | 2 | 7 | 0 | 1 | 23 |  |  | DI | 4 | BCV130BDS06 | BDS06 | PRIMARY CRUSHING DISCHARGE CONVEYOR | Belt Drift Switch 6 | Healthy |  | BCV130 |  | 2.7\0.1:23 | BR4-2110-E-00108 | 0 |  | S | [6 empty] | F1 | 31 | 32
BCV130 | DX07 | DIO1 | 130 | 2 | 7 | 0 | 1 | 24 |  |  | DI | 4 | BCV130BDS07 | BDS07 | PRIMARY CRUSHING DISCHARGE CONVEYOR | Belt Drift Switch 7 | Healthy |  | BCV130 |  | 2.7\0.1:24 | BR4-2110-E-00108 | 0 |  | S | [6 empty] | F1 | 33 | 34
BCV130 | DX07 | DIO1 | 130 | 2 | 7 | 0 | 1 | 25 |  |  | DI | 4 | BCV130BDS08 | BDS08 | PRIMARY CRUSHING DISCHARGE CONVEYOR | Belt Drift Switch 8 | Healthy |  | BCV130 |  | 2.7\0.1:25 | BR4-2110-E-00108 | 0 |  | S | [6 empty] | F1 | 35 | 36
BCV130 | DX07 | DIO1 | 130 | 2 | 7 | 0 | 1 | 26 |  |  | DI | 4 | BCV130BRS01 | BRS01 | PRIMARY CRUSHING DISCHARGE CONVEYOR | Belt Rip Switch 1 | Healthy |  | BCV130 |  | 2.7\0.1:26 | BR4-2110-E-00108 | 0 |  | S | [6 empty] | F1 | 37 | 38
BCV130 | DX07 | DIO1 | 130 | 2 | 7 | 0 | 1 | 27 |  |  | DI | 4 | BCV130BRS02 | BRS02 | PRIMARY CRUSHING DISCHARGE CONVEYOR | Belt Rip Switch 2 | Healthy |  | BCV130 |  | 2.7\0.1:27 | BR4-2110-E-00108 | 0 |  | S | [6 empty] | F1 | 39 | 40
BCV130 | DX07 | DIO1 | 130 | 2 | 7 | 0 | 1 | 28 |  |  | DI | 4 | BCV130BRS03 | BRS03 | PRIMARY CRUSHING DISCHARGE CONVEYOR | Belt Rip Switch 3 | Healthy |  | BCV130 |  | 2.7\0.1:28 | BR4-2110-E-00108 | 0 |  | S | [6 empty] | F1 | 41 | 42
BCV130 | DX07 | DIO1 | 130 | 2 | 7 | 0 | 1 | 29 |  |  | DI | [9 empty] | 2.7\0.1:29 |  |  |  | S | [6 empty] | F1 | 43 | 44
BCV130 | DX07 | DIO1 | 130 | 2 | 7 | 0 | 1 | 30 |  |  | DI | [9 empty] | 2.7\0.1:30 |  |  |  | S | [6 empty] | F1 | 45 | 46
BCV130 | DX07 | DIO1 | 130 | 2 | 7 | 0 | 1 | 31 |  |  | DI | [9 empty] | 2.7\0.1:31 |  |  |  | S | [6 empty] | F1 | 47 | 48
BCV130 | DX07 | DIO1 | 130 | 2 | 7 | 0 | 2 | 0 | BMXFCW303 | BMXDDI3202K | DI | 4 | BCV130LCS02 | STT01 | PRIMARY CRUSHING DISCHARGE CONVEYOR | Start Pushbutton | Activated | STT01 | BCV130 |  | 2.7\0.2:0 | BR4-2110-E-00108 | 0 |  | S | [6 empty] | F2 | 1 | 2
BCV130 | DX07 | DIO1 | 130 | 2 | 7 | 0 | 2 | 1 |  |  | DI | 4 | BCV130LCS02 | STP01 | PRIMARY CRUSHING DISCHARGE CONVEYOR | Stop Pushbutton | Activated | STP01 | BCV130 |  | 2.7\0.2:1 | BR4-2110-E-00108 | 0 |  | S | [6 empty] | F2 | 3 | 4
BCV130 | DX07 | DIO1 | 130 | 2 | 7 | 0 | 2 | 2 |  |  | DI | 4 | BCV130LCS02 | SY01 | PRIMARY CRUSHING DISCHARGE CONVEYOR | Emergency Stop Relay | Healthy | K275 | BCV130 |  | 2.7\0.2:2 | BR4-2110-E-00107 | 0 |  | D | [6 empty] | F2 | 5 | 6
BCV130 | DX07 | DIO1 | 130 | 2 | 7 | 0 | 2 | 3 |  |  | DI | [9 empty] | 2.7\0.2:3 |  |  |  | S | [6 empty] | F2 | 7 | 8
BCV130 | DX07 | DIO1 | 130 | 2 | 7 | 0 | 2 | 4 |  |  | DI | 4 | BCV130FT04 | FQ04 | PRIMARY CRUSHING DISCHARGE CONVEYOR BULK ORE CONDITIONING | Flow Totaliser Pulse | Active |  | BCV130 |  | 2.7\0.2:4 | BR4-2110-E-00108 | 0 |  | S | [6 empty] | F2 | 9 | 10
BCV130 | DX07 | DIO1 | 130 | 2 | 7 | 0 | 2 | 5 |  |  | DI | [9 empty] | 2.7\0.2:5 |  |  |  | S | [6 empty] | F2 | 11 | 12
BCV130 | DX07 | DIO1 | 130 | 2 | 7 | 0 | 2 | 6 |  |  | DI | 4 | BCV130LCS03 | SY01 | PRIMARY CRUSHER DISCHARGE CONVEYOR | Emergency Stop Relay | Healthy | K286 | BCV130 |  | 2.7\0.2:6 | BR4-2110-E-00107 | 0 |  | D | [6 empty] | F2 | 13 | 14
BCV130 | DX07 | DIO1 | 130 | 2 | 7 | 0 | 2 | 7 |  |  | DI | 7 | BCV130AIT01ZS01 | ZS01 | BELT PROFILE SCANNER POSITION SWITCH |  | In Position |  | BCV130 |  | 2.7\0.2:7 | BR4-2110-E-00108 | 1 |  | S | [6 empty] | F2 | 15 | 16
BCV130 | DX07 | DIO1 | 130 | 2 | 7 | 0 | 2 | 8 |  |  | DI | [9 empty] | 2.7\0.2:8 |  |  |  | S | [6 empty] | F2 | 17 | 18
BCV130 | DX07 | DIO1 | 130 | 2 | 7 | 0 | 2 | 9 |  |  | DI | [9 empty] | 2.7\0.2:9 |  |  |  | S | [6 empty] | F2 | 19 | 20
BCV130 | DX07 | DIO1 | 130 | 2 | 7 | 0 | 2 | 10 |  |  | DI | [9 empty] | 2.7\0.2:10 |  |  |  | S | [6 empty] | F2 | 21 | 22
BCV130 | DX07 | DIO1 | 130 | 2 | 7 | 0 | 2 | 11 |  |  | DI | [9 empty] | 2.7\0.2:11 |  |  |  | S | [6 empty] | F2 | 23 | 24
BCV130 | DX07 | DIO1 | 130 | 2 | 7 | 0 | 2 | 12 |  |  | DI | [9 empty] | 2.7\0.2:12 |  |  |  | S | [6 empty] | F2 | 25 | 26
BCV130 | DX07 | DIO1 | 130 | 2 | 7 | 0 | 2 | 13 |  |  | DI | [9 empty] | 2.7\0.2:13 |  |  |  | S | [6 empty] | F2 | 27 | 28
BCV130 | DX07 | DIO1 | 130 | 2 | 7 | 0 | 2 | 14 |  |  | DI | [9 empty] | 2.7\0.2:14 |  |  |  | S | [6 empty] | F2 | 29 | 30
BCV130 | DX07 | DIO1 | 130 | 2 | 7 | 0 | 2 | 15 |  |  | DI | [9 empty] | 2.7\0.2:15 |  |  |  | S | [6 empty] | F2 | 31 | 32
BCV130 | DX07 | DIO1 | 130 | 2 | 7 | 0 | 2 | 16 |  |  | DI | 7 | BCV130MD01 | XS01 | Metal | Healthy |  | BCV130MD01 |  |  | 2.7\0.2:16 | BR4-2110-E-00108 |  |  | S
BCV130 | DX07 | DIO1 | 130 | 2 | 7 | 0 | 2 | 17 |  |  | DI | 7 | BCV130MD01 | XS02 | Unit | Detected |  | BCV130MD01 |  |  | 2.7\0.2:17 | BR4-2110-E-00108 |  |  | S
BCV130 | DX07 | DIO1 | 130 | 2 | 7 | 0 | 2 | 18 |  |  | DI | 7 | BCV130MD01 | XS03 | Unit | Bypassed |  | BCV130MD01 |  |  | 2.7\0.2:18 | BR4-2110-E-00108 |  |  | S
BCV130 | DX07 | DIO1 | 130 | 2 | 7 | 0 | 2 | 19 |  |  | DI | [9 empty] | 2.7\0.2:19 |  |  |  | S
BCV130 | DX07 | DIO1 | 130 | 2 | 7 | 0 | 2 | 20 |  |  | DI | [9 empty] | 2.7\0.2:20 |  |  |  | S | [6 empty] | F3 | 9 | 10
BCV130 | DX07 | DIO1 | 130 | 2 | 7 | 0 | 2 | 21 |  |  | DI | [9 empty] | 2.7\0.2:21 |  |  |  | S | [6 empty] | F3 | 11 | 12
BCV130 | DX07 | DIO1 | 130 | 2 | 7 | 0 | 2 | 22 |  |  | DI | [9 empty] | 2.7\0.2:22 |  |  |  | S | [6 empty] | F3 | 13 | 14
BCV130 | DX07 | DIO1 | 130 | 2 | 7 | 0 | 2 | 23 |  |  | DI | [9 empty] | 2.7\0.2:23 |  |  |  | S | [6 empty] | F3 | 15 | 16
BCV130 | DX07 | DIO1 | 130 | 2 | 7 | 0 | 2 | 24 |  |  | DI | [9 empty] | 2.7\0.2:24 |  |  |  | S | [6 empty] | F3 | 17 | 18
BCV130 | DX07 | DIO1 | 130 | 2 | 7 | 0 | 2 | 25 |  |  | DI | [9 empty] | 2.7\0.2:25 |  |  |  | S | [6 empty] | F3 | 19 | 20
BCV130 | DX07 | DIO1 | 130 | 2 | 7 | 0 | 2 | 26 |  |  | DI | [9 empty] | 2.7\0.2:26 |  |  |  | S | [6 empty] | F3 | 21 | 22
BCV130 | DX07 | DIO1 | 130 | 2 | 7 | 0 | 2 | 27 |  |  | DI | [9 empty] | 2.7\0.2:27 |  |  |  | S | [6 empty] | F3 | 23 | 24
BCV130 | DX07 | DIO1 | 130 | 2 | 7 | 0 | 2 | 28 |  |  | DI | [9 empty] | 2.7\0.2:28 |  |  |  | S | [6 empty] | F3 | 25 | 26
BCV130 | DX07 | DIO1 | 130 | 2 | 7 | 0 | 2 | 29 |  |  | DI | [9 empty] | 2.7\0.2:29 |  |  |  | S | [6 empty] | F3 | 27 | 28
BCV130 | DX07 | DIO1 | 130 | 2 | 7 | 0 | 2 | 30 |  |  | DI | [9 empty] | 2.7\0.2:30 |  |  |  | S | [6 empty] | F3 | 29 | 30
BCV130 | DX07 | DIO1 | 130 | 2 | 7 | 0 | 2 | 31 |  |  | DI | [9 empty] | 2.7\0.2:31 |  |  |  | S | [6 empty] | F3 | 31 | 32
BCV130 | DX07 | DIO1 | 130 | 2 | 7 | 0 | 3 | 0 | BMXFTB2010 | BMXDDO1602 | DO | 4 | BCV130YA04 | YA04 | PRIMARY CRUSHING DISCHARGE CONVEYOR | Start Up Warning |  |  | BCV130 |  | 2.7\0.3:0 | BR4-2110-E-00108 | 0 |  | S | [6 empty] | F5 | 1 | 2
BCV130 | DX07 | DIO1 | 130 | 2 | 7 | 0 | 3 | 1 |  |  | DO | 4 | BCV130SV04 | SV04 | PRIMARY CRUSHING DISCHARGE CONVEYOR | Bulk Ore Conditioning Solenoid 4 |  |  | BCV130 |  | 2.7\0.3:1 | BR4-2110-E-00108 | 0 |  | S | [6 empty] | F5 | 3 | 4
BCV130 | DX07 | DIO1 | 130 | 2 | 7 | 0 | 3 | 2 |  |  | DO | 4 | BCV130SV05 | SV05 | PRIMARY CRUSHING DISCHARGE CONVEYOR | Bulk Ore Conditioning Solenoid 5 |  |  | BCV130 |  | 2.7\0.3:2 | BR4-2110-E-00108 | 0 |  | S | [6 empty] | F5 | 5 | 6
BCV130 | DX07 | DIO1 | 130 | 2 | 7 | 0 | 3 | 3 |  |  | DO | 4 | BCV130SV06 | SV06 | PRIMARY CRUSHING DISCHARGE CONVEYOR | Bulk Ore Conditioning Solenoid 6 |  |  | BCV130 |  | 2.7\0.3:3 | BR4-2110-E-00108 | 0 |  | S | [6 empty] | F5 | 7 | 8
BCV130 | DX07 | DIO1 | 130 | 2 | 7 | 0 | 3 | 4 |  |  | DO | [9 empty] | 2.7\0.3:4 |  |  |  | S | [6 empty] | F5 | 9 | 10
BCV130 | DX07 | DIO1 | 130 | 2 | 7 | 0 | 3 | 5 |  |  | DO | [9 empty] | 2.7\0.3:5 |  |  |  | S | [6 empty] | F5 | 11 | 12
BCV130 | DX07 | DIO1 | 130 | 2 | 7 | 0 | 3 | 6 |  |  | DO | [9 empty] | 2.7\0.3:6 |  |  |  | S | [6 empty] | F5 | 13 | 14
BCV130 | DX07 | DIO1 | 130 | 2 | 7 | 0 | 3 | 7 |  |  | DO | [9 empty] | 2.7\0.3:7 |  |  |  | S | [6 empty] | F5 | 15 | 16
BCV130 | DX07 | DIO1 | 130 | 2 | 7 | 0 | 3 | 8 |  |  | DO | [9 empty] | 2.7\0.3:8 |  |  |  | S | [6 empty] | F5 | 17 | 18
BCV130 | DX07 | DIO1 | 130 | 2 | 7 | 0 | 3 | 9 |  |  | DO | [9 empty] | 2.7\0.3:9 |  |  |  | S | [6 empty] | F5 | 19 | 20
BCV130 | DX07 | DIO1 | 130 | 2 | 7 | 0 | 3 | 10 |  |  | DO | [9 empty] | 2.7\0.3:10 |  |  |  | S | [6 empty] | F5 | 21 | 22
BCV130 | DX07 | DIO1 | 130 | 2 | 7 | 0 | 3 | 11 |  |  | DO | [9 empty] | 2.7\0.3:11 |  |  |  | S | [6 empty] | F5 | 23 | 24
BCV130 | DX07 | DIO1 | 130 | 2 | 7 | 0 | 3 | 12 |  |  | DO | [9 empty] | 2.7\0.3:12 |  |  |  | S | [6 empty] | F5 | 25 | 26
BCV130 | DX07 | DIO1 | 130 | 2 | 7 | 0 | 3 | 13 |  |  | DO | [9 empty] | 2.7\0.3:13 |  |  |  | S | [6 empty] | F5 | 27 | 28
BCV130 | DX07 | DIO1 | 130 | 2 | 7 | 0 | 3 | 14 |  |  | DO | [9 empty] | 2.7\0.3:14 |  |  |  | S | [6 empty] | F5 | 29 | 30
BCV130 | DX07 | DIO1 | 130 | 2 | 7 | 0 | 3 | 15 |  |  | DO | [9 empty] | 2.7\0.3:15 |  |  |  | S | [6 empty] | F5 | 31 | 32
BCV130 | DX07 | DIO1 | 130 | 2 | 7 | 0 | 4 | 0 | BMXFTW301S | BMEAHI0812 | AI | 4 | BCV130FT04 | FT04 | PRIMARY CRUSHING DISCHARGE CONVEYOR BULK ORE CONDITIONING | Flow Rate |  | m3/h | BCV130 | REAL | 2.7\0.4:0 | BR4-2110-E-00108 | 0 |  | S |  | 0 | 10 | 0 | 10 | #.# EU | F5 | 33 | 34
BCV130 | DX07 | DIO1 | 130 | 2 | 7 | 0 | 4 | 1 |  |  | AI | [9 empty] | 2.7\0.4:1 |  |  |  | S | [6 empty] | F5 | 35 | 36
BCV130 | DX07 | DIO1 | 130 | 2 | 7 | 0 | 4 | 2 |  |  | AI | [9 empty] | 2.7\0.4:2 |  |  |  | S | [6 empty] | F5 | 37 | 38
BCV130 | DX07 | DIO1 | 130 | 2 | 7 | 0 | 4 | 3 |  |  | AI | [9 empty] | 2.7\0.4:3 |  |  |  | S | [6 empty] | F5 | 39 | 40
BCV130 | DX07 | DIO1 | 130 | 2 | 7 | 0 | 4 | 4 |  |  | AI | [9 empty] | 2.7\0.4:4 |  |  |  | S | [6 empty] | F5 | 41 | 42
BCV130 | DX07 | DIO1 | 130 | 2 | 7 | 0 | 4 | 5 |  |  | AI | [9 empty] | 2.7\0.4:5 |  |  |  | S | [6 empty] | F5 | 43 | 44
BCV130 | DX07 | DIO1 | 130 | 2 | 7 | 0 | 4 | 6 |  |  | AI | [9 empty] | 2.7\0.4:6 |  |  |  | S | [6 empty] | F5 | 45 | 46
BCV130 | DX07 | DIO1 | 130 | 2 | 7 | 0 | 4 | 7 |  |  | AI | [9 empty] | 2.7\0.4:7 |  |  |  | S | [6 empty] | F5 | 47 | 48
BCV130 | DX07 | DIO1 | 130 | 2 | 7 | 0 | 5 | 0 | BMXFTB2010 | BMXEHC0800 | HSCI | 4 | BCV130SS01 | SS01 | PRIMARY CRUSHING DISCHARGE CONVEYOR | Underspeed Pulse |  |  | BCV130 |  | 2.7\0.5:0 | BR4-2110-E-00108 | 0 |  | S | [6 empty] | F2 | 37 | 38
BCV130 | DX07 | DIO1 | 130 | 2 | 7 | 0 | 5 | 1 |  |  | HSCI | 4 | BCV130ZQ01 | ZQ01 | PRIMARY CRUSHING DISCHARGE CONVEYOR | Distance Pulse |  |  | BCV130 |  | 2.7\0.5:1 | BR4-2110-E-00108 | 0 |  | S | [6 empty] | F2 | 39 | 40
BCV130 | DX07 | DIO1 | 130 | 2 | 7 | 0 | 5 | 2 |  |  | HSCI | [9 empty] | 2.7\0.5:2 |  |  |  | S | [6 empty] | F2 | 41 | 42
BCV130 | DX07 | DIO1 | 130 | 2 | 7 | 0 | 5 | 3 |  |  | HSCI | [9 empty] | 2.7\0.5:3 |  |  |  | S | [6 empty] | F2 | 43 | 44
BCV130 | DX07 | DIO1 | 130 | 2 | 7 | 0 | 5 | 4 |  |  | HSCI | [9 empty] | 2.7\0.5:4 |  |  |  | S | [6 empty] | F2 | 45 | 46
BCV130 | DX07 | DIO1 | 130 | 2 | 7 | 0 | 5 | 5 |  |  | HSCI | [9 empty] | 2.7\0.5:5 |  |  |  | S | [6 empty] | F2 | 47 | 48
BCV130 | DX07 | DIO1 | 130 | 2 | 7 | 0 | 5 | 6 |  |  | HSCI | [9 empty] | 2.7\0.5:6 |  |  |  | S | [6 empty] | F2 | 49 | 50
BCV130 | DX07 | DIO1 | 130 | 2 | 7 | 0 | 5 | 7 |  |  | HSCI | [9 empty] | 2.7\0.5:7 |  |  |  | S | [6 empty] | F2 | 51 | 52
BCV130 | DX07 | DIO1 | 130 | 2 | 7 | 0 | 6 |  |  | BMXX0 |  | 0 | [8 empty] | 2.7\0.6:
BCV130 | DX07 | DIO1 | 130 | 2 | 7 | 0 | 6 |  |  |  |  | 0 | [8 empty] | 2.7\0.6:
BCV130 | DX07 | DIO1 | 130 | 2 | 7 | 0 | 6 |  |  |  |  | 0 | [8 empty] | 2.7\0.6:
BCV130 | DX07 | DIO1 | 130 | 2 | 7 | 0 | 6 |  |  |  |  | 0 | [8 empty] | 2.7\0.6:
BCV130 | DX07 | DIO1 | 130 | 2 | 7 | 0 | 7 |  |  | BMXX0 |  | 0 | [8 empty] | 2.7\0.7:
BCV130 | DX07 | DIO1 | 130 | 2 | 7 | 0 | 7 |  |  |  |  | 0 | [8 empty] | 2.7\0.7:
BCV130 | DX07 | DIO1 | 130 | 2 | 7 | 0 | 7 |  |  |  |  | 0 | [8 empty] | 2.7\0.7:
BCV130 | DX07 | DIO1 | 130 | 2 | 7 | 0 | 7 |  |  |  |  | 0 | [8 empty] | 2.7\0.7:
BCV130 | DX07 | DIO1 | 130 | 2 | 7 | 0 | 8 |  |  | BMXX0 |  | 0 | [8 empty] | 2.7\0.8:
BCV130 | DX07 | DIO1 | 130 | 2 | 7 | 0 | 8 |  |  |  |  | 0 | [8 empty] | 2.7\0.8:
BCV130 | DX07 | DIO1 | 130 | 2 | 7 | 0 | 8 |  |  |  |  | 0 | [8 empty] | 2.7\0.8:
BCV130 | DX07 | DIO1 | 130 | 2 | 7 | 0 | 8 |  |  |  |  | 0 | [8 empty] | 2.7\0.8:
BCV130 | DX07 | DIO1 | 130 | 2 | 7 | 0 | 9 |  |  | BMXX0 |  | 0 | [8 empty] | 2.7\0.9:
BCV130 | DX07 | DIO1 | 130 | 2 | 7 | 0 | 9 |  |  |  |  | 0 | [8 empty] | 2.7\0.9:
BCV130 | DX07 | DIO1 | 130 | 2 | 7 | 0 | 9 |  |  |  |  | 0 | [8 empty] | 2.7\0.9:
BCV130 | DX07 | DIO1 | 130 | 2 | 7 | 0 | 9 |  |  |  |  | 0 | [8 empty] | 2.7\0.9:
BCV130 | DX07 | DIO1 | 130 | 2 | 7 | 0 | 10 |  |  | BMXX0 |  | 0 | [8 empty] | 2.7\0.10:
BCV130 | DX07 | DIO1 | 130 | 2 | 7 | 0 | 10 |  |  |  |  | 0 | [8 empty] | 2.7\0.10:
BCV130 | DX07 | DIO1 | 130 | 2 | 7 | 0 | 10 |  |  |  |  | 0 | [8 empty] | 2.7\0.10:
BCV130 | DX07 | DIO1 | 130 | 2 | 7 | 0 | 10 |  |  |  |  | 0 | [8 empty] | 2.7\0.10:
BCV130 | DX07 | DIO1 | 130 | 2 | 7 | 0 | 11 |  |  | BMXX0 |  | 0 | [8 empty] | 2.7\0.11:
BCV130 | DX07 | DIO1 | 130 | 2 | 7 | 0 | 11 |  |  |  |  | 0 | [8 empty] | 2.7\0.11:
BCV130 | DX07 | DIO1 | 130 | 2 | 7 | 0 | 11 |  |  |  |  | 0 | [8 empty] | 2.7\0.11:
BCV130 | DX07 | DIO1 | 130 | 2 | 7 | 0 | 11 |  |  |  |  | 0 | [8 empty] | 2.7\0.11:
[16 empty] | Safety Relay (To Sumation Relay Bsr130Dx02) |  | K403 | BCV130 |  |  | BR4-2110-E-00122 | 0 | [8 empty] | F7 | 1 | 2 | 3 | 4
[32 empty] | F7 | 5 | 6 | 7 | 8
[32 empty] | F7 | 9 | 10 | 11 | 12
[10 empty] | PNOZs4 | Safety Relay | 1 | BCV130PWS09 | PWS09 | PRIMARY CRUSHING DISCHARGE CONVEYOR | Pullwire Switch 9 | Healthy | K203 | BCV130 |  |  | BR4-2110-E-00107 | 0 | [8 empty] | F7 | 13 | 14 | 15 | 16
[10 empty] | PNOZs4 | Safety Relay | 1 | BCV130PWS10 | PWS10 | PRIMARY CRUSHING DISCHARGE CONVEYOR | Pullwire Switch 10 | Healthy | K214 | BCV130 |  |  | BR4-2110-E-00107 | 0 | [8 empty] | F7 | 17 | 18 | 19 | 20
[10 empty] | PNOZs4 | Safety Relay | 1 | BCV130PWS11 | PWS11 | PRIMARY CRUSHING DISCHARGE CONVEYOR | Pullwire Switch 11 | Healthy | K225 | BCV130 |  |  | BR4-2110-E-00107 | 0 | [8 empty] | F7 | 21 | 22 | 23 | 24
[10 empty] | PNOZs4 | Safety Relay | 1 | BCV130PWS12 | PWS12 | PRIMARY CRUSHING DISCHARGE CONVEYOR | Pullwire Switch 12 | Healthy | K236 | BCV130 |  |  | BR4-2110-E-00107 | 0 | [8 empty] | F7 | 25 | 26 | 27 | 28
[10 empty] | PNOZs4 | Safety Relay | 1 | BCV130PWS13 | PWS13 | PRIMARY CRUSHING DISCHARGE CONVEYOR | Pullwire Switch 13 | Healthy | K253 | BCV130 |  |  | BR4-2110-E-00107 | 0 | [8 empty] | F7 | 29 | 30 | 31 | 32
[10 empty] | PNOZs4 | Safety Relay | 1 | BCV130PWS14 | PWS14 | PRIMARY CRUSHING DISCHARGE CONVEYOR | Pullwire Switch 14 | Healthy | K264 | BCV130 |  |  | BR4-2110-E-00107 | 0 | [8 empty] | F7 | 33 | 34 | 35 | 36
[10 empty] | PNOZs4 | Safety Relay | 1 | BCV130LCS02 | LOS01 | PRIMARY CRUSHING DISCHARGE CONVEYOR | Emergency Stop Relay | Healthy | K275 | BCV130 |  |  | BR4-2110-E-00107 | 0 | [8 empty] | F7 | 37 | 38 | 39 | 40
[10 empty] | PNOZs4 | Safety Relay | 1 | BCV130LCS03 | LOS01 | PRIMARY CRUSHING DISCHARGE CONVEYOR | Emergency Stop Relay | Healthy | K286 | BCV130 |  |  | BR4-2110-E-00107 | 0 | [8 empty] | F7 | 41 | 42 | 43 | 44
[32 empty] | F7 | 45 | 46 | 47 | 48
BCV130DX08 - Primary Crusher Discharge Conveyor - Magnet
EIO node #8 | DX08 | DIO1 | 130 | 2 | 8 | 0
BCV130 | DX08 | DIO1 | 130 | 2 | 8 | 0 |  | Chassis |  | BMEXBP1200
BCV130 | DX08 | DIO1 | 130 | 2 | 8 | 0 |  | Power |  | BMXCPS4022 |  | total |  | spare |  | % spare
BCV130 | DX08 | DIO1 | 130 | 2 | 8 | 0 | 0 | Comms |  | BMECRA31210 | I/O1 | 104 |  | 53 |  | 50.96%
BCV130 | DX08 | DIO1 | 130 | 2 | 8 | 0 | 1 | 0 | BMXFCW303 | BMXDDI3202K | DI | 4 | BCV130DX08 | CB01 |  | 240VAC BCV130MD02 Circuit Breaker | Closed | Q106 | BCV130DX08 |  | 2.8\0.1:0 | BR4-2110-E-00109 | 0 |  | D | [6 empty] | F1 |  | 1
BCV130 | DX08 | DIO1 | 130 | 2 | 8 | 0 | 1 | 1 |  |  | DI | 4 | BCV130DX08 | VDC01 |  | 24VDC DIO1 Output Control Supply | Healthy | Q143 | BCV130DX08 |  | 2.8\0.1:1 | BR4-2110-E-00109 | 0 |  | D | [6 empty] | F1 |  | 2
BCV130 | DX08 | DIO1 | 130 | 2 | 8 | 0 | 1 | 2 |  |  | DI | 4 | BCV130DX08 | VDC02 |  | 24VDC GW1 Control Supply | Healthy | Q157 | BCV130DX08 |  | 2.8\0.1:2 | BR4-2110-E-00109 | 0 |  | D | [6 empty] | F1 |  | 3
BCV130 | DX08 | DIO1 | 130 | 2 | 8 | 0 | 1 | 3 |  |  | DI | 4 | BCV130DX08 | VDC03 |  | 24VDC Instrument Supply | Healthy | Q164 | BCV130DX08 |  | 2.8\0.1:3 | BR4-2110-E-00109 | 0 |  | D | [6 empty] | F1 |  | 4
BCV130 | DX08 | DIO1 | 130 | 2 | 8 | 0 | 1 | 4 |  |  | DI | 4 | BCV130DX08 | VDC04 |  | 24VDC Transmitter Supply | Healthy | Q168 | BCV130DX08 |  | 2.8\0.1:4 | BR4-2110-E-00109 | 0 |  | D | [6 empty] | F1 |  | 5
BCV130 | DX08 | DIO1 | 130 | 2 | 8 | 0 | 1 | 5 |  |  | DI | 4 | BCV130DX08 | VDC05 |  | 24VDC BCV130DX08 PLC Control Supply | Healthy | Q172 | BCV130DX08 |  | 2.8\0.1:5 | BR4-2110-E-00109 | 0 |  | D | [6 empty] | F1 |  | 6
BCV130 | DX08 | DIO1 | 130 | 2 | 8 | 0 | 1 | 6 |  |  | DI | 4 | BCV130DX08 | VDC06 |  | 24VDC Tramp Metal Magnet Safety Relay Supply | Healthy | Q176 | BCV130DX08 |  | 2.8\0.1:6 | BR4-2110-E-00109 | 0 |  | D | [6 empty] | F1 |  | 7
BCV130 | DX08 | DIO1 | 130 | 2 | 8 | 0 | 1 | 7 |  |  | DI | 7 | BCV130DX08 | VDC07 |  | 24VDC BCV130MT01IS01 Control Supply | Healthy | Q180 | BCV130DX08 |  | 2.8\0.1:7 | BR4-2110-E-00109 | 0 |  | D | [6 empty] | F1 |  | 8
BCV130 | DX08 | DIO1 | 130 | 2 | 8 | 0 | 1 | 8 |  |  | DI | 7 | BCV130DX08 | VDC08 |  | 24VDC BCV130MT01IS02 Control Supply | Healthy | Q184 | BCV130DX08 |  | 2.8\0.1:8 | BR4-2110-E-00109 | 0 |  | D | [6 empty] | F1 |  | 9
BCV130 | DX08 | DIO1 | 130 | 2 | 8 | 0 | 1 | 9 |  |  | DI | 7 | BCV130DX08 | VDC09 |  | BCV130MD02 Control Supply | Healthy | Q188 | BCV130DX08 |  | 2.8\0.1:9 | BR4-2110-E-00109 | 0 |  | D | [6 empty] | F1 |  | 10
BCV130 | DX08 | DIO1 | 130 | 2 | 8 | 0 | 1 | 10 |  |  | DI | 4 | BCV130DX08 | VDC10 |  | Spare Control Supply | Healthy | Q192 | BCV130DX08 |  | 2.8\0.1:10 | BR4-2110-E-00109 | 0 |  | D | [6 empty] | F1 |  | 11
BCV130 | DX08 | DIO1 | 130 | 2 | 8 | 0 | 1 | 11 |  |  | DI | 4 | BCV130DX08 | VDC11 |  | Spare Control Supply | Healthy | Q196 | BCV130DX08 |  | 2.8\0.1:11 | BR4-2110-E-00109 | 0 |  | D | [6 empty] | F1 |  | 12
BCV130 | DX08 | DIO1 | 130 | 2 | 8 | 0 | 1 | 12 |  |  | DI | [9 empty] | 2.8\0.1:12 |  |  |  | S | [6 empty] | F1 |  | 13
BCV130 | DX08 | DIO1 | 130 | 2 | 8 | 0 | 1 | 13 |  |  | DI | [9 empty] | 2.8\0.1:13 |  |  |  | S | [6 empty] | F1 |  | 14
BCV130 | DX08 | DIO1 | 130 | 2 | 8 | 0 | 1 | 14 |  |  | DI | [9 empty] | 2.8\0.1:14 |  |  |  | S | [6 empty] | F1 |  | 15
BCV130 | DX08 | DIO1 | 130 | 2 | 8 | 0 | 1 | 15 |  |  | DI | [9 empty] | 2.8\0.1:15 |  |  |  | S | [6 empty] | F1 |  | 16
BCV130 | DX08 | DIO1 | 130 | 2 | 8 | 0 | 1 | 16 |  |  | DI | 4 | BCV130PWS05 | PWS05 | PRIMARY CRUSHING DISCHARGE CONVEYOR | Pullwire Switch 5 | Healthy | K203 | BCV130 |  | 2.8\0.1:16 | BR4-2110-E-00110 | 0 |  | D | [6 empty] | F1 | 17 | 18
BCV130 | DX08 | DIO1 | 130 | 2 | 8 | 0 | 1 | 17 |  |  | DI | 4 | BCV130PWS06 | PWS06 | PRIMARY CRUSHING DISCHARGE CONVEYOR | Pullwire Switch 6 | Healthy | K214 | BCV130 |  | 2.8\0.1:17 | BR4-2110-E-00110 | 0 |  | D | [6 empty] | F1 | 19 | 20
BCV130 | DX08 | DIO1 | 130 | 2 | 8 | 0 | 1 | 18 |  |  | DI | 4 | BCV130PWS07 | PWS07 | PRIMARY CRUSHING DISCHARGE CONVEYOR | Pullwire Switch 7 | Healthy | K225 | BCV130 |  | 2.8\0.1:18 | BR4-2110-E-00110 | 0 |  | D | [6 empty] | F1 | 21 | 22
BCV130 | DX08 | DIO1 | 130 | 2 | 8 | 0 | 1 | 19 |  |  | DI | 4 | BCV130PWS08 | PWS08 | PRIMARY CRUSHING DISCHARGE CONVEYOR | Pullwire Switch 8 | Healthy | K236 | BCV130 |  | 2.8\0.1:19 | BR4-2110-E-00110 | 0 |  | D | [6 empty] | F1 | 23 | 24
BCV130 | DX08 | DIO1 | 130 | 2 | 8 | 0 | 1 | 20 |  |  | DI | [9 empty] | 2.8\0.1:20 |  |  |  | S | [6 empty] | F1 | 25 | 26
BCV130 | DX08 | DIO1 | 130 | 2 | 8 | 0 | 1 | 21 |  |  | DI | 4 | BCV130PP03LCS01 | STT01 | DE-WATERING PLOUGH SUMP PUMP | Start Pushbutton | Activated | STT01 | BCV130PP03 |  | 2.8\0.1:21 | BR4-2110-E-00218 | 1 |  | S | [6 empty] | F1 | 27 | 28
BCV130 | DX08 | DIO1 | 130 | 2 | 8 | 0 | 1 | 22 |  |  | DI | 4 | BCV130PP03LCS01 | STP01 | DE-WATERING PLOUGH SUMP PUMP | Stop Pushbutton | Activated | STP01 | BCV130PP03 |  | 2.8\0.1:22 | BR4-2110-E-00218 | 1 |  | S | [6 empty] | F1 | 29 | 30
BCV130 | DX08 | DIO1 | 130 | 2 | 8 | 0 | 1 | 23 |  |  | DI | 5 | BCV130PP03LCS01 | IS01 | DE-WATERING PLOUGH SUMP PUMP | Isolator | Closed | IS01 | BCV130PP03 |  | 2.8\0.1:23 | BR4-2110-E-00218 | 1 |  | S | [6 empty] | F1 | 31 | 32
BCV130 | DX08 | DIO1 | 130 | 2 | 8 | 0 | 1 | 24 |  |  | DI | 4 | BCV130BP02ZS01 | ZS01 | DE-WATERING PLOUGH SUMP | Position Switch | Activated |  | BCV130BP02 |  | 2.8\0.1:24 | BR4-2110-E-00110 | 0 |  | S | [6 empty] | F1 | 33 | 34
BCV130 | DX08 | DIO1 | 130 | 2 | 8 | 0 | 1 | 25 |  |  | DI | [9 empty] | 2.8\0.1:25 |  |  |  | S | [6 empty] | F1 | 35 | 36
BCV130 | DX08 | DIO1 | 130 | 2 | 8 | 0 | 1 | 26 |  |  | DI | [9 empty] | 2.8\0.1:26 |  |  |  | S | [6 empty] | F1 | 37 | 38
BCV130 | DX08 | DIO1 | 130 | 2 | 8 | 0 | 1 | 27 |  |  | DI | [9 empty] | 2.8\0.1:27 |  |  |  | S | [6 empty] | F1 | 39 | 40
BCV130 | DX08 | DIO1 | 130 | 2 | 8 | 0 | 1 | 28 |  |  | DI | [9 empty] | 2.8\0.1:28 |  |  |  | S | [6 empty] | F1 | 41 | 42
BCV130 | DX08 | DIO1 | 130 | 2 | 8 | 0 | 1 | 29 |  |  | DI | 7 | BCV130MD02 | XS01 | Metal | Healthy |  | BCV130MD02 |  |  | 2.8\0.1:29 | BR4-2110-E-00110 |  |  | S | [6 empty] | F1 | 43 | 44
BCV130 | DX08 | DIO1 | 130 | 2 | 8 | 0 | 1 | 30 |  |  | DI | 7 | BCV130MD02 | XS02 | Unit | Detected |  | BCV130MD02 |  |  | 2.8\0.1:30 | BR4-2110-E-00110 |  |  | S | [6 empty] | F1 | 45 | 46
BCV130 | DX08 | DIO1 | 130 | 2 | 8 | 0 | 1 | 31 |  |  | DI | 7 | BCV130MD02 | XS03 | Unit | Bypassed |  | BCV130MD02 |  |  | 2.8\0.1:31 | BR4-2110-E-00110 |  | Vendor drgs | S | [6 empty] | F1 | 47 | 48
BCV130 | DX08 | DIO1 | 130 | 2 | 8 | 0 | 2 | 0 | BMXFCW303 | BMXDDI3202K | DI | 4 | BCV130MA01 | IS01 | TRAMP METAL MAGNET | 415V Mains Isolator | Closed | IS01 | BCV130MA01 |  | 2.8\0.2:0 | BR4-2110-E-00111 | 0 | BR4-2110-E-00526 / 1 | S | [6 empty] | F2 | 1 | 2
BCV130 | DX08 | DIO1 | 130 | 2 | 8 | 0 | 2 | 1 |  |  | DI | 4 | BCV130MA01 | RLY01 | TRAMP METAL MAGNET | Mains Phase Fail Relay | Healthy | RLY01 | BCV130MA01 |  | 2.8\0.2:1 | BR4-2110-E-00111 | 0 | BR4-2110-E-00526 / 1 | S | [6 empty] | F2 | 3 | 4
BCV130 | DX08 | DIO1 | 130 | 2 | 8 | 0 | 2 | 2 |  |  | DI | 4 | BCV130MA01 | CAX01 | TRAMP METAL MAGNET | Full Power Contactor | Closed | CAX01 | BCV130MA01 |  | 2.8\0.2:2 | BR4-2110-E-00111 | 0 | BR4-2110-E-00526 / 1 | S | [6 empty] | F2 | 5 | 6
BCV130 | DX08 | DIO1 | 130 | 2 | 8 | 0 | 2 | 3 |  |  | DI | 4 | BCV130MA01 | CAX02 | TRAMP METAL MAGNET | Reduced Power Contactor | Closed | CAX02 | BCV130MA01 |  | 2.8\0.2:3 | BR4-2110-E-00111 | 0 | BR4-2110-E-00526 / 1 | S | [6 empty] | F2 | 7 | 8
BCV130 | DX08 | DIO1 | 130 | 2 | 8 | 0 | 2 | 4 |  |  | DI | 4 | BCV130MA01 | RLY02 | TRAMP METAL MAGNET | Transformer/Rectifier Overtemperature | Healthy | RLY02 | BCV130MA01 |  | 2.8\0.2:4 | BR4-2110-E-00111 | 0 | BR4-2110-E-00526 / 1 | S | [6 empty] | F2 | 9 | 10
BCV130 | DX08 | DIO1 | 130 | 2 | 8 | 0 | 2 | 5 |  |  | DI | 4 | BCV130MA01 | CB01 | TRAMP METAL MAGNET | 415VAC Mains Circuit Breaker | Closed | CB01 | BCV130MA01 |  | 2.8\0.2:5 | BR4-2110-E-00111 | 0 | BR4-2110-E-00526 / 1 | S | [6 empty] | F2 | 11 | 12
BCV130 | DX08 | DIO1 | 130 | 2 | 8 | 0 | 2 | 6 |  |  | DI | 4 | BCV130MA01 | CB02 | TRAMP METAL MAGNET | Full Power Circuit Breaker | Closed | CB02 | BCV130MA01 |  | 2.8\0.2:6 | BR4-2110-E-00111 | 0 | BR4-2110-E-00526 / 1 | S | [6 empty] | F2 | 13 | 14
BCV130 | DX08 | DIO1 | 130 | 2 | 8 | 0 | 2 | 7 |  |  | DI | 4 | BCV130MA01 | CB03 | TRAMP METAL MAGNET | Reduced Power Circuit Breaker | Closed | CB03 | BCV130MA01 |  | 2.8\0.2:7 | BR4-2110-E-00111 | 0 | BR4-2110-E-00526 / 1 | S | [6 empty] | F2 | 15 | 16
BCV130 | DX08 | DIO1 | 130 | 2 | 8 | 0 | 2 | 8 |  |  | DI | 4 | BCV130MA01 | CB05 | TRAMP METAL MAGNET | 240VAC Circuit Breaker | Closed | CB05 | BCV130MA01 |  | 2.8\0.2:8 | BR4-2110-E-00111 | 0 | BR4-2110-E-00526 / 1 | S | [6 empty] | F2 | 17 | 18
BCV130 | DX08 | DIO1 | 130 | 2 | 8 | 0 | 2 | 9 |  |  | DI | 4 | BCV130MA01 | RLY03 | TRAMP METAL MAGNET | Fans Running Relay | Healthy | RLY03 | BCV130MA01 |  | 2.8\0.2:9 | BR4-2110-E-00111 | 0 | BR4-2110-E-00526 / 1 | S | [6 empty] | F2 | 19 | 20
BCV130 | DX08 | DIO1 | 130 | 2 | 8 | 0 | 2 | 10 |  |  | DI | 4 | BCV130MA01 | PB01 | TRAMP METAL MAGNET | Magnet Start Full Power | Activated | PB01 | BCV130MA01 |  | 2.8\0.2:10 | BR4-2110-E-00111 | 0 | BR4-2110-E-00526 / 1 | S | [6 empty] | F2 | 21 | 22
BCV130 | DX08 | DIO1 | 130 | 2 | 8 | 0 | 2 | 11 |  |  | DI | 4 | BCV130MA01 | PB02 | TRAMP METAL MAGNET | Magnet Start Reduced Power | Activated | PB02 | BCV130MA01 |  | 2.8\0.2:11 | BR4-2110-E-00111 | 0 | BR4-2110-E-00526 / 1 | S | [6 empty] | F2 | 23 | 24
BCV130 | DX08 | DIO1 | 130 | 2 | 8 | 0 | 2 | 12 |  |  | DI | 4 | BCV130MA01 | PB03 | TRAMP METAL MAGNET | Magnet Stop | Activated | PB03 | BCV130MA01 |  | 2.8\0.2:12 | BR4-2110-E-00111 | 0 | BR4-2110-E-00526 / 1 | S | [6 empty] | F2 | 25 | 26
BCV130 | DX08 | DIO1 | 130 | 2 | 8 | 0 | 2 | 13 |  |  | DI | 5 | BCV130MA01 | PB04 | TRAMP METAL MAGNET | Trolley Forward North (Maintenance) | Activated | PB04 | BCV130MT01 |  | 2.8\0.2:13 | BR4-2110-E-00236 | 0 | BR4-2110-E-00526 / 1 | S | [6 empty] | F2 | 27 | 28
BCV130 | DX08 | DIO1 | 130 | 2 | 8 | 0 | 2 | 14 |  |  | DI | 5 | BCV130MA01 | PB05 | TRAMP METAL MAGNET | Trolley Stop | Activated | PB05 | BCV130MT01 |  | 2.8\0.2:14 | BR4-2110-E-00236 | 0 | BR4-2110-E-00526 / 1 | S | [6 empty] | F2 | 29 | 30
BCV130 | DX08 | DIO1 | 130 | 2 | 8 | 0 | 2 | 15 |  |  | DI | 5 | BCV130MA01 | PB06 | TRAMP METAL MAGNET | Trolley Reverse South (Cleaning) | Activated | PB06 | BCV130MT01 |  | 2.8\0.2:15 | BR4-2110-E-00236 | 0 | BR4-2110-E-00526 / 1 | S | [6 empty] | F2 | 31 | 32
BCV130 | DX08 | DIO1 | 130 | 2 | 8 | 0 | 2 | 16 |  |  | DI | 4 | BCV130MA01 | PB07 | TRAMP METAL MAGNET | Cooling Start | Activated | PB07 | BCV130MA01 |  | 2.8\0.2:16 | BR4-2110-E-00111 |  | BR4-2110-E-00526 / 1 | S | [6 empty] | F3 | 1 | 2
BCV130 | DX08 | DIO1 | 130 | 2 | 8 | 0 | 2 | 17 |  |  | DI | 4 | BCV130MA01 | PB08 | TRAMP METAL MAGNET | Cooling Stop | Activated | PB08 | BCV130MA01 |  | 2.8\0.2:17 | BR4-2110-E-00111 |  | BR4-2110-E-00526 / 1 | S | [6 empty] | F3 | 3 | 4
BCV130 | DX08 | DIO1 | 130 | 2 | 8 | 0 | 2 | 18 |  |  | DI | 4 | BCV130MA01 | PB09 | TRAMP METAL MAGNET | Lamp Test | Activated | PB09 | BCV130MA01 |  | 2.8\0.2:18 | BR4-2110-E-00111 | 0 | BR4-2110-E-00526 / 1 | S | [6 empty] | F3 | 5 | 6
BCV130 | DX08 | DIO1 | 130 | 2 | 8 | 0 | 2 | 19 |  |  | DI | 4 | BCV130MA01PN01 | SY01 | TRAMP METAL MAGNET | Safety Relay | Healthy | SY01 | BCV130MA01 |  | 2.8\0.2:19 | BR4-2110-E-00111 | 0 | BR4-2110-E-00526 / 1 | S | [6 empty] | F3 | 7 | 8
BCV130 | DX08 | DIO1 | 130 | 2 | 8 | 0 | 2 | 20 |  |  | DI | 4 | BCV130MA01 | ZS01 | TRAMP METAL MAGNET | Cleaning Overtravel | Activated |  | BCV130MA01 |  | 2.8\0.2:20 | BR4-2110-E-00111 | 0 | BR4-2110-E-00526 / 1 | S | [6 empty] | F3 | 9 | 10
BCV130 | DX08 | DIO1 | 130 | 2 | 8 | 0 | 2 | 21 |  |  | DI | 4 | BCV130MA01 | ZS02 | TRAMP METAL MAGNET | Cleaning Position | Activated |  | BCV130MA01 |  | 2.8\0.2:21 | BR4-2110-E-00111 | 0 | BR4-2110-E-00526 / 1 | S | [6 empty] | F3 | 11 | 12
BCV130 | DX08 | DIO1 | 130 | 2 | 8 | 0 | 2 | 22 |  |  | DI | 4 | BCV130MA01 | ZS03 | TRAMP METAL MAGNET | Operating Position | Activated |  | BCV130MA01 |  | 2.8\0.2:22 | BR4-2110-E-00111 | 0 | BR4-2110-E-00526 / 1 | S | [6 empty] | F3 | 13 | 14
BCV130 | DX08 | DIO1 | 130 | 2 | 8 | 0 | 2 | 23 |  |  | DI | 4 | BCV130MA01 | ZS04 | TRAMP METAL MAGNET | Maintenance Position | Activated |  | BCV130MA01 |  | 2.8\0.2:23 | BR4-2110-E-00111 | 0 | BR4-2110-E-00526 / 1 | S | [6 empty] | F3 | 15 | 16
BCV130 | DX08 | DIO1 | 130 | 2 | 8 | 0 | 2 | 24 |  |  | DI | 4 | BCV130MA01 | ZS05 | TRAMP METAL MAGNET | Maintenance Overtravel | Activated |  | BCV130MA01 |  | 2.8\0.2:24 | BR4-2110-E-00111 | 0 | BR4-2110-E-00526 / 1 | S | [6 empty] | F3 | 17 | 18
BCV130 | DX08 | DIO1 | 130 | 2 | 8 | 0 | 2 | 25 |  |  | DI | 4 | BCV130MA01 | ZS06 | TRAMP METAL MAGNET | Overtension Arm | Activated |  | BCV130MA01 |  | 2.8\0.2:25 | BR4-2110-E-00111 | 0 | BR4-2110-E-00526 / 1 | S | [6 empty] | F3 | 19 | 20
BCV130 | DX08 | DIO1 | 130 | 2 | 8 | 0 | 2 | 26 |  |  | DI | 4 | BCV130PP02 | FS01 | TRAMP METAL MAGNET OIL PUMP | Magnet Oil Flow | Healthy |  | BCV130PP02 |  | 2.8\0.2:26 | BR4-2110-E-00111 | 0 | BR4-2110-E-00526 / 1 | S | [6 empty] | F3 | 21 | 22
BCV130 | DX08 | DIO1 | 130 | 2 | 8 | 0 | 2 | 27 |  |  | DI | 4 | BCV130MA01 | TS01 | TRAMP METAL MAGNET | Oil Temperature | Healthy |  | BCV130MA01 |  | 2.8\0.2:27 | BR4-2110-E-00111 | 0 | BR4-2110-E-00526 / 1 | S | [6 empty] | F3 | 23 | 24
BCV130 | DX08 | DIO1 | 130 | 2 | 8 | 0 | 2 | 28 |  |  | DI | 4 | BCV130MT01 | IS01 | TRAMP METAL MAGNET OIL COOLER | 415V Mains Isolator | Closed | IS01 | BCV130MT01 |  | 2.8\0.2:28 | BR4-2110-E-00233 | 0 |  | S | [6 empty] | F3 | 25 | 26
BCV130 | DX08 | DIO1 | 130 | 2 | 8 | 0 | 2 | 29 |  |  | DI | 4 | BCV130MT02 | IS02 | TRAMP METAL MAGNET LONG TRAVEL TROLLEY | 415V Mains Isolator | Closed | IS01 | BCV130MT01 |  | 2.8\0.2:29 | BR4-2110-E-00236 | 0 |  | S | [6 empty] | F3 | 27 | 28
BCV130 | DX08 | DIO1 | 130 | 2 | 8 | 0 | 2 | 30 |  |  | DI | [9 empty] | 2.8\0.2:30 |  |  |  | S | [6 empty] | F3 | 29 | 30
BCV130 | DX08 | DIO1 | 130 | 2 | 8 | 0 | 2 | 31 |  |  | DI | [9 empty] | 2.8\0.2:31 |  |  |  | S | [6 empty] | F3 | 31 | 32
BCV130 | DX08 | DIO1 | 130 | 2 | 8 | 0 | 3 | 0 | BMXFTB2010 | BMXDDO1602 | DO | 4 | BCV130MA01 | CAX01 | TRAMP METAL MAGNET | Full Power Contactor |  |  | BCV130MA01 |  | 2.8\0.3:0 | BR4-2110-E-00112 | 0 | BR4-2110-E-00526/1 | S | [6 empty] | F5 | 1 | 2
BCV130 | DX08 | DIO1 | 130 | 2 | 8 | 0 | 3 | 1 |  |  | DO | 4 | BCV130MA01 | CAX02 | TRAMP METAL MAGNET | Reduced Power Contactor |  |  | BCV130MA01 |  | 2.8\0.3:1 | BR4-2110-E-00112 | 0 | BR4-2110-E-00526/1 | S | [6 empty] | F5 | 3 | 4
BCV130 | DX08 | DIO1 | 130 | 2 | 8 | 0 | 3 | 2 |  |  | DO | 4 | BCV130MA01 | IL01 | TRAMP METAL MAGNET | Auto Mode Light |  |  | BCV130MA01 |  | 2.8\0.3:2 | BR4-2110-E-00112 | 0 | BR4-2110-E-00526/1 | S | [6 empty] | F5 | 5 | 6
BCV130 | DX08 | DIO1 | 130 | 2 | 8 | 0 | 3 | 3 |  |  | DO | 4 | BCV130MA01 | IL02 | TRAMP METAL MAGNET | Local Mode Light |  |  | BCV130MA01 |  | 2.8\0.3:3 | BR4-2110-E-00112 | 0 | BR4-2110-E-00526/1 | S | [6 empty] | F5 | 7 | 8
BCV130 | DX08 | DIO1 | 130 | 2 | 8 | 0 | 3 | 4 |  |  | DO | 4 | BCV130MA01 | IL03 | TRAMP METAL MAGNET | Mains Healthy Light |  |  | BCV130MA01 |  | 2.8\0.3:4 | BR4-2110-E-00112 | 0 | BR4-2110-E-00526/1 | S | [6 empty] | F5 | 9 | 10
BCV130 | DX08 | DIO1 | 130 | 2 | 8 | 0 | 3 | 5 |  |  | DO | 4 | BCV130MA01 | IL04 | TRAMP METAL MAGNET | Magnet Running Light |  |  | BCV130MA01 |  | 2.8\0.3:5 | BR4-2110-E-00112 | 0 | BR4-2110-E-00526/1 | S | [6 empty] | F5 | 11 | 12
BCV130 | DX08 | DIO1 | 130 | 2 | 8 | 0 | 3 | 6 |  |  | DO | 4 | BCV130MA01 | IL05 | TRAMP METAL MAGNET | Magnet Fault Light |  |  | BCV130MA01 |  | 2.8\0.3:6 | BR4-2110-E-00112 | 0 | BR4-2110-E-00526/1 | S | [6 empty] | F5 | 13 | 14
BCV130 | DX08 | DIO1 | 130 | 2 | 8 | 0 | 3 | 7 |  |  | DO | 4 | BCV130MA01 | IL06 | TRAMP METAL MAGNET | Trolley Fault Light |  |  | BCV130MA01 |  | 2.8\0.3:7 | BR4-2110-E-00112 | 0 | BR4-2110-E-00526/1 | S | [6 empty] | F5 | 15 | 16
BCV130 | DX08 | DIO1 | 130 | 2 | 8 | 0 | 3 | 8 |  |  | DO | 4 | BCV130MA01 | IL07 | TRAMP METAL MAGNET | Cooling Running Light |  |  | BCV130MA01 |  | 2.8\0.3:8 | BR4-2110-E-00112 | 0 | BR4-2110-E-00526/1 | S | [6 empty] | F5 | 17 | 18
BCV130 | DX08 | DIO1 | 130 | 2 | 8 | 0 | 3 | 9 |  |  | DO | 4 | BCV130MA01 | IL08 | TRAMP METAL MAGNET | Cooling Fault Light |  |  | BCV130MA01 |  | 2.8\0.3:9 | BR4-2110-E-00112 | 0 | BR4-2110-E-00526/1 | S | [6 empty] | F5 | 19 | 20
BCV130 | DX08 | DIO1 | 130 | 2 | 8 | 0 | 3 | 10 |  |  | DO | 4 | BCV130MA01 | IL09 | TRAMP METAL MAGNET | Cleaning Cycle In Progress Light |  |  | BCV130MA01 |  | 2.8\0.3:10 | BR4-2110-E-00112 | 0 | BR4-2110-E-00526/1 | S | [6 empty] | F5 | 21 | 22
BCV130 | DX08 | DIO1 | 130 | 2 | 8 | 0 | 3 | 11 |  |  | DO | 4 | BCV130MA01 | IL10 | TRAMP METAL MAGNET | Maintenance Position Light |  |  | BCV130MA01 |  | 2.8\0.3:11 | BR4-2110-E-00112 | 0 | BR4-2110-E-00526/1 | S | [6 empty] | F5 | 23 | 24
BCV130 | DX08 | DIO1 | 130 | 2 | 8 | 0 | 3 | 12 |  |  | DO | 4 | BCV130MA01 | IL11 | TRAMP METAL MAGNET | Operating Position Light |  |  | BCV130MA01 |  | 2.8\0.3:12 | BR4-2110-E-00112 | 0 | BR4-2110-E-00526/1 | S | [6 empty] | F5 | 25 | 26
BCV130 | DX08 | DIO1 | 130 | 2 | 8 | 0 | 3 | 13 |  |  | DO | 4 | BCV130MA01 | IL12 | TRAMP METAL MAGNET | Cleaning Position Light |  |  | BCV130MA01 |  | 2.8\0.3:13 | BR4-2110-E-00112 | 0 | BR4-2110-E-00526/1 | S | [6 empty] | F5 | 27 | 28
BCV130 | DX08 | DIO1 | 130 | 2 | 8 | 0 | 3 | 14 |  |  | DO | 4 | BCV130MA01 | YA01 | TRAMP METAL MAGNET | Start Up Warning |  |  | BCV130MA01 |  | 2.8\0.3:14 | BR4-2110-E-00112 | 0 | BR4-2110-E-00526/1 | S | [6 empty] | F5 | 29 | 30
BCV130 | DX08 | DIO1 | 130 | 2 | 8 | 0 | 3 | 15 |  |  | DO | [9 empty] | 2.8\0.3:15 |  |  |  | S | [6 empty] | F5 | 31 | 32
BCV130 | DX08 | DIO1 | 130 | 2 | 8 | 0 | 4 | 0 | BMXFTB2010 | BMXDDO1602 | DO | 4 | BCV130YA02 | YA02 | PRIMARY CRUSHING DISCHARGE CONVEYOR | Start Up Warning Siren 2 |  |  | BCV130 |  | 2.8\0.4:0 | BR4-2110-E-00110 | 0 |  | S | [6 empty] | F6 | 1 | 2
BCV130 | DX08 | DIO1 | 130 | 2 | 8 | 0 | 4 | 1 |  |  | DO | 4 | BCV130YA03 | YA03 | PRIMARY CRUSHING DISCHARGE CONVEYOR | Start Up Warning Siren 3 |  |  | BCV130 |  | 2.8\0.4:1 | BR4-2110-E-00110 | 0 |  | S | [6 empty] | F6 | 3 | 4
BCV130 | DX08 | DIO1 | 130 | 2 | 8 | 0 | 4 | 2 |  |  | DO | 4 | BCV130PP03SV02 | SV02 | DE-WATERING PLOUGH SUMP PUMP | Agitator Solenoid Valve |  |  | BCV130SM01 |  | 2.8\0.4:2 | BR4-2110-E-00110 | 0 |  | S | [6 empty] | F6 | 5 | 6
BCV130 | DX08 | DIO1 | 130 | 2 | 8 | 0 | 4 | 3 |  |  | DO | [9 empty] | 2.8\0.4:3 |  |  |  | S | [6 empty] | F6 | 7 | 8
BCV130 | DX08 | DIO1 | 130 | 2 | 8 | 0 | 4 | 4 |  |  | DO | [9 empty] | 2.8\0.4:4 |  |  |  | S | [6 empty] | F6 | 9 | 10
BCV130 | DX08 | DIO1 | 130 | 2 | 8 | 0 | 4 | 5 |  |  | DO | [9 empty] | 2.8\0.4:5 |  |  |  | S | [6 empty] | F6 | 11 | 12
BCV130 | DX08 | DIO1 | 130 | 2 | 8 | 0 | 4 | 6 |  |  | DO | [9 empty] | 2.8\0.4:6 |  |  |  | S | [6 empty] | F6 | 13 | 14
BCV130 | DX08 | DIO1 | 130 | 2 | 8 | 0 | 4 | 7 |  |  | DO | [9 empty] | 2.8\0.4:7 |  |  |  | S | [6 empty] | F6 | 15 | 16
BCV130 | DX08 | DIO1 | 130 | 2 | 8 | 0 | 4 | 8 |  |  | DO | [9 empty] | 2.8\0.4:8 |  |  |  | S | [6 empty] | F6 | 17 | 18
BCV130 | DX08 | DIO1 | 130 | 2 | 8 | 0 | 4 | 9 |  |  | DO | [9 empty] | 2.8\0.4:9 |  |  |  | S | [6 empty] | F6 | 19 | 20
BCV130 | DX08 | DIO1 | 130 | 2 | 8 | 0 | 4 | 10 |  |  | DO | [9 empty] | 2.8\0.4:10 |  |  |  | S | [6 empty] | F6 | 21 | 22
BCV130 | DX08 | DIO1 | 130 | 2 | 8 | 0 | 4 | 11 |  |  | DO | [9 empty] | 2.8\0.4:11 |  |  |  | S | [6 empty] | F6 | 23 | 24
BCV130 | DX08 | DIO1 | 130 | 2 | 8 | 0 | 4 | 12 |  |  | DO | [9 empty] | 2.8\0.4:12 |  |  |  | S | [6 empty] | F6 | 25 | 26
BCV130 | DX08 | DIO1 | 130 | 2 | 8 | 0 | 4 | 13 |  |  | DO | [9 empty] | 2.8\0.4:13 |  |  |  | S | [6 empty] | F6 | 27 | 28
BCV130 | DX08 | DIO1 | 130 | 2 | 8 | 0 | 4 | 14 |  |  | DO | [9 empty] | 2.8\0.4:14 |  |  |  | S | [6 empty] | F6 | 29 | 30
BCV130 | DX08 | DIO1 | 130 | 2 | 8 | 0 | 4 | 15 |  |  | DO | [9 empty] | 2.8\0.4:15 |  |  |  | S | [6 empty] | F6 | 31 | 32
BCV130 | DX08 | DIO1 | 130 | 2 | 8 | 0 | 5 | 0 | BMXFTW301S | BMEAHI0812 | AI | 4 | BCV130MA01IT01 | IT01 | TRAMP METAL MAGNET | Current |  |  | BCV130MA01 | REAL | 2.8\0.5:0 | BR4-2110-E-00112 | 0 | BR4-2110-E-00526/1 | S |  | 0 | 300 | 0 | 300 | #.# EU | F5 | 33 | 34
BCV130 | DX08 | DIO1 | 130 | 2 | 8 | 0 | 5 | 1 |  |  | AI | 4 | BCV130MA01XT01 | XT01 | TRAMP METAL MAGNET | Voltage |  |  | BCV130MA01 | REAL | 2.8\0.5:1 | BR4-2110-E-00112 | 0 | BR4-2110-E-00526/1 | S |  | 0 | 600 | 0 | 600 | #.# EU | F5 | 35 | 36
BCV130 | DX08 | DIO1 | 130 | 2 | 8 | 0 | 5 | 2 |  |  | AI | 4 | BCV130SM01LT01 | LT01 | DE-WATERING PLOUGH SUMP | Level Transmitter |  |  | BCV130SM01 | REAL | 2.8\0.5:2 | BR4-2110-E-00112 | 0 | BR4-2110-E-00526/1 | S |  | 0 | 100 | 0 | 100 | #.# EU | F5 | 37 | 38
BCV130 | DX08 | DIO1 | 130 | 2 | 8 | 0 | 5 | 3 |  |  | AI | 4 | BCV130MA01WT01 | WT01 | TRAMP METAL MAGNET | Weightometer |  |  | BCV130MA01 | REAL | 2.8\0.5:3 | BR4-2110-E-00112 | 0 | BR4-2110-E-00526/1 | S |  | 0 | 6206 | 0 | 6206 | #.# EU | F5 | 39 | 40
BCV130 | DX08 | DIO1 | 130 | 2 | 8 | 0 | 5 | 4 |  |  | AI | [9 empty] | 2.8\0.5:4 |  |  |  | S | [6 empty] | F5 | 41 | 42
BCV130 | DX08 | DIO1 | 130 | 2 | 8 | 0 | 5 | 5 |  |  | AI | [9 empty] | 2.8\0.5:5 |  |  |  | S | [6 empty] | F5 | 43 | 44
BCV130 | DX08 | DIO1 | 130 | 2 | 8 | 0 | 5 | 6 |  |  | AI | [9 empty] | 2.8\0.5:6 |  |  |  | S | [6 empty] | F5 | 45 | 46
BCV130 | DX08 | DIO1 | 130 | 2 | 8 | 0 | 5 | 7 |  |  | AI | [9 empty] | 2.8\0.5:7 |  |  |  | S | [6 empty] | F5 | 47 | 48
BCV130 | DX08 | DIO1 | 130 | 2 | 8 | 0 | 6 |  |  | BMXX0 |  | 0 | [8 empty] | 2.8\0.6:
BCV130 | DX08 | DIO1 | 130 | 2 | 8 | 0 | 6 |  |  |  |  | 0 | [8 empty] | 2.8\0.6:
BCV130 | DX08 | DIO1 | 130 | 2 | 8 | 0 | 6 |  |  |  |  | 0 | [8 empty] | 2.8\0.6:
BCV130 | DX08 | DIO1 | 130 | 2 | 8 | 0 | 6 |  |  |  |  | 0 | [8 empty] | 2.8\0.6:
BCV130 | DX08 | DIO1 | 130 | 2 | 8 | 0 | 7 |  |  | BMXX0 |  | 0 | [8 empty] | 2.8\0.7:
BCV130 | DX08 | DIO1 | 130 | 2 | 8 | 0 | 7 |  |  |  |  | 0 | [8 empty] | 2.8\0.7:
BCV130 | DX08 | DIO1 | 130 | 2 | 8 | 0 | 7 |  |  |  |  | 0 | [8 empty] | 2.8\0.7:
BCV130 | DX08 | DIO1 | 130 | 2 | 8 | 0 | 7 |  |  |  |  | 0 | [8 empty] | 2.8\0.7:
BCV130 | DX08 | DIO1 | 130 | 2 | 8 | 0 | 8 |  |  | BMXX0 |  | 0 | [8 empty] | 2.8\0.8:
BCV130 | DX08 | DIO1 | 130 | 2 | 8 | 0 | 8 |  |  |  |  | 0 | [8 empty] | 2.8\0.8:
BCV130 | DX08 | DIO1 | 130 | 2 | 8 | 0 | 8 |  |  |  |  | 0 | [8 empty] | 2.8\0.8:
BCV130 | DX08 | DIO1 | 130 | 2 | 8 | 0 | 8 |  |  |  |  | 0 | [8 empty] | 2.8\0.8:
BCV130 | DX08 | DIO1 | 130 | 2 | 8 | 0 | 9 |  |  | BMXX0 |  | 0 | [8 empty] | 2.8\0.9:
BCV130 | DX08 | DIO1 | 130 | 2 | 8 | 0 | 9 |  |  |  |  | 0 | [8 empty] | 2.8\0.9:
BCV130 | DX08 | DIO1 | 130 | 2 | 8 | 0 | 9 |  |  |  |  | 0 | [8 empty] | 2.8\0.9:
BCV130 | DX08 | DIO1 | 130 | 2 | 8 | 0 | 9 |  |  |  |  | 0 | [8 empty] | 2.8\0.9:
BCV130 | DX08 | DIO1 | 130 | 2 | 8 | 0 | 10 |  |  | BMXX0 |  | 0 | [8 empty] | 2.8\0.10:
BCV130 | DX08 | DIO1 | 130 | 2 | 8 | 0 | 10 |  |  |  |  | 0 | [8 empty] | 2.8\0.10:
BCV130 | DX08 | DIO1 | 130 | 2 | 8 | 0 | 10 |  |  |  |  | 0 | [8 empty] | 2.8\0.10:
BCV130 | DX08 | DIO1 | 130 | 2 | 8 | 0 | 10 |  |  |  |  | 0 | [8 empty] | 2.8\0.10:
BCV130 | DX08 | DIO1 | 130 | 2 | 8 | 0 | 11 |  |  | BMXX0 |  | 0 | [8 empty] | 2.8\0.11:
BCV130 | DX08 | DIO1 | 130 | 2 | 8 | 0 | 11 |  |  |  |  | 0 | [8 empty] | 2.8\0.11:
BCV130 | DX08 | DIO1 | 130 | 2 | 8 | 0 | 11 |  |  |  |  | 0 | [8 empty] | 2.8\0.11:
BCV130 | DX08 | DIO1 | 130 | 2 | 8 | 0 | 11 |  |  |  |  | 0 | [8 empty] | 2.8\0.11:
[10 empty] | * |  |  | BCV130MA01 | LOS01 |  | Emergency Stop Contact (BCV130FN03) |  | SUB LINK | BCV130FN03 |  |  | BR4-2110-E-00111 | 0 | [8 empty] | F7 | 1 | 2
[10 empty] | * |  |  | BCV130MA01 | LOS01 |  | Emergency Stop Contact (BCV130FN04) |  | SUB LINK | BCV130FN04 |  |  | BR4-2110-E-00111 | 0 | [8 empty] | F7 | 3 | 6
[10 empty] | * |  |  | BCV130MA01 | LOS01 |  | Emergency Stop Contact (BCV130PP02) |  | SUB LINK | BCV130PP02 |  |  | BR4-2110-E-00111 | 0 | [8 empty] | F7 | 5 | 6
[10 empty] | * |  |  | BCV130MA01 | LOS01 |  | Emetgency Stop Contact (BCV130MT01 & EM02) |  | SUB LINK | BCV130MT01 & EM02 |  |  | BR4-2110-E-00111 | 0 | [8 empty] | F7 | 7 | 8
[10 empty] | * | [5 empty] | Safety Relay (To Sumation Relay BSR130DX02) |  |  | BCV130 |  |  | BR4-2110-E-00122 | 0 | [8 empty] | F7 | 9 | 10 | 11 | 12
[10 empty] | * |  |  | BCV130PP03LCS01 | LOS01 | DE-WATERING PLOUGH SUMP PUMP | Emergency Stop Relay |  | SUB LINK | BCV130PP03 |  |  | BR4-2110-E-00218 | 1 | [8 empty] | F7 | 13 | 14 | 15 | 16
[32 empty] | F7 | 17 | 18 | 19 | 20
[10 empty] | PNOZs4 | Safety Relay | 1 | BCV130PWS05 | PWS05 | PRIMARY CRUSHING DISCHARGE CONVEYOR | Pullwire Switch 5 |  | K203 | BCV130 |  |  | BR4-2110-E-00110 | 0 | [8 empty] | F7 | 21 | 22 | 23 | 24
[10 empty] | PNOZs4 | Safety Relay | 1 | BCV130PWS06 | PWS06 | PRIMARY CRUSHING DISCHARGE CONVEYOR | Pullwire Switch 6 |  | K214 | BCV130 |  |  | BR4-2110-E-00110 | 0 | [8 empty] | F7 | 25 | 26 | 27 | 28
[10 empty] | PNOZs4 | Safety Relay | 1 | BCV130PWS07 | PWS07 | PRIMARY CRUSHING DISCHARGE CONVEYOR | Pullwire Switch 7 |  | K225 | BCV130 |  |  | BR4-2110-E-00110 | 0 | [8 empty] | F7 | 29 | 30 | 31 | 32
[10 empty] | PNOZs4 | Safety Relay | 1 | BCV130PWS08 | PWS08 | PRIMARY CRUSHING DISCHARGE CONVEYOR | Pullwire Switch 8 |  | K236 | BCV130 |  |  | BR4-2110-E-00110 | 0 | [8 empty] | F7 | 33 | 34 | 35 | 36
[32 empty] | F7 | 37 | 38 | 39 | 40
[32 empty] | F7 | 41 | 42 | 43 | 44
[32 empty] | F7 | 45 | 46 | 47 | 48
BCV130DX09 - Primary Crusher Discharge Conveyor - Head End
EIO node #9 | DX09 | DIO1 | 130 | 2 | 9 | 0
BCV130 | DX09 | DIO1 | 130 | 2 | 9 | 0 |  | Chassis |  | BMEXBP1200
BCV130 | DX09 | DIO1 | 130 | 2 | 9 | 0 |  | Power |  | BMXCPS4022 |  | total |  | spare |  | % spare
BCV130 | DX09 | DIO1 | 130 | 2 | 9 | 0 | 0 | Comms |  | BMECRA31210 | I/O1 | 136 |  | 76 |  | 55.88%
BCV130 | DX09 | DIO1 | 130 | 2 | 9 | 0 | 1 | 0 | BMXFCW303 | BMXDDI3202K | DI | 4 | BCV130DX09 | CB01 |  | 240VAC Circuit Breaker | Closed | Q106 | BCV130DX09 |  | 2.9\0.1:0 | BR4-2110-E-00113 | 0 |  | D | [6 empty] | F1 |  | 1
BCV130 | DX09 | DIO1 | 130 | 2 | 9 | 0 | 1 | 1 |  |  | DI | 4 | BCV130DX09 | VDC01 |  | 24VDC DIO1 Output Control Supply | Healthy | Q143 | BCV130DX09 |  | 2.9\0.1:1 | BR4-2110-E-00113 | 0 |  | D | [6 empty] | F1 |  | 2
BCV130 | DX09 | DIO1 | 130 | 2 | 9 | 0 | 1 | 2 |  |  | DI | 4 | BCV130DX09 | VDC02 |  | 24VDC GW1 Control Supply | Healthy | Q157 | BCV130DX09 |  | 2.9\0.1:2 | BR4-2110-E-00113 | 0 |  | D | [6 empty] | F1 |  | 3
BCV130 | DX09 | DIO1 | 130 | 2 | 9 | 0 | 1 | 3 |  |  | DI | 4 | BCV130DX09 | VDC03 |  | 24VDC Instrument Supply | Healthy | Q164 | BCV130DX09 |  | 2.9\0.1:3 | BR4-2110-E-00113 | 0 |  | D | [6 empty] | F1 |  | 4
BCV130 | DX09 | DIO1 | 130 | 2 | 9 | 0 | 1 | 4 |  |  | DI | 4 | BCV130DX09 | VDC04 |  | 24VDC Transmitter Supply | Healthy | Q168 | BCV130DX09 |  | 2.9\0.1:4 | BR4-2110-E-00113 | 0 |  | D | [6 empty] | F1 |  | 5
BCV130 | DX09 | DIO1 | 130 | 2 | 9 | 0 | 1 | 5 |  |  | DI | 4 | BCV130DX09 | VDC05 | 24VDC BCV130 Field Control Supply | 24VDC BCV130 Field Control Supply | Healthy | Q172 | BCV130DX09 |  | 2.9\0.1:5 | BR4-2110-E-00113 | 0 |  | D | [6 empty] | F1 |  | 6
BCV130 | DX09 | DIO1 | 130 | 2 | 9 | 0 | 1 | 6 |  |  | DI | 4 | BCV130DX09 | VDC06 | 24VDC BCV130COO01 Control Supply | 24VDC BCV130PP04 Control Supply | Healthy | Q176 | BCV130DX09 |  | 2.9\0.1:6 | BR4-2110-E-00113 | 0 |  | D | [6 empty] | F1 |  | 7
BCV130 | DX09 | DIO1 | 130 | 2 | 9 | 0 | 1 | 7 |  |  | DI | 4 | BCV130DX09 | VDC07 | 24VDC BCV130BK01 Control Supply | 24VDC BCV130BK01 Control Supply | Healthy | Q180 | BCV130DX09 |  | 2.9\0.1:7 | BR4-2110-E-00113 | 0 |  | D | [6 empty] | F1 |  | 8
BCV130 | DX09 | DIO1 | 130 | 2 | 9 | 0 | 1 | 8 |  |  | DI | 4 | BCV130DX09 | VDC08 | 24VDC BCV130FN01 Control Supply | 24VDC BCV130FN01 Control Supply | Healthy | Q184 | BCV130DX09 |  | 2.9\0.1:8 | BR4-2110-E-00113 | 0 |  | D | [6 empty] | F1 |  | 9
BCV130 | DX09 | DIO1 | 130 | 2 | 9 | 0 | 1 | 9 |  |  | DI | 4 | BCV130DX09 | VDC09 | 24VDC BCV130PP03 Sump Control Supply | 24VDC BTN130SM01 Sump Control Supply | Healthy | Q188 | BCV130DX09 |  | 2.9\0.1:9 | BR4-2110-E-00113 | 0 |  | D | [6 empty] | F1 |  | 10
BCV130 | DX09 | DIO1 | 130 | 2 | 9 | 0 | 1 | 10 |  |  | DI | 4 | BCV130DX09 | VDC10 |  | Spare Control Supply | Healthy | Q192 | BCV130DX09 |  | 2.9\0.1:10 | BR4-2110-E-00113 | 0 |  | D | [6 empty] | F1 |  | 11
BCV130 | DX09 | DIO1 | 130 | 2 | 9 | 0 | 1 | 11 |  |  | DI | 4 | BCV130DX09 | VDC11 |  | Spare Control Supply | Healthy | Q196 | BCV130DX09 |  | 2.9\0.1:11 | BR4-2110-E-00113 | 0 |  | D | [6 empty] | F1 |  | 12
BCV130 | DX09 | DIO1 | 130 | 2 | 9 | 0 | 1 | 12 |  |  | DI | [9 empty] | 2.9\0.1:12 |  |  |  | S | [6 empty] | F1 |  | 13
BCV130 | DX09 | DIO1 | 130 | 2 | 9 | 0 | 1 | 13 |  |  | DI | [9 empty] | 2.9\0.1:13 |  |  |  | S | [6 empty] | F1 |  | 14
BCV130 | DX09 | DIO1 | 130 | 2 | 9 | 0 | 1 | 14 |  |  | DI | [9 empty] | 2.9\0.1:14 |  |  |  | S | [6 empty] | F1 |  | 15
BCV130 | DX09 | DIO1 | 130 | 2 | 9 | 0 | 1 | 15 |  |  | DI | [9 empty] | 2.9\0.1:15 |  |  |  | S | [6 empty] | F1 |  | 16
BCV130 | DX09 | DIO1 | 130 | 2 | 9 | 0 | 1 | 16 |  |  | DI | 4 | BCV130LCS01 | STT01 | PRIMARY CRUSHING DISCHARGE CONVEYOR | Start Pushbutton | Activated | STT01 | BCV130 |  | 2.9\0.1:16 | BR4-2110-E-00114 | 0 |  | S | [6 empty] | F1 | 17 | 18
BCV130 | DX09 | DIO1 | 130 | 2 | 9 | 0 | 1 | 17 |  |  | DI | 4 | BCV130LCS01 | STP01 | PRIMARY CRUSHING DISCHARGE CONVEYOR | Stop Pushbutton | Activated | STP01 | BCV130 |  | 2.9\0.1:17 | BR4-2110-E-00114 | 0 |  | S | [6 empty] | F1 | 19 | 20
BCV130 | DX09 | DIO1 | 130 | 2 | 9 | 0 | 1 | 18 |  |  | DI | 4 | BCV130LCS01 | SY01 | PRIMARY CRUSHING DISCHARGE CONVEYOR | Emergency Stop Relay | Healthy | K253 | BCV130 |  | 2.9\0.1:18 | BR4-2110-E-00114 | 0 |  | D | [6 empty] | F1 | 21 | 22
BCV130 | DX09 | DIO1 | 130 | 2 | 9 | 0 | 1 | 19 |  |  | DI | [9 empty] | 2.9\0.1:19 |  |  |  | S | [6 empty] | F1 | 23 | 24
BCV130 | DX09 | DIO1 | 130 | 2 | 9 | 0 | 1 | 20 |  |  | DI | [9 empty] | 2.9\0.1:20 |  |  |  | S | [6 empty] | F1 | 25 | 26
BCV130 | DX09 | DIO1 | 130 | 2 | 9 | 0 | 1 | 21 |  |  | DI | [9 empty] | 2.9\0.1:21 |  |  |  | S | [6 empty] | F1 | 27 | 28
BCV130 | DX09 | DIO1 | 130 | 2 | 9 | 0 | 1 | 22 |  |  | DI | [9 empty] | 2.9\0.1:22 |  |  |  | S | [6 empty] | F1 | 29 | 30
BCV130 | DX09 | DIO1 | 130 | 2 | 9 | 0 | 1 | 23 |  |  | DI | [9 empty] | 2.9\0.1:23 |  |  |  | S | [6 empty] | F1 | 31 | 32
BCV130 | DX09 | DIO1 | 130 | 2 | 9 | 0 | 1 | 24 |  |  | DI | 4 | BCV130PWS01 | PWS01 | PRIMARY CRUSHING DISCHARGE CONVEYOR | Pullwire Switch 1 | Healthy | K203 | BCV130 |  | 2.9\0.1:24 | BR4-2110-E-00114 | 0 |  | D | [6 empty] | F1 | 33 | 34
BCV130 | DX09 | DIO1 | 130 | 2 | 9 | 0 | 1 | 25 |  |  | DI | 4 | BCV130PWS02 | PWS02 | PRIMARY CRUSHING DISCHARGE CONVEYOR | Pullwire Switch 2 | Healthy | K214 | BCV130 |  | 2.9\0.1:25 | BR4-2110-E-00114 | 0 |  | D | [6 empty] | F1 | 35 | 36
BCV130 | DX09 | DIO1 | 130 | 2 | 9 | 0 | 1 | 26 |  |  | DI | 4 | BCV130PWS03 | PWS03 | PRIMARY CRUSHING DISCHARGE CONVEYOR | Pullwire Switch 3 | Healthy | K225 | BCV130 |  | 2.9\0.1:26 | BR4-2110-E-00114 | 0 |  | D | [6 empty] | F1 | 37 | 38
BCV130 | DX09 | DIO1 | 130 | 2 | 9 | 0 | 1 | 27 |  |  | DI | 4 | BCV130PWS04 | PWS04 | PRIMARY CRUSHING DISCHARGE CONVEYOR | Pullwire Switch 4 | Healthy | K236 | BCV130 |  | 2.9\0.1:27 | BR4-2110-E-00114 | 0 |  | D | [6 empty] | F1 | 39 | 40
BCV130 | DX09 | DIO1 | 130 | 2 | 9 | 0 | 1 | 28 |  |  | DI | 4 | BCV130ZS01 | ZS01 | PRIMARY CRUSHING DISCHARGE CONVEYOR | Take-Up Trolley Outer Position | Healthy |  | BCV130 |  | 2.9\0.1:28 | BR4-2110-E-00115 | 0 |  | S | [6 empty] | F1 | 41 | 42
BCV130 | DX09 | DIO1 | 130 | 2 | 9 | 0 | 1 | 29 |  |  | DI | 4 | BCV130ZS02 | ZS02 | PRIMARY CRUSHING DISCHARGE CONVEYOR | Take-Up Trolley Inner Position | Healthy |  | BCV130 |  | 2.9\0.1:29 | BR4-2110-E-00115 | 0 |  | S | [6 empty] | F1 | 43 | 44
BCV130 | DX09 | DIO1 | 130 | 2 | 9 | 0 | 1 | 30 |  |  | DI | 4 | BCV130ZS03 | ZS03 | PRIMARY CRUSHING DISCHARGE CONVEYOR | Take-Up Tower Upper Position | Healthy |  | BCV130 |  | 2.9\0.1:30 | BR4-2110-E-00115 | 0 |  | S | [6 empty] | F1 | 45 | 46
BCV130 | DX09 | DIO1 | 130 | 2 | 9 | 0 | 1 | 31 |  |  | DI | 4 | BCV130ZS04 | ZS04 | PRIMARY CRUSHING DISCHARGE CONVEYOR | Take-Up Tower Lower Position | Healthy |  | BCV130 |  | 2.9\0.1:31 | BR4-2110-E-00115 | 0 |  | S | [6 empty] | F1 | 47 | 48
BCV130 | DX09 | DIO1 | 130 | 2 | 9 | 0 | 2 | 0 | BMXFCW303 | BMXDDI3202K | DI | 4 | BCV130BDS01 | BDS01 | PRIMARY CRUSHING DISCHARGE CONVEYOR | Belt Drift Switch 1 | Healthy |  | BCV130 |  | 2.9\0.2:0 | BR4-2110-E-00115 | 0 |  | S | [6 empty] | F2 | 1 | 2
BCV130 | DX09 | DIO1 | 130 | 2 | 9 | 0 | 2 | 1 |  |  | DI | 4 | BCV130BDS02 | BDS02 | PRIMARY CRUSHING DISCHARGE CONVEYOR | Belt Drift Switch 2 | Healthy |  | BCV130 |  | 2.9\0.2:1 | BR4-2110-E-00115 | 0 |  | S | [6 empty] | F2 | 3 | 4
BCV130 | DX09 | DIO1 | 130 | 2 | 9 | 0 | 2 | 2 |  |  | DI | 4 | BCV130BDS03 | BDS03 | PRIMARY CRUSHING DISCHARGE CONVEYOR | Belt Drift Switch 3 | Healthy |  | BCV130 |  | 2.9\0.2:2 | BR4-2110-E-00115 | 0 |  | S | [6 empty] | F2 | 5 | 6
BCV130 | DX09 | DIO1 | 130 | 2 | 9 | 0 | 2 | 3 |  |  | DI | 4 | BCV130BDS04 | BDS04 | PRIMARY CRUSHING DISCHARGE CONVEYOR | Belt Drift Switch 4 | Healthy |  | BCV130 |  | 2.9\0.2:3 | BR4-2110-E-00115 | 0 |  | S | [6 empty] | F2 | 7 | 8
BCV130 | DX09 | DIO1 | 130 | 2 | 9 | 0 | 2 | 4 |  |  | DI | 4 | BCV130CH03BCS01 | BCS01 | PRIMARY CRUSHING DISCHARGE CONVEYOR | Blocked Chute Switch 1 | Healthy |  | BCV130CH03 |  | 2.9\0.2:4 | BR4-2110-E-00115 | 0 |  | S | [6 empty] | F2 | 9 | 10
BCV130 | DX09 | DIO1 | 130 | 2 | 9 | 0 | 2 | 5 |  |  | DI | 4 | BCV130CH03BCS02 | BCS02 | PRIMARY CRUSHING DISCHARGE CONVEYOR | Blocked Chute Switch 2 | Healthy |  | BCV130CH03 |  | 2.9\0.2:5 | BR4-2110-E-00115 | 0 |  | S | [6 empty] | F2 | 11 | 12
BCV130 | DX09 | DIO1 | 130 | 2 | 9 | 0 | 2 | 6 |  |  | DI | [9 empty] | 2.9\0.2:6 |  |  |  | S | [6 empty] | F2 | 13 | 14
BCV130 | DX09 | DIO1 | 130 | 2 | 9 | 0 | 2 | 7 |  |  | DI | 5 | BCV130BK01LCS01 | STT01 | PRIMARY CRUSHING DISCHARGE CONVEYOR DRIVE BRAKE | Start Pushbutton | Activated | STT01 | BCV130BK01 |  | 2.9\0.2:7 | BR4-2110-E-00216 | A |  | S | [6 empty] | F2 | 15 | 16
BCV130 | DX09 | DIO1 | 130 | 2 | 9 | 0 | 2 | 8 |  |  | DI | 5 | BCV130BK01LCS01 | STP01 | PRIMARY CRUSHING DISCHARGE CONVEYOR DRIVE BRAKE | Stop Pushbutton | Activated | STP01 | BCV130BK01 |  | 2.9\0.2:8 | BR4-2110-E-00216 | A |  | S | [6 empty] | F2 | 17 | 18
BCV130 | DX09 | DIO1 | 130 | 2 | 9 | 0 | 2 | 9 |  |  | DI | 5 | BCV130BK01LCS01 | SY01 | PRIMARY CRUSHING DISCHARGE CONVEYOR DRIVE BRAKE | Emergency Stop Relay | Healthy | K275 | BCV130BK01 |  | 2.9\0.2:9 | BR4-2110-E-00114 | 0 |  | S | [6 empty] | F2 | 19 | 20
BCV130 | DX09 | DIO1 | 130 | 2 | 9 | 0 | 2 | 10 |  |  | DI | [9 empty] | 2.9\0.2:10 |  |  |  | S | [6 empty] | F2 | 21 | 22
BCV130 | DX09 | DIO1 | 130 | 2 | 9 | 0 | 2 | 11 |  |  | DI | [9 empty] | 2.9\0.2:11 |  |  |  | S | [6 empty] | F2 | 23 | 24
BCV130 | DX09 | DIO1 | 130 | 2 | 9 | 0 | 2 | 12 |  |  | DI | 5 | BCV130FN01LCS01 | STT01 | PRIMARY CRUSHING DISCHARGE CONVEYOR MOTOR COOLING FAN | Start Pushbutton | Activated | STT01 | BCV130FN01 |  | 2.9\0.2:12 | BR4-2110-E-00231 | 0 |  | S | [6 empty] | F2 | 25 | 26
BCV130 | DX09 | DIO1 | 130 | 2 | 9 | 0 | 2 | 13 |  |  | DI | 5 | BCV130FN01LCS01 | STP01 | PRIMARY CRUSHING DISCHARGE CONVEYOR MOTOR COOLING FAN | Stop Pushbutton | Activated | STP01 | BCV130FN01 |  | 2.9\0.2:13 | BR4-2110-E-00231 | 0 |  | S | [6 empty] | F2 | 27 | 28
BCV130 | DX09 | DIO1 | 130 | 2 | 9 | 0 | 2 | 14 |  |  | DI | 5 | BCV130FN02LCS01 | STT01 | PRIMARY CRUSHING DISCHARGE CONVEYOR REDUCER COOLING FAN | Start Pushbutton | Activated | STT01 | BCV130FN02 |  | 2.9\0.2:14 | BR4-2110-E-00216 | 0 |  | S | [6 empty] | F2 | 29 | 30
BCV130 | DX09 | DIO1 | 130 | 2 | 9 | 0 | 2 | 15 |  |  | DI | 5 | BCV130FN02LCS01 | STP01 | PRIMARY CRUSHING DISCHARGE CONVEYOR REDUCER COOLING FAN | Stop Pushbutton | Activated | STP01 | BCV130FN02 |  | 2.9\0.2:15 | BR4-2110-E-00216 | 0 |  | S | [6 empty] | F2 | 31 | 32
BCV130 | DX09 | DIO1 | 130 | 2 | 9 | 0 | 2 | 16 |  |  | DI | [9 empty] | 2.9\0.2:16 |  |  |  | S | [6 empty] | F3 | 1 | 2
BCV130 | DX09 | DIO1 | 130 | 2 | 9 | 0 | 2 | 17 |  |  | DI | 4 | BCV130BK01PS01 | PS01 | PRIMARY CRUSHING DISCHARGE CONVEYOR BRAKE | Brake | Lifted |  | BCV130BK01 |  | 2.9\0.2:17 | BR4-2110-E-00117 | 0 |  | S | [6 empty] | F3 | 3 | 4
BCV130 | DX09 | DIO1 | 130 | 2 | 9 | 0 | 2 | 18 |  |  | DI | 4 | BCV130BK01PS01 | PS01A | PRIMARY CRUSHING DISCHARGE CONVEYOR BRAKE | Brake Pressure | Low |  | BCV130BK01 |  | 2.9\0.2:18 | BR4-2110-E-00117 | 0 |  | S | [6 empty] | F3 | 5 | 6
BCV130 | DX09 | DIO1 | 130 | 2 | 9 | 0 | 2 | 19 |  |  | DI | 4 | BCV130BK01ZS01 | ZS01A | PRIMARY CRUSHING DISCHARGE CONVEYOR BRAKE | Brake Caliper 1 | Lifted |  | BCV130BK01 |  | 2.9\0.2:19 | BR4-2110-E-00117 | 0 |  | S | [6 empty] | F3 | 7 | 8
BCV130 | DX09 | DIO1 | 130 | 2 | 9 | 0 | 2 | 20 |  |  | DI | 4 | BCV130BK01ZS01 | ZS01B | PRIMARY CRUSHING DISCHARGE CONVEYOR BRAKE | Brake Caliper 1 Wear | Healthy |  | BCV130BK01 |  | 2.9\0.2:20 | BR4-2110-E-00117 | 0 |  | S | [6 empty] | F3 | 9 | 10
BCV130 | DX09 | DIO1 | 130 | 2 | 9 | 0 | 2 | 21 |  |  | DI | 4 | BCV130BK01ZS02 | ZS02A | PRIMARY CRUSHING DISCHARGE CONVEYOR BRAKE | Brake Caliper 2 | Lifted |  | BCV130BK01 |  | 2.9\0.2:21 | BR4-2110-E-00117 | 0 |  | S | [6 empty] | F3 | 11 | 12
BCV130 | DX09 | DIO1 | 130 | 2 | 9 | 0 | 2 | 22 |  |  | DI | 4 | BCV130BK01ZS02 | ZS02B | PRIMARY CRUSHING DISCHARGE CONVEYOR BRAKE | Brake Caliper 2 Wear | Healthy |  | BCV130BK01 |  | 2.9\0.2:22 | BR4-2110-E-00117 | 0 |  | S | [6 empty] | F3 | 13 | 14
BCV130 | DX09 | DIO1 | 130 | 2 | 9 | 0 | 2 | 23 |  |  | DI | 4 | BCV130BK01UI01 | LS01 | PRIMARY CRUSHING DISCHARGE CONVEYOR DRIVE BRAKE HPU | Level | Low |  | BCV130BK01 |  | 2.9\0.2:23 | BR4-2110-E-00117 | 0 |  | S | [6 empty] | F3 | 15 | 16
BCV130 | DX09 | DIO1 | 130 | 2 | 9 | 0 | 2 | 24 |  |  | DI | 4 | BCV130BK01UI01 | TS01 | PRIMARY CRUSHING DISCHARGE CONVEYOR DRIVE BRAKE HPU | Temperature | High |  | BCV130BK01 |  | 2.9\0.2:24 | BR4-2110-E-00117 | 0 |  | S | [6 empty] | F3 | 17 | 18
BCV130 | DX09 | DIO1 | 130 | 2 | 9 | 0 | 2 | 25 |  |  | DI | 4 | BCV130GB01LCS01 | STT01 | PRIMARY CRUSHING DISCHARGE CONVEYOR REDUCER LUBRICATION PUMP | Start Pushbutton | Activated | STT01 | BCV130GB01 |  | 2.9\0.2:25 | BR4-2110-E-00221 | A |  | S | [6 empty] | F3 | 19 | 20
BCV130 | DX09 | DIO1 | 130 | 2 | 9 | 0 | 2 | 26 |  |  | DI | 4 | BCV130GB01LCS01 | STP01 | PRIMARY CRUSHING DISCHARGE CONVEYOR REDUCER LUBRICATION PUMP | Stop Pushbutton | Activated | STP01 | BCV130GB01 |  | 2.9\0.2:26 | BR4-2110-E-00221 | A |  | S | [6 empty] | F3 | 21 | 22
BCV130 | DX09 | DIO1 | 130 | 2 | 9 | 0 | 2 | 27 |  |  | DI | [9 empty] | 2.9\0.2:27 |  |  |  | S | [6 empty] | F3 | 23 | 24
BCV130 | DX09 | DIO1 | 130 | 2 | 9 | 0 | 2 | 28 |  |  | DI | 4 | BCV130FT03 | FQ03 | PRIMARY CRUSHING DISCHARGE CONVEYOR ORE CONDITIONING SPRAYS | Flow Totaliser Pulse | Active |  | BCV130 |  | 2.9\0.2:28 | BR4-2110-E-00116 | 0 |  | S | [6 empty] | F3 | 25 | 26
BCV130 | DX09 | DIO1 | 130 | 2 | 9 | 0 | 2 | 29 |  |  | DI | 5 | BTN130PP01LCS01 | STT01 | TRANSFER TOWER SUMP PUMP | Start Pushbutton | Activated | STT01 | BTN130PP01 |  | 2.9\0.2:29 | BR4-2110-E-00213 | 0 |  | S | [6 empty] | F3 | 27 | 28
BCV130 | DX09 | DIO1 | 130 | 2 | 9 | 0 | 2 | 30 |  |  | DI | 5 | BTN130PP01LCS01 | STP01 | TRANSFER TOWER SUMP PUMP | Stop Pushbutton | Activated | STP01 | BTN130PP01 |  | 2.9\0.2:30 | BR4-2110-E-00213 | 0 |  | S | [6 empty] | F3 | 29 | 30
BCV130 | DX09 | DIO1 | 130 | 2 | 9 | 0 | 2 | 31 |  |  | DI | 5 | BTN130PP01LCS01 | IS01 | TRANSFER TOWER SUMP PUMP | Isolator | Closed | IS01 | BTN130PP01 |  | 2.9\0.2:31 | BR4-2110-E-00213 | 0 |  | S | [6 empty] | F3 | 31 | 32
BCV130 | DX09 | DIO1 | 130 | 2 | 9 | 0 | 3 | 0 | BMXFCW303 | BMXDDI3202K | DI | 4 | BCV130CH01ZS01 | ZS01 | PRIMARY CRUSHING DISCHARGE CONVEYOR | Impact Plate | Locked In Position |  | BCV130CH01 |  | 2.9\0.3:0 | BR4-2110-E-00115 | 0 |  | S | [6 empty] | F4 | 1 | 2
BCV130 | DX09 | DIO1 | 130 | 2 | 9 | 0 | 3 | 1 |  |  | DI | 4 | BCV130CH01ZS02 | ZS02 | PRIMARY CRUSHING DISCHARGE CONVEYOR | Impact Plate | Locked In Position |  | BCV130CH01 |  | 2.9\0.3:1 | BR4-2110-E-00115 | 0 |  | S | [6 empty] | F4 | 3 | 4
BCV130 | DX09 | DIO1 | 130 | 2 | 9 | 0 | 3 | 2 |  |  | DI | 4 | BCV130CH03ZS01 | ZS01 | PRIMARY CRUSHING DISCHARGE CONVEYOR | Rotable Chute | In Operating Position |  | BCV130CH03 |  | 2.9\0.3:2 | BR4-2110-E-00115 | 0 |  | S | [6 empty] | F4 | 5 | 6
BCV130 | DX09 | DIO1 | 130 | 2 | 9 | 0 | 3 | 3 |  |  | DI | [9 empty] | 2.9\0.3:3 |  |  |  | S | [6 empty] | F4 | 7 | 8
BCV130 | DX09 | DIO1 | 130 | 2 | 9 | 0 | 3 | 4 |  |  | DI | [9 empty] | 2.9\0.3:4 |  |  |  | S | [6 empty] | F4 | 9 | 10
BCV130 | DX09 | DIO1 | 130 | 2 | 9 | 0 | 3 | 5 |  |  | DI | [9 empty] | 2.9\0.3:5 |  |  |  | S | [6 empty] | F4 | 11 | 12
BCV130 | DX09 | DIO1 | 130 | 2 | 9 | 0 | 3 | 6 |  |  | DI | [9 empty] | 2.9\0.3:6 |  |  |  | S | [6 empty] | F4 | 13 | 14
BCV130 | DX09 | DIO1 | 130 | 2 | 9 | 0 | 3 | 7 |  |  | DI | [9 empty] | 2.9\0.3:7 |  |  |  | S | [6 empty] | F4 | 15 | 16
BCV130 | DX09 | DIO1 | 130 | 2 | 9 | 0 | 3 | 8 |  |  | DI | [9 empty] | 2.9\0.3:8 |  |  |  | S | [6 empty] | F4 | 17 | 18
BCV130 | DX09 | DIO1 | 130 | 2 | 9 | 0 | 3 | 9 |  |  | DI | [9 empty] | 2.9\0.3:9 |  |  |  | S | [6 empty] | F4 | 19 | 20
BCV130 | DX09 | DIO1 | 130 | 2 | 9 | 0 | 3 | 10 |  |  | DI | [9 empty] | 2.9\0.3:10 |  |  |  | S | [6 empty] | F4 | 21 | 22
BCV130 | DX09 | DIO1 | 130 | 2 | 9 | 0 | 3 | 11 |  |  | DI | [9 empty] | 2.9\0.3:11 |  |  |  | S | [6 empty] | F4 | 23 | 24
BCV130 | DX09 | DIO1 | 130 | 2 | 9 | 0 | 3 | 12 |  |  | DI | [9 empty] | 2.9\0.3:12 |  |  |  | S | [6 empty] | F4 | 25 | 26
BCV130 | DX09 | DIO1 | 130 | 2 | 9 | 0 | 3 | 13 |  |  | DI | [9 empty] | 2.9\0.3:13 |  |  |  | S | [6 empty] | F4 | 27 | 28
BCV130 | DX09 | DIO1 | 130 | 2 | 9 | 0 | 3 | 14 |  |  | DI | [9 empty] | 2.9\0.3:14 |  |  |  | S | [6 empty] | F4 | 29 | 30
BCV130 | DX09 | DIO1 | 130 | 2 | 9 | 0 | 3 | 15 |  |  | DI | [9 empty] | 2.9\0.3:15 |  |  |  | S | [6 empty] | F4 | 31 | 32
BCV130 | DX09 | DIO1 | 130 | 2 | 9 | 0 | 3 | 16 |  |  | DI | [9 empty] | 2.9\0.3:16 |  |  |  | S | [6 empty] | F4 | 33 | 34
BCV130 | DX09 | DIO1 | 130 | 2 | 9 | 0 | 3 | 17 |  |  | DI | [9 empty] | 2.9\0.3:17 |  |  |  | S | [6 empty] | F4 | 35 | 36
BCV130 | DX09 | DIO1 | 130 | 2 | 9 | 0 | 3 | 18 |  |  | DI | [9 empty] | 2.9\0.3:18 |  |  |  | S | [6 empty] | F4 | 37 | 38
BCV130 | DX09 | DIO1 | 130 | 2 | 9 | 0 | 3 | 19 |  |  | DI | [9 empty] | 2.9\0.3:19 |  |  |  | S | [6 empty] | F4 | 39 | 40
BCV130 | DX09 | DIO1 | 130 | 2 | 9 | 0 | 3 | 20 |  |  | DI | [9 empty] | 2.9\0.3:20 |  |  |  | S | [6 empty] | F4 | 41 | 42
BCV130 | DX09 | DIO1 | 130 | 2 | 9 | 0 | 3 | 21 |  |  | DI | [9 empty] | 2.9\0.3:21 |  |  |  | S | [6 empty] | F4 | 43 | 44
BCV130 | DX09 | DIO1 | 130 | 2 | 9 | 0 | 3 | 22 |  |  | DI | [9 empty] | 2.9\0.3:22 |  |  |  | S | [6 empty] | F4 | 45 | 46
BCV130 | DX09 | DIO1 | 130 | 2 | 9 | 0 | 3 | 23 |  |  | DI | [9 empty] | 2.9\0.3:23 |  |  |  | S | [6 empty] | F4 | 47 | 48
BCV130 | DX09 | DIO1 | 130 | 2 | 9 | 0 | 3 | 24 |  |  | DI | [9 empty] | 2.9\0.3:24 |  |  |  | S | [6 empty] | F4 | 49 | 50
BCV130 | DX09 | DIO1 | 130 | 2 | 9 | 0 | 3 | 25 |  |  | DI | [9 empty] | 2.9\0.3:25 |  |  |  | S | [6 empty] | F4 | 51 | 52
BCV130 | DX09 | DIO1 | 130 | 2 | 9 | 0 | 3 | 26 |  |  | DI | [9 empty] | 2.9\0.3:26 |  |  |  | S | [6 empty] | F3 | 41 | 42
BCV130 | DX09 | DIO1 | 130 | 2 | 9 | 0 | 3 | 27 |  |  | DI | [9 empty] | 2.9\0.3:27 |  |  |  | S | [6 empty] | F3 | 43 | 44
BCV130 | DX09 | DIO1 | 130 | 2 | 9 | 0 | 3 | 28 |  |  | DI | [9 empty] | 2.9\0.3:28 |  |  |  | S | [6 empty] | F3 | 45 | 46
BCV130 | DX09 | DIO1 | 130 | 2 | 9 | 0 | 3 | 29 |  |  | DI | [9 empty] | 2.9\0.3:29 |  |  |  | S | [6 empty] | F3 | 47 | 48
BCV130 | DX09 | DIO1 | 130 | 2 | 9 | 0 | 3 | 30 |  |  | DI | [9 empty] | 2.9\0.3:30 |  |  |  | S | [6 empty] | F3 | 49 | 50
BCV130 | DX09 | DIO1 | 130 | 2 | 9 | 0 | 3 | 31 |  |  | DI | [9 empty] | 2.9\0.3:31 |  |  |  | S | [6 empty] | F3 | 51 | 52
BCV130 | DX09 | DIO1 | 130 | 2 | 9 | 0 | 4 | 0 | BMXFTB2010 | BMXDDO1602 | DO | 4 | BCV130BK01SV01 | SV01 | PRIMARY CRUSHING DISCHARGE CONVEYOR | Brake Lift Solenoid |  |  | BCV130BK01 |  | 2.9\0.4:0 | BR4-2110-E-00117 | 0 |  | S | [6 empty] | F5 | 1 | 2
BCV130 | DX09 | DIO1 | 130 | 2 | 9 | 0 | 4 | 1 |  |  | DO | 4 | BCV130BK01SV02 | SV02 | PRIMARY CRUSHING DISCHARGE CONVEYOR | Brake Release Solenoid |  |  | BCV130BK01 |  | 2.9\0.4:1 | BR4-2110-E-00117 | 0 |  | S | [6 empty] | F5 | 3 | 4
BCV130 | DX09 | DIO1 | 130 | 2 | 9 | 0 | 4 | 2 |  |  | DO | 4 | BCV130YA01 | YA01 | PRIMARY CRUSHING DISCHARGE CONVEYOR | Bcv130 Start Up Warning Siren |  |  | BCV130 |  | 2.9\0.4:2 | BR4-2110-E-00117 | 0 |  | S | [6 empty] | F5 | 5 | 6
BCV130 | DX09 | DIO1 | 130 | 2 | 9 | 0 | 4 | 3 |  |  | DO | 4 | BSR130DB05 | SR01 | TRANSFER TOWER | Lighting Relay |  |  | BSR130DB05 |  | 2.9\0.4:3 | BR4-2110-E-00117 | 0 |  | S | [6 empty] | F5 | 7 | 8
BCV130 | DX09 | DIO1 | 130 | 2 | 9 | 0 | 4 | 4 |  |  | DO | [9 empty] | 2.9\0.4:4 |  |  |  | S | [6 empty] | F5 | 9 | 10
BCV130 | DX09 | DIO1 | 130 | 2 | 9 | 0 | 4 | 5 |  |  | DO | 4 | BTN130PP01SV02 | SV02 | TRANSFER TOWER SUMP PUMP | Agitator Solenoid Valve |  |  | BTN130PP01 |  | 2.9\0.4:5 | BR4-2110-E-00117 | 0 |  | S | [6 empty] | F5 | 11 | 12
BCV130 | DX09 | DIO1 | 130 | 2 | 9 | 0 | 4 | 6 |  |  | DO | [9 empty] | 2.9\0.4:6 |  |  |  | S | [6 empty] | F5 | 13 | 14
BCV130 | DX09 | DIO1 | 130 | 2 | 9 | 0 | 4 | 7 |  |  | DO | 4 | BCV130SV09 | SV09 | PRIMARY CRUSHING DISCHARGE CONVEYOR | Ore Conditioning Spray Bar (1 Sprays) |  |  | BCV130 |  | 2.9\0.4:7 | BR4-2110-E-00117 | 0 |  | S | [6 empty] | F5 | 15 | 16
BCV130 | DX09 | DIO1 | 130 | 2 | 9 | 0 | 4 | 8 |  |  | DO | 4 | BCV130SV08 | SV08 | PRIMARY CRUSHING DISCHARGE CONVEYOR | Ore Conditioning Spray Bar (2 Sprays) |  |  | BCV130 |  | 2.9\0.4:8 | BR4-2110-E-00117 | 0 |  | S | [6 empty] | F5 | 17 | 18
BCV130 | DX09 | DIO1 | 130 | 2 | 9 | 0 | 4 | 9 |  |  | DO | 4 | BCV130SV07 | SV07 | PRIMARY CRUSHING DISCHARGE CONVEYOR | Ore Conditioning Spray Bar (4 Sprays) |  |  | BCV130 |  | 2.9\0.4:9 | BR4-2110-E-00117 | 0 |  | S | [6 empty] | F5 | 19 | 20
BCV130 | DX09 | DIO1 | 130 | 2 | 9 | 0 | 4 | 10 |  |  | DO | [9 empty] | 2.9\0.4:10 |  |  |  | S | [6 empty] | F5 | 21 | 22
BCV130 | DX09 | DIO1 | 130 | 2 | 9 | 0 | 4 | 11 |  |  | DO | [9 empty] | 2.9\0.4:11 |  |  |  | S | [6 empty] | F5 | 23 | 24
BCV130 | DX09 | DIO1 | 130 | 2 | 9 | 0 | 4 | 12 |  |  | DO | [9 empty] | 2.9\0.4:12 |  |  |  | S | [6 empty] | F5 | 25 | 26
BCV130 | DX09 | DIO1 | 130 | 2 | 9 | 0 | 4 | 13 |  |  | DO | [9 empty] | 2.9\0.4:13 |  |  |  | S | [6 empty] | F5 | 27 | 28
BCV130 | DX09 | DIO1 | 130 | 2 | 9 | 0 | 4 | 14 |  |  | DO | [9 empty] | 2.9\0.4:14 |  |  |  | S | [6 empty] | F5 | 29 | 30
BCV130 | DX09 | DIO1 | 130 | 2 | 9 | 0 | 4 | 15 |  |  | DO | [9 empty] | 2.9\0.4:15 |  |  |  | S | [6 empty] | F5 | 31 | 32
BCV130 | DX09 | DIO1 | 130 | 2 | 9 | 0 | 5 | 0 | BMXFTW301S | BMEAHI0812 | AI | 4 | BTN130SM01LT01 | LT01 | TRANSFER TOWER SUMP | Sump Level |  | % | BTN130SM01 | REAL | 2.9\0.5:0 | BR4-2110-E-00116 | 0 |  | S |  | 0 | 100 | 0 | 100 | #.# EU | F5 | 33 | 34
BCV130 | DX09 | DIO1 | 130 | 2 | 9 | 0 | 5 | 1 |  |  | AI | 4 | BTN130PT01 | PT01 | TRANSFER TOWER | Pressure Transmitter |  | kPa | BTN130 | REAL | 2.9\0.5:1 | BR4-2110-E-00115 | 0 |  | S | [6 empty] | F5 | 35 | 36
BCV130 | DX09 | DIO1 | 130 | 2 | 9 | 0 | 5 | 2 |  |  | AI | 4 | BCV130FT03 | FT03 | PRIMARY CRUSHING DISCHARGE CONVEYOR ORE CONDITIONING SPRAYS | Flow Rate |  | m3/h | BCV130 | REAL | 2.9\0.5:2 | BR4-2110-E-00116 | 0 |  | S |  | 0 | 10 | 0 | 10 | #.# EU | F5 | 37 | 38
BCV130 | DX09 | DIO1 | 130 | 2 | 9 | 0 | 5 | 3 |  |  | AI | 4 | BCV130PP04FT01 | FT01 | PRIMARY CRUSHING DISCHARGE CONVEYOR REDUCER LUBRICATION PUMP | Flow Rate |  | m3/h | BCV130PP04 | REAL | 2.9\0.5:3 | BR4-2110-E-00116 | 0 |  | S |  | 0 | 10 | 0 | 10 | #.# EU | F5 | 39 | 40
BCV130 | DX09 | DIO1 | 130 | 2 | 9 | 0 | 5 | 4 |  |  | AI | [9 empty] | 2.9\0.5:4 |  |  |  | S | [6 empty] | F5 | 41 | 42
BCV130 | DX09 | DIO1 | 130 | 2 | 9 | 0 | 5 | 5 |  |  | AI | [9 empty] | 2.9\0.5:5 |  |  |  | S | [6 empty] | F5 | 43 | 44
BCV130 | DX09 | DIO1 | 130 | 2 | 9 | 0 | 5 | 6 |  |  | AI | [9 empty] | 2.9\0.5:6 |  |  |  | S | [6 empty] | F5 | 45 | 46
BCV130 | DX09 | DIO1 | 130 | 2 | 9 | 0 | 5 | 7 |  |  | AI | [9 empty] | 2.9\0.5:7 |  |  |  | S | [6 empty] | F5 | 47 | 48
BCV130 | DX09 | DIO1 | 130 | 2 | 9 | 0 | 6 | 0 | BMXFCW301S | BMXART0814 | RTDI | 4 | BCV130RTD01 | RTD01 |  | Motor Red Winding 1 Temperature |  | C | BCV130 | REAL | 2.9\0.6:0 | BR4-2110-E-00118 | 0 |  | S |  | 0 | 200 | 0 | 200 | # EU | F6 | 1 | 2 | 3
BCV130 | DX09 | DIO1 | 130 | 2 | 9 | 0 | 6 | 1 | BMXFCW301S |  | RTDI | 4 | BCV130RTD02 | RTD02 |  | Motor White Winding 1 Temperature |  | C | BCV130 | REAL | 2.9\0.6:1 | BR4-2110-E-00118 | 0 |  | S |  | 0 | 200 | 0 | 200 | # EU | F6 | 4 | 5 | 6
BCV130 | DX09 | DIO1 | 130 | 2 | 9 | 0 | 6 | 2 |  |  | RTDI | 4 | BCV130RTD03 | RTD03 |  | Motor Blue Winding 1 Temperature |  | C | BCV130 | REAL | 2.9\0.6:2 | BR4-2110-E-00118 | 0 |  | S |  | 0 | 200 | 0 | 200 | # EU | F6 | 7 | 8 | 9
BCV130 | DX09 | DIO1 | 130 | 2 | 9 | 0 | 6 | 3 |  |  | RTDI | 4 | BCV130RTD04 | RTD04 |  | Motor Red Winding 2 Temperature |  | C | BCV130 | REAL | 2.9\0.6:3 | BR4-2110-E-00118 | 0 |  | S |  | 0 | 200 | 0 | 200 | # EU | F6 | 10 | 11 | 12
BCV130 | DX09 | DIO1 | 130 | 2 | 9 | 0 | 6 | 4 |  |  | RTDI | 4 | BCV130RTD05 | RTD05 |  | Motor White Winding 2 Temperature |  | C | BCV130 | REAL | 2.9\0.6:4 | BR4-2110-E-00118 | 0 |  | S |  | 0 | 200 | 0 | 200 | # EU | F6 | 13 | 14 | 15
BCV130 | DX09 | DIO1 | 130 | 2 | 9 | 0 | 6 | 5 |  |  | RTDI | 4 | BCV130RTD06 | RTD06 |  | Motor Blue Winding 2 Temperature |  | C | BCV130 | REAL | 2.9\0.6:5 | BR4-2110-E-00118 | 0 |  | S |  | 0 | 200 | 0 | 200 | # EU | F6 | 16 | 17 | 18
BCV130 | DX09 | DIO1 | 130 | 2 | 9 | 0 | 6 | 6 |  |  | RTDI | 4 | BCV130RTD07 | RTD07 |  | Motor Non Drive End Bearing Temperature |  | C | BCV130 | REAL | 2.9\0.6:6 | BR4-2110-E-00118 | 0 |  | S |  | 0 | 200 | 0 | 200 | # EU | F6 | 19 | 20 | 21
BCV130 | DX09 | DIO1 | 130 | 2 | 9 | 0 | 6 | 7 |  |  | RTDI | 4 | BCV130RTD08 | RTD08 |  | Motor Drive End Bearing Temperature |  | C | BCV130 | REAL | 2.9\0.6:7 | BR4-2110-E-00118 | 0 |  | S |  | 0 | 200 | 0 | 200 | # EU | F6 | 22 | 23 | 24
BCV130 | DX09 | DIO1 | 130 | 2 | 9 | 0 | 7 | 0 | BMXFCW301S | BMXART0814 | RTDI | 4 | BCV130RTD09 | RTD09 |  | Motor Air Inlet Ambient Temperature |  | C | BCV130 | REAL | 2.9\0.7:0 | BR4-2110-E-00118 | 0 |  | S |  | 0 | 200 | 0 | 200 | # EU | F6 | 25 | 26 | 27
BCV130 | DX09 | DIO1 | 130 | 2 | 9 | 0 | 7 | 1 | BMXFCW301S |  | RTDI | 4 | BCV130GB01RTD01 | RTD01 |  | Gearboxdrive End Bearing Temperature |  | C | BCV130GB01 | REAL | 2.9\0.7:1 | BR4-2110-E-00118 | 0 |  | S |  | 0 | 200 | 0 | 200 | # EU | F6 | 28 | 29 | 30
BCV130 | DX09 | DIO1 | 130 | 2 | 9 | 0 | 7 | 2 |  |  | RTDI | 4 | BCV130GB01RTD02 | RTD02 |  | Gearboxoil Temperature |  | C | BCV130GB01 | REAL | 2.9\0.7:2 | BR4-2110-E-00118 | 0 |  | S |  | 0 | 200 | 0 | 200 | # EU | F6 | 31 | 32 | 33
BCV130 | DX09 | DIO1 | 130 | 2 | 9 | 0 | 7 | 3 |  |  | RTDI | [9 empty] | 2.9\0.7:3 |  |  |  | S | [6 empty] | F6 | 34 | 35 | 36
BCV130 | DX09 | DIO1 | 130 | 2 | 9 | 0 | 7 | 4 |  |  | RTDI | [9 empty] | 2.9\0.7:4 |  |  |  | S | [6 empty] | F6 | 37 | 38 | 39
BCV130 | DX09 | DIO1 | 130 | 2 | 9 | 0 | 7 | 5 |  |  | RTDI | [9 empty] | 2.9\0.7:5 |  |  |  | S | [6 empty] | F6 | 40 | 41 | 42
BCV130 | DX09 | DIO1 | 130 | 2 | 9 | 0 | 7 | 6 |  |  | RTDI | [9 empty] | 2.9\0.7:6 |  |  |  | S | [6 empty] | F6 | 43 | 44 | 45
BCV130 | DX09 | DIO1 | 130 | 2 | 9 | 0 | 7 | 7 |  |  | RTDI | [9 empty] | 2.9\0.7:7 |  |  |  | S | [6 empty] | F6 | 46 | 47 | 48
BCV130 | DX09 | DIO1 | 130 | 2 | 9 | 0 | 8 |  |  | BMXX0 |  | 0 | [8 empty] | 2.9\0.8:
BCV130 | DX09 | DIO1 | 130 | 2 | 9 | 0 | 8 |  |  |  |  | 0 | [8 empty] | 2.9\0.8:
BCV130 | DX09 | DIO1 | 130 | 2 | 9 | 0 | 8 |  |  |  |  | 0 | [8 empty] | 2.9\0.8:
BCV130 | DX09 | DIO1 | 130 | 2 | 9 | 0 | 8 |  |  |  |  | 0 | [8 empty] | 2.9\0.8:
BCV130 | DX09 | DIO1 | 130 | 2 | 9 | 0 | 9 |  |  | BMXX0 |  | 0 | [8 empty] | 2.9\0.9:
BCV130 | DX09 | DIO1 | 130 | 2 | 9 | 0 | 9 |  |  |  |  | 0 | [8 empty] | 2.9\0.9:
BCV130 | DX09 | DIO1 | 130 | 2 | 9 | 0 | 9 |  |  |  |  | 0 | [8 empty] | 2.9\0.9:
BCV130 | DX09 | DIO1 | 130 | 2 | 9 | 0 | 9 |  |  |  |  | 0 | [8 empty] | 2.9\0.9:
BCV130 | DX09 | DIO1 | 130 | 2 | 9 | 0 | 10 |  |  | BMXX0 |  | 0 | [8 empty] | 2.9\0.10:
BCV130 | DX09 | DIO1 | 130 | 2 | 9 | 0 | 10 |  |  |  |  | 0 | [8 empty] | 2.9\0.10:
BCV130 | DX09 | DIO1 | 130 | 2 | 9 | 0 | 10 |  |  |  |  | 0 | [8 empty] | 2.9\0.10:
BCV130 | DX09 | DIO1 | 130 | 2 | 9 | 0 | 10 |  |  |  |  | 0 | [8 empty] | 2.9\0.10:
BCV130 | DX09 | DIO1 | 130 | 2 | 9 | 0 | 11 |  |  | BMXX0 |  | 0 | [8 empty] | 2.9\0.11:
BCV130 | DX09 | DIO1 | 130 | 2 | 9 | 0 | 11 |  |  |  |  | 0 | [8 empty] | 2.9\0.11:
BCV130 | DX09 | DIO1 | 130 | 2 | 9 | 0 | 11 |  |  |  |  | 0 | [8 empty] | 2.9\0.11:
BCV130 | DX09 | DIO1 | 130 | 2 | 9 | 0 | 11 |  |  |  |  | 0 | [8 empty] | 2.9\0.11:
[10 empty] | * | [5 empty] | Safety Relay (To Sumation Relay BSR130DX02) |  | K453 | BCV130 |  |  | BR4-2110-E-00122 | 1 | [8 empty] | F7 | 1 | 2 | 3 | 4
[10 empty] | * |  | 1 | BCV130FN01LCS01 | SY01 | PRIMARY CRUSHING DISCHARGE CONVEYOR MOTOR COOLING FAN | Lock Off Stop |  | SUB LINK | BCV130FN01 |  |  | BR4-2110-E-00231 | 0 | [8 empty] | F7 | 5 | 6 | 7 | 8
[10 empty] | * |  | 2 | BCV130GB01LCS01 | LOS01 | PRIMARY CRUSHING DISCHARGE CONVEYOR REDUCER COOLING FAN | Lock Off Stop |  | SUB LINK | BCV130FN02 / PP04 |  |  | BR4-2110-E-00122 | 1 | [8 empty] | F7 | 9 | 10 | 11 | 12
[10 empty] | * |  | 1 | BTN130PP01LCS01 | SY01 | TRANSFER TOWER SUMP PUMP | Emergency Stop Relay |  | SUB LINK | BTN130PP01 |  |  | BR4-2110-E-00213 | 0 | [8 empty] | F7 | 13 | 14 | 15 | 16
[32 empty] | F7 | 17 | 18 | 19 | 20
[10 empty] | PNOZs4 | Safety Relay | 1 | BCV130PWS01 | PWS01 | PRIMARY CRUSHING DISCHARGE CONVEYOR | Pullwire Switch 1 |  | K203 | BCV130 |  |  | BR4-2110-E-00114 | 0 | [8 empty] | F7 | 21 | 22 | 23 | 24
[10 empty] | PNOZs4 | Safety Relay | 1 | BCV130PWS02 | PWS02 | PRIMARY CRUSHING DISCHARGE CONVEYOR | Pullwire Switch 2 |  | K214 | BCV130 |  |  | BR4-2110-E-00114 | 0 | [8 empty] | F7 | 25 | 26 | 27 | 28
[10 empty] | PNOZs4 | Safety Relay | 1 | BCV130PWS03 | PWS03 | PRIMARY CRUSHING DISCHARGE CONVEYOR | Pullwire Switch 3 |  | K225 | BCV130 |  |  | BR4-2110-E-00114 | 0 | [8 empty] | F7 | 29 | 30 | 31 | 32
[10 empty] | PNOZs4 | Safety Relay | 1 | BCV130PWS04 | PWS04 | PRIMARY CRUSHING DISCHARGE CONVEYOR | Pullwire Switch 4 |  | K236 | BCV130 |  |  | BR4-2110-E-00114 | 0 | [8 empty] | F7 | 33 | 34 | 35 | 36
[10 empty] | PNOZs4 | Safety Relay | 1 | BCV130LCS01 | LOS01 | PRIMARY CRUSHING DISCHARGE CONVEYOR | Emergency Stop Relay |  | K253 | BCV130 |  |  | BR4-2110-E-00114 | 0 | [8 empty] | F7 | 37 | 38 | 39 | 40
[10 empty] | PNOZs4 | Safety Relay | 2 | BCV130BK01LCS01 | LOS03 | PRIMARY CRUSHING DISCHARGE CONVEYOR DRIVE BRAKE | Emergency Stop Relay |  | K275 | BCV130BK01 |  |  | BR4-2110-E-00114 | 0 | [8 empty] | F7 | 41 | 42 | 43 | 44
[32 empty] | F7 | 45 | 46 | 47 | 48
SUB902DX10 - East Turkey's Nest - Storage & Bulk Raw Water
EIO node #10 | DX10 | DIO1 | 130 | 2 | 10 | 0
SUB902 | DX10 | DIO1 | 130 | 2 | 10 | 0 |  | Chassis |  | BMEXBP0400
SUB902 | DX10 | DIO1 | 130 | 2 | 10 | 0 |  | Power |  | BMXCPS2010 |  | total |  | spare |  | % spare
SUB902 | DX10 | DIO1 | 130 | 2 | 10 | 0 | 0 | Comms |  | BMECRA31210 | I/O1 | 164 |  | 83 |  | 50.61%
SUB902 | DX10 | DIO1 | 130 | 2 | 10 | 0 | 1 | 0 | BMXFCW303 | BMXDDI3202K | DI | 4 | SUB902DX10 | VDC01 |  | DX10 24VDC Control Supply Healthy | Healthy | Q110 | SUB902DX10 |  | 2.10\0.1:0 | BR4-1860-E-00195 | A | INTERNAL WIRING | [7 empty] | F1 | 1 | 2
SUB902 | DX10 | DIO1 | 130 | 2 | 10 | 0 | 1 | 1 |  |  | DI | 4 | SUB902DX10 | VDC02 |  | DX10 24VDC Output Module Control Supply | Healthy | Q144 | SUB902DX10 |  | 2.10\0.1:1 | BR4-1860-E-00195 | A | [8 empty] | F1 | 3 | 4
SUB902 | DX10 | DIO1 | 130 | 2 | 10 | 0 | 1 | 2 |  |  | DI | 4 | SUB902DX10 | VDC03 |  | Instrument 24VDC Control Supply | Healthy | Q160 | SUB902DX10 |  | 2.10\0.1:2 | BR4-1860-E-00195 | A | [8 empty] | F1 | 5 | 6
SUB902 | DX10 | DIO1 | 130 | 2 | 10 | 0 | 1 | 3 |  |  | DI | 4 | SUB902DX10 | VDC04 |  | Transmitter 24VDC Control Supply | Healthy | Q163 | SUB902DX10 |  | 2.10\0.1:3 | BR4-1860-E-00195 | A | [8 empty] | F1 | 7 | 8
SUB902 | DX10 | DIO1 | 130 | 2 | 10 | 0 | 1 | 4 |  |  | DI | 4 | SUB902DX10 | VDC05 |  | BTY1501LS01 24VDC Control Supply | Healthy | Q166 | SUB902DX10 |  | 2.10\0.1:4 | BR4-1860-E-00195 | A | [8 empty] | F1 | 9 | 10
SUB902 | DX10 | DIO1 | 130 | 2 | 10 | 0 | 1 | 5 |  |  | DI | 4 | SUB902DX10 | VDC06 |  | SUB902BC01 24VDC Control Supply | Healthy | Q169 | SUB902DX10 |  | 2.10\0.1:5 | BR4-1860-E-00195 | A | [8 empty] | F1 | 11 | 12
SUB902 | DX10 | DIO1 | 130 | 2 | 10 | 0 | 1 | 6 |  |  | DI | 4 | SUB902DX10 | VDC07 |  | SUB902BC02 24VDC Control Supply | Healthy | Q172 | SUB902DX10 |  | 2.10\0.1:6 | BR4-1860-E-00195 | A | [8 empty] | F1 | 13 | 14
SUB902 | DX10 | DIO1 | 130 | 2 | 10 | 0 | 1 | 7 |  |  | DI | 4 | SUB902DX10 | VDC08 |  | Misc Switchroom Alarms 24VDC Control Supply | Healthy | Q175 | SUB902DX10 |  | 2.10\0.1:7 | BR4-1860-E-00195 | A | [8 empty] | F1 | 15 | 16
SUB902 | DX10 | DIO1 | 130 | 2 | 10 | 0 | 1 | 8 |  |  | DI | 4 | SUB902DX10 | VDC09 |  | BSTD1108 HME Standpipe 24VDC Control Supply | Healthy | Q178 | SUB902DX10 |  | 2.10\0.1:8 | BR4-1860-E-00195 | A | [8 empty] | F1 | 17 | 18
SUB902 | DX10 | DIO1 | 130 | 2 | 10 | 0 | 1 | 9 |  |  | DI | 4 | SUB902DX10 | VDC10 |  | Spare Control Supply | Healthy | Q181 | SUB902DX10 |  | 2.10\0.1:9 | BR4-1860-E-00195 | A | [8 empty] | F1 | 19 | 20
SUB902 | DX10 | DIO1 | 130 | 2 | 10 | 0 | 1 | 10 |  |  | DI | 4 | SUB902DX10 | VDC11 |  | Spare Control Supply | Healthy | Q184 | SUB902DX10 |  | 2.10\0.1:10 | BR4-1860-E-00195 | A | [8 empty] | F1 | 21 | 22
SUB902 | DX10 | DIO1 | 130 | 2 | 10 | 0 | 1 | 11 |  |  | DI | 4 | SUB902DX10 | VDC12 |  | Spare Control Supply | Healthy | Q187 | SUB902DX10 |  | 2.10\0.1:11 | BR4-1860-E-00195 | A | [8 empty] | F1 | 23 | 24
SUB902 | DX10 | DIO1 | 130 | 2 | 10 | 0 | 1 | 12 |  |  | DI | [9 empty] | 2.10\0.1:12 | [10 empty] | F1 | 25 | 26
SUB902 | DX10 | DIO1 | 130 | 2 | 10 | 0 | 1 | 13 |  |  | DI | [9 empty] | 2.10\0.1:13 | [10 empty] | F1 | 27 | 28
SUB902 | DX10 | DIO1 | 130 | 2 | 10 | 0 | 1 | 14 |  |  | DI | [9 empty] | 2.10\0.1:14 | [10 empty] | F1 | 29 | 30
SUB902 | DX10 | DIO1 | 130 | 2 | 10 | 0 | 1 | 15 |  |  | DI | 4 | BTY1501FT02 | FQ02 | EAST TURKEYS NEST RAW WATER | Flow Totaliser Pulse | Active |  | BTY1501 |  | 2.10\0.1:15 | BR4-1860-E-00197 | A | BTY1501AX01-C1 | [7 empty] | F1 | 31 | 32
SUB902 | DX10 | DIO1 | 130 | 2 | 10 | 0 | 1 | 16 |  |  | DI | 4 | BSTD1108FT01 | FQ01 | EAST TURKEYS NEST RAW WATER | HME Standpipe Flow Totaliser Pulse | Active |  | BSTD1108 |  | 2.10\0.1:16 | BR4-1860-E-00197 | A | [8 empty] | F1 | 33 | 34
SUB902 | DX10 | DIO1 | 130 | 2 | 10 | 0 | 1 | 17 |  |  | DI | [9 empty] | 2.10\0.1:17 | [10 empty] | F1 | 35 | 36
SUB902 | DX10 | DIO1 | 130 | 2 | 10 | 0 | 1 | 18 |  |  | DI | [9 empty] | 2.10\0.1:18 | [10 empty] | F1 | 37 | 38
SUB902 | DX10 | DIO1 | 130 | 2 | 10 | 0 | 1 | 19 |  |  | DI | 4 | BTY1501LS01 | LS01 | EAST TURKEYS NEST RAW WATER | Level Switch | High-High |  | BTY1501 |  | 2.10\0.1:19 | BR4-1860-E-00196 | A | BTY1501LS01-C1 1 PAIR | [7 empty] | F1 | 39 | 40
SUB902 | DX10 | DIO1 | 130 | 2 | 10 | 0 | 1 | 20 |  |  | DI | 4 | BPP1108FS01 | FS01 | EAST TURKEYS NEST RAW WATER | HME Standpipe Pump 1 Flow Switch | Active |  | BPP1108 |  | 2.10\0.1:20 | BR4-1860-E-00196 | A | BPP1108FS01-C1 1 PAIR | [7 empty] | F1 | 41 | 42
SUB902 | DX10 | DIO1 | 130 | 2 | 10 | 0 | 1 | 21 |  |  | DI | 4 | BPP1109FS02 | FS02 | EAST TURKEYS NEST RAW WATER | HME Standpipe Pump 2 Flow Switch | Active |  | BPP1109 |  | 2.10\0.1:21 | BR4-1860-E-00196 | A | BPP1109FS02-C1 1 PAIR | [7 empty] | F1 | 43 | 44
SUB902 | DX10 | DIO1 | 130 | 2 | 10 | 0 | 1 | 22 |  |  | DI | [9 empty] | 2.10\0.1:22 | [10 empty] | F1 | 45 | 46
SUB902 | DX10 | DIO1 | 130 | 2 | 10 | 0 | 1 | 23 |  |  | DI | [9 empty] | 2.10\0.1:23 | [10 empty] | F1 | 47 | 48
SUB902 | DX10 | DIO1 | 130 | 2 | 10 | 0 | 1 | 24 |  |  | DI | [9 empty] | 2.10\0.1:24 | [10 empty] | F1 | 49 | 50
SUB902 | DX10 | DIO1 | 130 | 2 | 10 | 0 | 1 | 25 |  |  | DI | 4 | SUB902DX10 | XS01 |  | SUB902DX10 24VDC Power Supply 1 | Healthy | U103A | SUB902DX10 |  | 2.10\0.1:25 | BR4-1860-E-00198 | A | INTERNAL WIRING | [7 empty] | F1 | 51 | 52
SUB902 | DX10 | DIO1 | 130 | 2 | 10 | 0 | 1 | 26 |  |  | DI | 4 | SUB902DX10 | XS02 |  | SUB902DX10 24VDC Power Supply 2 | Healthy | U103B | SUB902DX10 |  | 2.10\0.1:26 | BR4-1860-E-00198 | A | INTERNAL WIRING | [7 empty] | F1 | 53 | 54
SUB902 | DX10 | DIO1 | 130 | 2 | 10 | 0 | 1 | 27 |  |  | DI | 4 | SUB902DX10 | XS03 |  | SUB902DX10 24VDC Power Supply 3 | Healthy | U153A | SUB902DX10 |  | 2.10\0.1:27 | BR4-1860-E-00198 | A | INTERNAL WIRING | [7 empty] | F1 | 55 | 56
SUB902 | DX10 | DIO1 | 130 | 2 | 10 | 0 | 1 | 28 |  |  | DI | 4 | SUB902DX10 | XS04 |  | SUB902DX10 24VDC Power Supply 4 | Healthy | U153B | SUB902DX10 |  | 2.10\0.1:28 | BR4-1860-E-00198 | A | INTERNAL WIRING | [7 empty] | F1 | 57 | 58
SUB902 | DX10 | DIO1 | 130 | 2 | 10 | 0 | 1 | 29 |  |  | DI | 4 | SUB902NEP01 | CB01 |  | SUB902NEP01 Primary PDU Circuit Breaker | Closed | Q108 | SUB902NEP01 |  | 2.10\0.1:29 | BR4-1860-E-00198 | A | [8 empty] | F1 | 59 | 60
SUB902 | DX10 | DIO1 | 130 | 2 | 10 | 0 | 1 | 30 |  |  | DI | 4 | SUB902NEP01 | CB02 |  | NEP Secondary PDU Circuit Breaker | Closed | Q114 | SUB902NEP01 |  | 2.10\0.1:30 | BR4-1860-E-00198 | A | [8 empty] | F1 | 61 | 62
SUB902 | DX10 | DIO1 | 130 | 2 | 10 | 0 | 1 | 31 |  |  | DI | 4 | SUB902DB01 | XS01 |  | SUB902DB01 Surge Protection | Healthy | SD106 | SUB902DB01 |  | 2.10\0.1:31 | BR4-1860-E-00198 | A | SUB902DB01-C2 1 PAIR | [7 empty] | F1 | 63 | 64
SUB902 | DX10 | DIO1 | 130 | 2 | 10 | 0 | 2 | 0 | BMXFCW303 | BMXDDI3202K | DI | 4 | BPP1108LCS01 | STT01 | EAST TURKEYS NEST HME STANDPIPE PUMP 1 | Start Pushbutton | Activated | STT01 | BPP1108 |  | 2.10\0.2:0 | BR4-1860-E-00190 |  | BPP1108LCS01-C1 4 PAIR | [7 empty] | F2 | 1 | 2
SUB902 | DX10 | DIO1 | 130 | 2 | 10 | 0 | 2 | 1 |  |  | DI | 4 | BPP1108LCS01 | STP01 | EAST TURKEYS NEST HME STANDPIPE PUMP 1 | Stop Pushbutton | Activated | STP01 | BPP1108 |  | 2.10\0.2:1 | BR4-1860-E-00190 | [9 empty] | F2 | 3 | 4
SUB902 | DX10 | DIO1 | 130 | 2 | 10 | 0 | 2 | 2 |  |  | DI | 4 | BPP1108 | THR01 | EAST TURKEYS NEST HME STANDPIPE PUMP 1 | PTC Thermistor Relay | Healthy |  | BPP1108 |  | 2.10\0.2:2 | BR4-1860-E-00190 |  | INTERNAL WIRING | [7 empty] | F2 | 5 | 6
SUB902 | DX10 | DIO1 | 130 | 2 | 10 | 0 | 2 | 3 |  |  | DI | 4 | BPP1108 | VDC01 | EAST TURKEYS NEST HME STANDPIPE PUMP 1 | 24VDC Control Supply | Healthy | Q155 | BPP1108 |  | 2.10\0.2:3 | BR4-1860-E-00190 |  | BPP1108-C1 | [7 empty] | F2 | 7 | 8
SUB902 | DX10 | DIO1 | 130 | 2 | 10 | 0 | 2 | 4 |  |  | DI | [9 empty] | 2.10\0.2:4 | [10 empty] | F2 | 9 | 10
SUB902 | DX10 | DIO1 | 130 | 2 | 10 | 0 | 2 | 5 |  |  | DI | [9 empty] | 2.10\0.2:5 | [10 empty] | F2 | 11 | 12
SUB902 | DX10 | DIO1 | 130 | 2 | 10 | 0 | 2 | 6 |  |  | DI | [9 empty] | 2.10\0.2:6 | [10 empty] | F2 | 13 | 14
SUB902 | DX10 | DIO1 | 130 | 2 | 10 | 0 | 2 | 7 |  |  | DI | 4 | BPP1109LCS01 | STT01 | EAST TURKEYS NEST HME STANDPIPE PUMP 2 | Start Pushbutton | Activated | STT01 | BPP1109 |  | 2.10\0.2:7 | BR4-1860-E-00191 |  | BPP1109LCS01-C1 4 PAIR | [7 empty] | F2 | 15 | 16
SUB902 | DX10 | DIO1 | 130 | 2 | 10 | 0 | 2 | 8 |  |  | DI | 4 | BPP1109LCS01 | STP01 | EAST TURKEYS NEST HME STANDPIPE PUMP 2 | Stop Pushbutton | Activated | STP01 | BPP1109 |  | 2.10\0.2:8 | BR4-1860-E-00191 | [9 empty] | F2 | 17 | 18
SUB902 | DX10 | DIO1 | 130 | 2 | 10 | 0 | 2 | 9 |  |  | DI | 4 | BPP1109 | THR01 | EAST TURKEYS NEST HME STANDPIPE PUMP 2 | PTC Thermistor Relay | Healthy |  | BPP1109 |  | 2.10\0.2:9 | BR4-1860-E-00191 |  | INTERNAL WIRING | [7 empty] | F2 | 19 | 20
SUB902 | DX10 | DIO1 | 130 | 2 | 10 | 0 | 2 | 10 |  |  | DI | 4 | BPP1109 | VDC01 | EAST TURKEYS NEST HME STANDPIPE PUMP 2 | 24VDC Control Supply | Healthy | Q155 | BPP1109 |  | 2.10\0.2:10 | BR4-1860-E-00191 |  | BPP1109-C1 | [7 empty] | F2 | 21 | 22
SUB902 | DX10 | DIO1 | 130 | 2 | 10 | 0 | 2 | 11 |  |  | DI | [9 empty] | 2.10\0.2:11 | [10 empty] | F2 | 23 | 24
SUB902 | DX10 | DIO1 | 130 | 2 | 10 | 0 | 2 | 12 |  |  | DI | [9 empty] | 2.10\0.2:12 | [10 empty] | F2 | 25 | 26
SUB902 | DX10 | DIO1 | 130 | 2 | 10 | 0 | 2 | 13 |  |  | DI | [9 empty] | 2.10\0.2:13 | [10 empty] | F2 | 27 | 28
SUB902 | DX10 | DIO1 | 130 | 2 | 10 | 0 | 2 | 14 |  |  | DI | [9 empty] | 2.10\0.2:14 | [10 empty] | F2 | 29 | 30
SUB902 | DX10 | DIO1 | 130 | 2 | 10 | 0 | 2 | 15 |  |  | DI | 4 | BSTD1108LCS01 | STT01 | EAST TURKEYS NEST HME STANDPIPE | Start Pushbutton | Activated | STT01 | BSTD1108 |  | 2.10\0.2:15 | BR4-1860-E-00196 | A | BSTD1108LCS01-C1 12 pair | [7 empty] | F2 | 31 | 32
SUB902 | DX10 | DIO1 | 130 | 2 | 10 | 0 | 2 | 16 |  |  | DI |  | BSTD1108LCS01 | STP01 | EAST TURKEYS NEST HME STANDPIPE | Stop Pushbutton | Activated | STP01 | BSTD1108 |  | 2.10\0.2:16 | BR4-1860-E-00196 | A | [8 empty] | F2 | 33 | 34
SUB902 | DX10 | DIO1 | 130 | 2 | 10 | 0 | 2 | 17 |  |  | DI | 4 | BSTD1108LCS01 | STT02 | EAST TURKEYS NEST HME STANDPIPE | Elsema Run Interlock | Activated | STT02 | BSTD1108 |  | 2.10\0.2:17 | BR4-1860-E-00196 | A | [8 empty] | F2 | 35 | 36
SUB902 | DX10 | DIO1 | 130 | 2 | 10 | 0 | 2 | 18 |  |  | DI | [9 empty] | 2.10\0.2:18 | [10 empty] | F2 | 37 | 38
SUB902 | DX10 | DIO1 | 130 | 2 | 10 | 0 | 2 | 19 |  |  | DI | [9 empty] | 2.10\0.2:19 | [10 empty] | F2 | 39 | 40
SUB902 | DX10 | DIO1 | 130 | 2 | 10 | 0 | 2 | 20 |  |  | DI | [9 empty] | 2.10\0.2:20 | [10 empty] | F2 | 41 | 42
SUB902 | DX10 | DIO1 | 130 | 2 | 10 | 0 | 2 | 21 |  |  | DI | 4 | BTY1501FV01 | SW01 | EAST TURKEYS NEST RAW WATER | Remote Mode | Selected |  | BTY1501FV01 |  | 2.10\0.2:21 | BR4-1860-E-00197 | A | BTY1501AX01-C1 | [7 empty] | F2 | 43 | 44
SUB902 | DX10 | DIO1 | 130 | 2 | 10 | 0 | 2 | 22 |  |  | DI | 4 | BTY1501FV01 | ZS01 | EAST TURKEYS NEST RAW WATER | Valve Open | Open |  | BTY1501FV01 |  | 2.10\0.2:22 | BR4-1860-E-00197 | A | [8 empty] | F2 | 45 | 46
SUB902 | DX10 | DIO1 | 130 | 2 | 10 | 0 | 2 | 23 |  |  | DI | 4 | BTY1501FV01 | ZS02 | EAST TURKEYS NEST RAW WATER | Valve Closed | Closed |  | BTY1501FV01 |  | 2.10\0.2:23 | BR4-1860-E-00197 | A | [8 empty] | F2 | 47 | 48
SUB902 | DX10 | DIO1 | 130 | 2 | 10 | 0 | 2 | 24 |  |  | DI | 4 | BTY1501FV01 | XS01 | EAST TURKEYS NEST RAW WATER | Valve Fault | Fault |  | BTY1501FV01 |  | 2.10\0.2:24 | BR4-1860-E-00197 | A | [8 empty] | F2 | 49 | 50
SUB902 | DX10 | DIO1 | 130 | 2 | 10 | 0 | 2 | 25 |  |  | DI | 4 | BTY1501FV01 | CB01 | EAST TURKEYS NEST RAW WATER | 240VAC Circuit Breaker | Closed |  | BTY1501FV01 |  | 2.10\0.2:25 | BR4-1860-E-00197 | A | [8 empty] | F2 | 51 | 52
SUB902 | DX10 | DIO1 | 130 | 2 | 10 | 0 | 2 | 26 |  |  | DI | [9 empty] | 2.10\0.2:26 | [10 empty] | F2 | 53 | 54
SUB902 | DX10 | DIO1 | 130 | 2 | 10 | 0 | 2 | 27 |  |  | DI | 4 | BSTD1108FV01 | SW01 | EAST TURKEYS NEST RAW WATER | Remote Mode | Selected |  | BSTD1108FV01 |  | 2.10\0.2:27 | BR4-1860-E-00197 | A | BTY1501AX01-C1 | [7 empty] | F2 | 55 | 56
SUB902 | DX10 | DIO1 | 130 | 2 | 10 | 0 | 2 | 28 |  |  | DI | 4 | BSTD1108FV01 | ZS01 | EAST TURKEYS NEST RAW WATER | Valve Open | Open |  | BSTD1108FV01 |  | 2.10\0.2:28 | BR4-1860-E-00197 | A | [8 empty] | F2 | 57 | 58
SUB902 | DX10 | DIO1 | 130 | 2 | 10 | 0 | 2 | 29 |  |  | DI | 4 | BSTD1108FV01 | ZS02 | EAST TURKEYS NEST RAW WATER | Valve Closed | Closed |  | BSTD1108FV01 |  | 2.10\0.2:29 | BR4-1860-E-00197 | A | [8 empty] | F2 | 59 | 60
SUB902 | DX10 | DIO1 | 130 | 2 | 10 | 0 | 2 | 30 |  |  | DI | 4 | BSTD1108FV01 | XS01 | EAST TURKEYS NEST RAW WATER | Valve Fault | Fault |  | BSTD1108FV01 |  | 2.10\0.2:30 | BR4-1860-E-00197 | A | [8 empty] | F2 | 61 | 62
SUB902 | DX10 | DIO1 | 130 | 2 | 10 | 0 | 2 | 31 |  |  | DI | 4 | BSTD1108FV01 | CB01 | EAST TURKEYS NEST RAW WATER | 240VAC Circuit Breaker | Closed |  | BSTD1108FV01 |  | 2.10\0.2:31 | BR4-1860-E-00197 | A | [8 empty] | F2 | 63 | 64
SUB902 | DX10 | DIO1 | 130 | 2 | 10 | 0 | 3 | 0 | BMXFCW303 | BMXDDI3202K | DI | 5 | SUB902BC01 | VDC01 | UTILITIES TRIPPING AND CLOSING SUPPLY BATTERY CHARGER | 24VDC Control Supply | Healthy | Q155 | SUB902BC01 |  | 2.10\0.3:0 | BR4-1860-E-00188 | A | SUB902BC01-C1 | [7 empty] | F3 | 1 | 2
SUB902 | DX10 | DIO1 | 130 | 2 | 10 | 0 | 3 | 1 |  |  | DI | 5 | SUB902BC01 | CB01 | UTILITIES TRIPPING AND CLOSING SUPPLY BATTERY CHARGER | Main Circuit Breaker | Closed | Q103 | SUB902BC01 |  | 2.10\0.3:1 | BR4-1860-E-00188 | A | [8 empty] | F3 | 3 | 4
SUB902 | DX10 | DIO1 | 130 | 2 | 10 | 0 | 3 | 2 |  |  | DI | 5 | SUB902BC01 | TRP01 | UTILITIES TRIPPING AND CLOSING SUPPLY BATTERY CHARGER | Main Circuit Breaker | Tripped | Q103 | SUB902BC01 |  | 2.10\0.3:2 | BR4-1860-E-00188 | A | [8 empty] | F3 | 5 | 6
SUB902 | DX10 | DIO1 | 130 | 2 | 10 | 0 | 3 | 3 |  |  | DI | 5 | SUB902BC02 | VDC01 | FIXED PLANT TRIPPING AND CLOSING SUPPLY BATTERY CHARGER | 24VDC Control Supply | Healthy | Q155 | SUB902BC02 |  | 2.10\0.3:3 | BR4-1860-E-00192 | A | SUB902BC02-C1 | [7 empty] | F3 | 7 | 8
SUB902 | DX10 | DIO1 | 130 | 2 | 10 | 0 | 3 | 4 |  |  | DI | 5 | SUB902BC02 | CB01 | FIXED PLANT TRIPPING AND CLOSING SUPPLY BATTERY CHARGER | Main Circuit Breaker | Closed | Q103 | SUB902BC02 |  | 2.10\0.3:4 | BR4-1860-E-00192 | A | [8 empty] | F3 | 9 | 10
SUB902 | DX10 | DIO1 | 130 | 2 | 10 | 0 | 3 | 5 |  |  | DI | 5 | SUB902BC02 | TRP01 | FIXED PLANT TRIPPING AND CLOSING SUPPLY BATTERY CHARGER | Main Circuit Breaker | Tripped | Q103 | SUB902BC02 |  | 2.10\0.3:5 | BR4-1860-E-00192 | A | [8 empty] | F3 | 11 | 12
SUB902 | DX10 | DIO1 | 130 | 2 | 10 | 0 | 3 | 6 |  |  | DI | 5 | SUB902DB01 | VDC01 | KIOSK 415V LIGHTING AND SMALL POWER | 24VDC Control Supply | Healthy | Q155 | SUB902DB01 |  | 2.10\0.3:6 | BR4-1860-E-00189 | A | SUB902DB01-C1 | [7 empty] | F3 | 13 | 14
SUB902 | DX10 | DIO1 | 130 | 2 | 10 | 0 | 3 | 7 |  |  | DI | 5 | SUB902DB01 | CB01 | KIOSK 415V LIGHTING AND SMALL POWER | Main Circuit Breaker | Closed | Q103 | SUB902DB01 |  | 2.10\0.3:7 | BR4-1860-E-00189 | A | [8 empty] | F3 | 15 | 16
SUB902 | DX10 | DIO1 | 130 | 2 | 10 | 0 | 3 | 8 |  |  | DI | 5 | SUB902DB01 | TRP01 | KIOSK 415V LIGHTING AND SMALL POWER | Main Circuit Breaker | Tripped | Q103 | SUB902DB01 |  | 2.10\0.3:8 | BR4-1860-E-00189 | A | [8 empty] | F3 | 17 | 18
SUB902 | DX10 | DIO1 | 130 | 2 | 10 | 0 | 3 | 9 |  |  | DI | [9 empty] | 2.10\0.3:9 | [10 empty] | F3 | 19 | 20
SUB902 | DX10 | DIO1 | 130 | 2 | 10 | 0 | 3 | 10 |  |  | DI | [9 empty] | 2.10\0.3:10 | [10 empty] | F3 | 21 | 22
SUB902 | DX10 | DIO1 | 130 | 2 | 10 | 0 | 3 | 11 |  |  | DI | 4 | BMC802INC01 | VDC01 | INCOMER BMC802INC01 | 24VDC Control Supply | Healthy | Q267 | BMC802INC01 |  | 2.10\0.3:11 | BR4-1860-E-00184 | A | BMC802INC01-C1 12 pair | [7 empty] | F3 | 23 | 24
SUB902 | DX10 | DIO1 | 130 | 2 | 10 | 0 | 3 | 12 |  |  | DI | 4 | BMC802INC01 | CB02 | INCOMER BMC802INC01 | 110VDC Vamp Arc Flash Supply CB | Closed | Q204 | BMC802INC01 |  | 2.10\0.3:12 | BR4-1860-E-00184 | A | [8 empty] | F3 | 25 | 26
SUB902 | DX10 | DIO1 | 130 | 2 | 10 | 0 | 3 | 13 |  |  | DI | 4 | BMC802INC01 | TRP02 | INCOMER BMC802INC01 | Vamp Arc Flash Trip Alarm | Healthy | F113-A1 | BMC802INC01 |  | 2.10\0.3:13 | BR4-1860-E-00184 | A | [8 empty] | F3 | 27 | 28
SUB902 | DX10 | DIO1 | 130 | 2 | 10 | 0 | 3 | 14 |  |  | DI | 4 | BMC802INC01 | XS02 | INCOMER BMC802INC01 | Vamp Self Supervision System | Healthy | F113-SF | BMC802INC01 |  | 2.10\0.3:14 | BR4-1860-E-00184 | A | [8 empty] | F3 | 29 | 30
SUB902 | DX10 | DIO1 | 130 | 2 | 10 | 0 | 3 | 15 |  |  | DI | 4 | BMC802INC01 | CB03 | INCOMER BMC802INC01 | Incomer CB Comms Unit Circuit Breaker | Closed | Q258 | BMC802INC01 |  | 2.10\0.3:15 | BR4-1860-E-00184 | A | [8 empty] | F3 | 31 | 32
SUB902 | DX10 | DIO1 | 130 | 2 | 10 | 0 | 3 | 16 |  |  | DI | 4 | BMC802INC01 | CB04 | INCOMER BMC802INC01 | Circuit Breaker Trip Supply CB | Closed | Q220 | BMC802INC01 |  | 2.10\0.3:16 | BR4-1860-E-00184 | A | [8 empty] | F3 | 33 | 34
SUB902 | DX10 | DIO1 | 130 | 2 | 10 | 0 | 3 | 17 |  |  | DI | 4 | BMC802INC01 | CB05 | INCOMER BMC802INC01 | 24VDC Trip Unit Circuit Breaker | Closed | Q256 | BMC802INC01 |  | 2.10\0.3:17 | BR4-1860-E-00184 | A | [8 empty] | F3 | 35 | 36
SUB902 | DX10 | DIO1 | 130 | 2 | 10 | 0 | 3 | 18 |  |  | DI | 4 | BMC802INC01 | XS01 | INCOMER BMC802INC01 | Upstream Circuit Breaker Trip | Healthy | F153 | BMC802INC01 |  | 2.10\0.3:18 | BR4-1860-E-00184 | A | [8 empty] | F3 | 37 | 38
SUB902 | DX10 | DIO1 | 130 | 2 | 10 | 0 | 3 | 19 |  |  | DI | 4 | BMC802INC01 | XS03 | INCOMER BMC802INC01 | Surge Protection | Healthy | SD144-146 | BMC802INC01 |  | 2.10\0.3:19 | BR4-1860-E-00184 | A | [8 empty] | F3 | 39 | 40
SUB902 | DX10 | DIO1 | 130 | 2 | 10 | 0 | 3 | 20 |  |  | DI | 4 | BMC802INC01 | CB06 | INCOMER BMC802INC01 | 110VDC/24VDC Power Supply CB | Closed | Q215 | BMC802INC01 |  | 2.10\0.3:20 | BR4-1860-E-00184 | A | [8 empty] | F3 | 41 | 42
SUB902 | DX10 | DIO1 | 130 | 2 | 10 | 0 | 3 | 21 |  |  | DI | [9 empty] | 2.10\0.3:21 | [10 empty] | F3 | 43 | 44
SUB902 | DX10 | DIO1 | 130 | 2 | 10 | 0 | 3 | 22 |  |  | DI | [9 empty] | 2.10\0.3:22 | [10 empty] | F3 | 45 | 46
SUB902 | DX10 | DIO1 | 130 | 2 | 10 | 0 | 3 | 23 |  |  | DI | [9 empty] | 2.10\0.3:23 | [10 empty] | F3 | 47 | 48
SUB902 | DX10 | DIO1 | 130 | 2 | 10 | 0 | 3 | 24 |  |  | DI | 4 | BMC802INC02 | VDC01 | GENERATOR INCOMER | 24VDC Control Supply | Healthy | Q267 | BMC802INC02 |  | 2.10\0.3:24 | BR4-1860-E-00187 | A | BMC802INC02-C1 12 pair | [7 empty] | F3 | 49 | 50
SUB902 | DX10 | DIO1 | 130 | 2 | 10 | 0 | 3 | 25 |  |  | DI | 4 | BMC802INC02 | TRP02 | GENERATOR INCOMER | Arc Flash Trip Alarm | Healthy | F110 | BMC802INC02 |  | 2.10\0.3:25 | BR4-1860-E-00187 | A | [8 empty] | F3 | 51 | 52
SUB902 | DX10 | DIO1 | 130 | 2 | 10 | 0 | 3 | 26 |  |  | DI | 4 | BMC802INC02 | CB03 | GENERATOR INCOMER | Incomer CB Comms Unit Circuit Breaker | Closed | Q260 | BMC802INC02 |  | 2.10\0.3:26 | BR4-1860-E-00187 | A | [8 empty] | F3 | 53 | 54
SUB902 | DX10 | DIO1 | 130 | 2 | 10 | 0 | 3 | 27 |  |  | DI | 4 | BMC802INC02 | CB04 | GENERATOR INCOMER | Incomer Circuit Breaker Trip Supply | Ok | Q220 | BMC802INC02 |  | 2.10\0.3:27 | BR4-1860-E-00187 | A | [8 empty] | F3 | 55 | 56
SUB902 | DX10 | DIO1 | 130 | 2 | 10 | 0 | 3 | 28 |  |  | DI | 4 | BMC802INC02 | CB05 | GENERATOR INCOMER | 24VDC Trip Unit Circuit Breaker | Closed | Q256 | BMC802INC02 |  | 2.10\0.3:28 | BR4-1860-E-00187 | A | [8 empty] | F3 | 57 | 58
SUB902 | DX10 | DIO1 | 130 | 2 | 10 | 0 | 3 | 29 |  |  | DI | 4 | BMC802INC02 | CB06 | GENERATOR INCOMER | Arc Flash Expansion Module 24VDC Supply | Healthy | Q258 | BMC802INC02 |  | 2.10\0.3:29 | BR4-1860-E-00187 | A | [8 empty] | F3 | 59 | 60
SUB902 | DX10 | DIO1 | 130 | 2 | 10 | 0 | 3 | 30 |  |  | DI | 4 | BMC802INC02 | CB07 | GENERATOR INCOMER | 110VDC/24VDC Power Supply | Healthy | Q215 | BMC802INC02 |  | 2.10\0.3:30 | BR4-1860-E-00187 | A | [8 empty] | F3 | 61 | 62
SUB902 | DX10 | DIO1 | 130 | 2 | 10 | 0 | 3 | 31 |  |  | DI | [9 empty] | 2.10\0.3:31 | [10 empty] | F3 | 63 | 64
SUB902 | DX10 | DIO1 | 130 | 2 | 10 | 0 | 4 | 0 | BMXFCW303 | BMXDDI3202K | DI | 4 | SUB902BC02 | VDC02 |  | Battery Charger 110VDC Tripping Supply | Healthy | K112 | SUB902BC02 |  | 2.10\0.4:0 | BR4-1860-E-00199 |  | SUB902BC02-C2 8 Pair | [7 empty] | F4 | 1 | 2
SUB902 | DX10 | DIO1 | 130 | 2 | 10 | 0 | 4 | 1 |  |  | DI | 4 | SUB902BC02 | CB02 |  | BMC802 110VDC IC1 Tripping Supply Circuit Breaker | Closed | Q114 | SUB902BC02 |  | 2.10\0.4:1 | BR4-1860-E-00199 | [9 empty] | F4 | 3 | 4
SUB902 | DX10 | DIO1 | 130 | 2 | 10 | 0 | 4 | 2 |  |  | DI | 4 | SUB902BC02 | CB03 |  | BMC802 110VDC IC2 Tripping Supply Circuit Breaker | Closed | Q117 | SUB902BC02 |  | 2.10\0.4:2 | BR4-1860-E-00199 | [9 empty] | F4 | 5 | 6
SUB902 | DX10 | DIO1 | 130 | 2 | 10 | 0 | 4 | 3 |  |  | DI | 5 | SUB902BC02 | CB04 |  | SUB902NEP01 110VDC Tripping Supply Circuit Breaker | Closed |  | SUB902BC02 |  | 2.10\0.4:3 | BR4-1860-E-00199 | [9 empty] | F4 | 7 | 8
SUB902 | DX10 | DIO1 | 130 | 2 | 10 | 0 | 4 | 4 |  |  | DI | 5 | SUB902BC02 | CB05 |  | SUB902DX10 110VDC Tripping Supply Circuit Breaker | Closed |  | SUB902BC02 |  | 2.10\0.4:4 | BR4-1860-E-00199 | [9 empty] | F4 | 9 | 10
SUB902 | DX10 | DIO1 | 130 | 2 | 10 | 0 | 4 | 5 |  |  | DI | 4 | SUB902BC02 | CB06 |  | Spare 110VDC Tripping Supply Circuit Breaker | Closed |  | SUB902BC02 |  | 2.10\0.4:5 | BR4-1860-E-00199 | [9 empty] | F4 | 11 | 12
SUB902 | DX10 | DIO1 | 130 | 2 | 10 | 0 | 4 | 6 |  |  | DI | 4 | SUB902BC02 | CB07 |  | Spare 110VDC Tripping Supply Circuit Breaker | Closed |  | SUB902BC02 |  | 2.10\0.4:6 | BR4-1860-E-00199 | [9 empty] | F4 | 13 | 14
SUB902 | DX10 | DIO1 | 130 | 2 | 10 | 0 | 4 | 7 |  |  | DI | 4 | SUB902BC02 | CB08 |  | Spare 110VDC Tripping Supply Circuit Breaker | Closed |  | SUB902BC02 |  | 2.10\0.4:7 | BR4-1860-E-00199 | [9 empty] | F4 | 15 | 16
SUB902 | DX10 | DIO1 | 130 | 2 | 10 | 0 | 4 | 8 |  |  | DI | [9 empty] | 2.10\0.4:8 | [10 empty] | F4 | 17 | 18
SUB902 | DX10 | DIO1 | 130 | 2 | 10 | 0 | 4 | 9 |  |  | DI | [9 empty] | 2.10\0.4:9 | [10 empty] | F4 | 19 | 20
SUB902 | DX10 | DIO1 | 130 | 2 | 10 | 0 | 4 | 10 |  |  | DI | [9 empty] | 2.10\0.4:10 | [10 empty] | F4 | 21 | 22
SUB902 | DX10 | DIO1 | 130 | 2 | 10 | 0 | 4 | 11 |  |  | DI | [9 empty] | 2.10\0.4:11 | [10 empty] | F4 | 23 | 24
SUB902 | DX10 | DIO1 | 130 | 2 | 10 | 0 | 4 | 12 |  |  | DI | [9 empty] | 2.10\0.4:12 | [10 empty] | F4 | 25 | 26
SUB902 | DX10 | DIO1 | 130 | 2 | 10 | 0 | 4 | 13 |  |  | DI | [9 empty] | 2.10\0.4:13 | [10 empty] | F4 | 27 | 28
SUB902 | DX10 | DIO1 | 130 | 2 | 10 | 0 | 4 | 14 |  |  | DI | [9 empty] | 2.10\0.4:14 | [10 empty] | F4 | 29 | 30
SUB902 | DX10 | DIO1 | 130 | 2 | 10 | 0 | 4 | 15 |  |  | DI | [9 empty] | 2.10\0.4:15 | [10 empty] | F4 | 31 | 32
SUB902 | DX10 | DIO1 | 130 | 2 | 10 | 0 | 4 | 16 |  |  | DI | [9 empty] | 2.10\0.4:16 | [10 empty] | F4 | 33 | 34
SUB902 | DX10 | DIO1 | 130 | 2 | 10 | 0 | 4 | 17 |  |  | DI | [9 empty] | 2.10\0.4:17 | [10 empty] | F4 | 35 | 36
SUB902 | DX10 | DIO1 | 130 | 2 | 10 | 0 | 4 | 18 |  |  | DI | [9 empty] | 2.10\0.4:18 | [10 empty] | F4 | 37 | 38
SUB902 | DX10 | DIO1 | 130 | 2 | 10 | 0 | 4 | 19 |  |  | DI | [9 empty] | 2.10\0.4:19 | [10 empty] | F4 | 39 | 40
SUB902 | DX10 | DIO1 | 130 | 2 | 10 | 0 | 4 | 20 |  |  | DI | [9 empty] | 2.10\0.4:20 | [10 empty] | F4 | 41 | 42
SUB902 | DX10 | DIO1 | 130 | 2 | 10 | 0 | 4 | 21 |  |  | DI | [9 empty] | 2.10\0.4:21 | [10 empty] | F4 | 43 | 44
SUB902 | DX10 | DIO1 | 130 | 2 | 10 | 0 | 4 | 22 |  |  | DI | [9 empty] | 2.10\0.4:22 | [10 empty] | F4 | 45 | 46
SUB902 | DX10 | DIO1 | 130 | 2 | 10 | 0 | 4 | 23 |  |  | DI | [9 empty] | 2.10\0.4:23 | [10 empty] | F4 | 47 | 48
SUB902 | DX10 | DIO1 | 130 | 2 | 10 | 0 | 4 | 24 |  |  | DI | [9 empty] | 2.10\0.4:24 | [10 empty] | F4 | 49 | 50
SUB902 | DX10 | DIO1 | 130 | 2 | 10 | 0 | 4 | 25 |  |  | DI | [9 empty] | 2.10\0.4:25 | [10 empty] | F4 | 51 | 52
SUB902 | DX10 | DIO1 | 130 | 2 | 10 | 0 | 4 | 26 |  |  | DI | [9 empty] | 2.10\0.4:26 | [10 empty] | F4 | 53 | 54
SUB902 | DX10 | DIO1 | 130 | 2 | 10 | 0 | 4 | 27 |  |  | DI | [9 empty] | 2.10\0.4:27 | [10 empty] | F4 | 55 | 56
SUB902 | DX10 | DIO1 | 130 | 2 | 10 | 0 | 4 | 28 |  |  | DI | [9 empty] | 2.10\0.4:28 | [10 empty] | F4 | 57 | 58
SUB902 | DX10 | DIO1 | 130 | 2 | 10 | 0 | 4 | 29 |  |  | DI | [9 empty] | 2.10\0.4:29 | [10 empty] | F4 | 59 | 60
SUB902 | DX10 | DIO1 | 130 | 2 | 10 | 0 | 4 | 30 |  |  | DI | [9 empty] | 2.10\0.4:30 | [10 empty] | F4 | 61 | 62
SUB902 | DX10 | DIO1 | 130 | 2 | 10 | 0 | 4 | 31 |  |  | DI | [9 empty] | 2.10\0.4:31 | [10 empty] | F4 | 63 | 64
SUB902 | DX10 | DIO1 | 130 | 2 | 10 | 0 | 5 | 0 | BMXFTW301S | BMEAHI0812 | AI | 4 | BTY1501FT02 | FT02 | EAST TURKEYS NEST RAW WATER | Raw Water From East Pit Flow Rate |  | m3/h | BTY1501 | REAL | 2.10\0.5:0 | BR4-1860-E-00197 | A | BTY1501AX01-C2 |  |  | 0 | 500 | 0 | 500 | #.# EU | F5 | 1 | 2
SUB902 | DX10 | DIO1 | 130 | 2 | 10 | 0 | 5 | 1 |  |  | AI | 4 | BTY1501PT02 | PT02 | EAST TURKEYS NEST RAW WATER | Raw Water From East Pit Pressure |  | kPa | BTY1501 | REAL | 2.10\0.5:1 | BR4-1860-E-00196 | A | BTY1501PIT02-C1 |  |  | 0 | 1000 | 0 | 1000 | #.# EU | F5 | 3 | 4
SUB902 | DX10 | DIO1 | 130 | 2 | 10 | 0 | 5 | 2 |  |  | AI | 4 | BTY1501FV01 | ZT01 | EAST TURKEYS NEST RAW WATER | East Pit Flow Valve Position Feedback |  | % | BTY1501 | REAL | 2.10\0.5:2 | BR4-1860-E-00197 | A | BTY1501AX01-C2 |  |  | 0 | 100 | 0 | 100 | #.# EU | F5 | 5 | 6
SUB902 | DX10 | DIO1 | 130 | 2 | 10 | 0 | 5 | 3 |  |  | AI | 4 | BTY1501LT02 | LT02 | EAST TURKEYS NEST RAW WATER | Level Transmitter |  | % | BTY1501 | REAL | 2.10\0.5:3 | BR4-1860-E-00196 | A | BTY1501LIT02-C1 |  |  | 0 | 100 | 0 | 100 | #.# EU | F5 | 7 | 8
SUB902 | DX10 | DIO1 | 130 | 2 | 10 | 0 | 5 | 4 |  |  | AI | [9 empty] | 2.10\0.5:4 | [5 empty] | 0 | 100 | 0 | 100 | #.# EU | F5 | 9 | 10
SUB902 | DX10 | DIO1 | 130 | 2 | 10 | 0 | 5 | 5 |  |  | AI | [9 empty] | 2.10\0.5:5 | [10 empty] | F5 | 11 | 12
SUB902 | DX10 | DIO1 | 130 | 2 | 10 | 0 | 5 | 6 |  |  | AI | [9 empty] | 2.10\0.5:6 | [10 empty] | F5 | 13 | 14
SUB902 | DX10 | DIO1 | 130 | 2 | 10 | 0 | 5 | 7 |  |  | AI | [9 empty] | 2.10\0.5:7 | [10 empty] | F5 | 15 | 16
SUB902 | DX10 | DIO1 | 130 | 2 | 10 | 0 | 6 | 0 | BMXFTW301S | BMEAHI0812 | AI | 4 | BPP1108PT01 | PT01 | EAST TURKEYS NEST RAW WATER | HME Standpipe Pump 1 Pressure |  | kPa | BPP1108 | REAL | 2.10\0.6:0 | BR4-1860-E-00196 | A | BPP1108PIT01-C1 |  |  | 0 | 500 | 0 | 500 | #.# EU | F5 | 17 | 18
SUB902 | DX10 | DIO1 | 130 | 2 | 10 | 0 | 6 | 1 |  |  | AI | 4 | BPP1109PT02 | PT02 | EAST TURKEYS NEST RAW WATER | HME Standpipe Pump 2 Pressure |  | kPa | BPP1109 | REAL | 2.10\0.6:1 | BR4-1860-E-00196 | A | BPP1109PIT02-C1 |  |  | 0 | 500 | 0 | 500 | #.# EU | F5 | 19 | 20
SUB902 | DX10 | DIO1 | 130 | 2 | 10 | 0 | 6 | 2 |  |  | AI | 4 | BSTD1108FT01 | FT01 | EAST TURKEYS NEST RAW WATER | HME Standpipe Flow Rate |  | m3/h | BSTD1108 | REAL | 2.10\0.6:2 | BR4-1860-E-00197 | A | BTY1501AX01-C2 |  |  | 0 | 1000 | 0 | 1000 | #.# EU | F5 | 21 | 22
SUB902 | DX10 | DIO1 | 130 | 2 | 10 | 0 | 6 | 3 |  |  | AI | 4 | BSTD1108FV01 | ZT01 | EAST TURKEYS NEST RAW WATER | HME Standpipe Flow Valve Position |  | % | BSTD1108 | REAL | 2.10\0.6:3 | BR4-1860-E-00197 | A | BTY1501AX01-C2 |  |  | 0 | 100 | 0 | 100 | #.# EU | F5 | 23 | 24
SUB902 | DX10 | DIO1 | 130 | 2 | 10 | 0 | 6 | 4 |  |  | AI | [9 empty] | 2.10\0.6:4 | [10 empty] | F5 | 25 | 26
SUB902 | DX10 | DIO1 | 130 | 2 | 10 | 0 | 6 | 5 |  |  | AI | [9 empty] | 2.10\0.6:5 | [10 empty] | F5 | 27 | 28
SUB902 | DX10 | DIO1 | 130 | 2 | 10 | 0 | 6 | 6 |  |  | AI | [9 empty] | 2.10\0.6:6 | [10 empty] | F5 | 29 | 30
SUB902 | DX10 | DIO1 | 130 | 2 | 10 | 0 | 6 | 7 |  |  | AI | [9 empty] | 2.10\0.6:7 | [10 empty] | F5 | 31 | 32
SUB902 | DX10 | DIO1 | 130 | 2 | 10 | 0 | 7 | 0 | BMXFTW301S | BMEAHO0412 | AO | 4 | BTY1501FV01 | ZC01 | EAST TURKEYS NEST RAW WATER | East Pit Flow Valve Position Setpoint |  | % | BTY1501 | REAL | 2.10\0.7:0 | BR4-1860-E-00197 | A | BTY1501AX01-C2 |  |  | 0 | 110 | 0 | 110 | # EU | F5 | 33 | 34
SUB902 | DX10 | DIO1 | 130 | 2 | 10 | 0 | 7 | 1 |  |  | AO | 4 | BSTD1108FV01 | ZC01 | EAST TURKEYS NEST RAW WATER | HME Standpipe Flow Valve Position Reference |  | % | BSTD1108 | REAL | 2.10\0.7:1 | BR4-1860-E-00197 | A | BTY1501AX01-C2 |  |  | 0 | 100 | 0 | 100 | #.# EU | F5 | 35 | 36
SUB902 | DX10 | DIO1 | 130 | 2 | 10 | 0 | 7 | 2 |  |  | AO | [9 empty] | 2.10\0.7:2 | [10 empty] | F5 | 37 | 38
SUB902 | DX10 | DIO1 | 130 | 2 | 10 | 0 | 7 | 3 |  |  | AO | [9 empty] | 2.10\0.7:3 | [10 empty] | F5 | 39 | 40
SUB902 | DX10 | DIO1 | 130 | 2 | 10 | 0 | 8 | 0 | BMXFTB2010 | BMXDDO1602 | DO | 4 | BSTD1108LCS01 | IL01 | EAST TURKEYS NEST HME STANDPIPE | Standpipe | Running |  | BSTD1108 |  | 2.10\0.8:0 | BR4-1860-E-00196 | A | BSTD1108LCS01-C1 12 pair NEED TO CREATE "LCS" SCHEMATIC | [7 empty] | F6 | 1 | 2
SUB902 | DX10 | DIO1 | 130 | 2 | 10 | 0 | 8 | 1 |  |  | DO | 4 | BSTD1108LCS01 | IL02 | EAST TURKEYS NEST HME STANDPIPE | Standpipe | Fault |  | BSTD1108 |  | 2.10\0.8:1 | BR4-1860-E-00196 | A | [8 empty] | F6 | 3 | 4
SUB902 | DX10 | DIO1 | 130 | 2 | 10 | 0 | 8 | 2 |  |  | DO | 4 | BSTD1108LCS01 | IL03 | EAST TURKEYS NEST HME STANDPIPE | Standpipe | Ready |  | BSTD1108 |  | 2.10\0.8:2 | BR4-1860-E-00196 | A | [8 empty] | F6 | 5 | 6
SUB902 | DX10 | DIO1 | 130 | 2 | 10 | 0 | 8 | 3 |  |  | DO | 5 | SUB902DB01 | SR01 | Exterior Lighting Relay | SUB902DB01 | Closed |  | SUB902DB01 |  | 2.10\0.8:3 | BR4-1860-E-00078 | A | [8 empty] | F6 | 7 | 8
SUB902 | DX10 | DIO1 | 130 | 2 | 10 | 0 | 8 | 4 |  |  | DO | [9 empty] | 2.10\0.8:4 | [10 empty] | F6 | 9 | 10
SUB902 | DX10 | DIO1 | 130 | 2 | 10 | 0 | 8 | 5 |  |  | DO | [9 empty] | 2.10\0.8:5 | [10 empty] | F6 | 11 | 12
SUB902 | DX10 | DIO1 | 130 | 2 | 10 | 0 | 8 | 6 |  |  | DO | [9 empty] | 2.10\0.8:6 | [10 empty] | F6 | 13 | 14
SUB902 | DX10 | DIO1 | 130 | 2 | 10 | 0 | 8 | 7 |  |  | DO | [9 empty] | 2.10\0.8:7 | [10 empty] | F6 | 15 | 16
SUB902 | DX10 | DIO1 | 130 | 2 | 10 | 0 | 8 | 8 |  |  | DO | [9 empty] | 2.10\0.8:8 | [10 empty] | F6 | 17 | 18
SUB902 | DX10 | DIO1 | 130 | 2 | 10 | 0 | 8 | 9 |  |  | DO | [9 empty] | 2.10\0.8:9 | [10 empty] | F6 | 19 | 20
SUB902 | DX10 | DIO1 | 130 | 2 | 10 | 0 | 8 | 10 |  |  | DO | [9 empty] | 2.10\0.8:10 | [10 empty] | F6 | 21 | 22
SUB902 | DX10 | DIO1 | 130 | 2 | 10 | 0 | 8 | 11 |  |  | DO | [9 empty] | 2.10\0.8:11 | [10 empty] | F6 | 23 | 24
SUB902 | DX10 | DIO1 | 130 | 2 | 10 | 0 | 8 | 12 |  |  | DO | [9 empty] | 2.10\0.8:12 | [10 empty] | F6 | 25 | 26
SUB902 | DX10 | DIO1 | 130 | 2 | 10 | 0 | 8 | 13 |  |  | DO | [9 empty] | 2.10\0.8:13 | [10 empty] | F6 | 27 | 28
SUB902 | DX10 | DIO1 | 130 | 2 | 10 | 0 | 8 | 14 |  |  | DO | [9 empty] | 2.10\0.8:14 | [10 empty] | F6 | 29 | 30
SUB902 | DX10 | DIO1 | 130 | 2 | 10 | 0 | 8 | 15 |  |  | DO | [9 empty] | 2.10\0.8:15 | [10 empty] | F6 | 31 | 32
SUB902 | DX10 | DIO1 | 130 | 2 | 10 | 0 | 9 |  |  | BMXX0 | [10 empty] | 2.10\0.9:
SUB902 | DX10 | DIO1 | 130 | 2 | 10 | 0 | 9 | [13 empty] | 2.10\0.9:
SUB902 | DX10 | DIO1 | 130 | 2 | 10 | 0 | 9 | [13 empty] | 2.10\0.9:
SUB902 | DX10 | DIO1 | 130 | 2 | 10 | 0 | 9 | [13 empty] | 2.10\0.9:
SUB902 | DX10 | DIO1 | 130 | 2 | 10 | 0 | 10 |  |  | BMXX0 | [10 empty] | 2.10\0.10:
SUB902 | DX10 | DIO1 | 130 | 2 | 10 | 0 | 10 | [13 empty] | 2.10\0.10:
SUB902 | DX10 | DIO1 | 130 | 2 | 10 | 0 | 10 | [13 empty] | 2.10\0.10:
SUB902 | DX10 | DIO1 | 130 | 2 | 10 | 0 | 10 | [13 empty] | 2.10\0.10:
SUB902 | DX10 | DIO1 | 130 | 2 | 10 | 0 | 11 |  |  | BMXX0 | [10 empty] | 2.10\0.11:
SUB902 | DX10 | DIO1 | 130 | 2 | 10 | 0 | 11 | [13 empty] | 2.10\0.11:
SUB902 | DX10 | DIO1 | 130 | 2 | 10 | 0 | 11 | [13 empty] | 2.10\0.11:
SUB902 | DX10 | DIO1 | 130 | 2 | 10 | 0 | 11 | [13 empty] | 2.10\0.11:
[10 empty] | * |  | 4 | BPP1108LCS01 | SY01 | EAST TURKEYS NEST HME STANDPIPE PUMP 1 | EMERGENCY STOP RELAY |  | SUB LINK | BPP1108 |  |  |  |  | BPP1108LCS01-C1 4 PAIR | [7 empty] | F12 | 1 | 2 | 3 | 4
[10 empty] | * |  | 4 | BPP1109LCS01 | SY01 | EAST TURKEYS NEST HME STANDPIPE PUMP 2 | EMERGENCY STOP RELAY |  | SUB LINK | BPP1109 |  |  |  |  | BPP1109LCS01-C1 4 PAIR | [7 empty] | F12 | 5 | 6 | 7 | 8
[32 empty] | F12 | 9 | 10 | 11 | 12
[32 empty] | F12 | 13 | 14 | 15 | 16
[32 empty] | F12 | 17 | 18 | 19 | 20
[32 empty] | F12 | 21 | 22 | 23 | 24
[32 empty] | F12 | 25 | 26 | 27 | 28
[32 empty] | F12 | 29 | 30 | 31 | 32
[32 empty] | F12 | 33 | 34 | 35 | 36
[32 empty] | F12 | 37 | 38 | 39 | 40
[32 empty] | F12 | 41 | 42 | 43 | 44
[32 empty] | F12 | 45 | 46 | 47 | 48