## Sub IO Assignment
Item | Box | Node | PLC | Bus | Drop | Rack | Slot | Ch | Terminal | Node Type | IO Type | CPP | Rev | Instrument Tag | Device | Instrument List Description | Desc2 | State | Location | Drive | Datatype | Address | Drawing | Rev | Notes | FAT | SAT | Raw_Zero | Raw_Full | Eng_Zero | Eng_Full | Format | TS | T1 | T2 | T3 | T4 | Alm_AREA | Alm_PRIV | Alm_HELP | Alm_CATEGORY | Alm_CUSTOM1 | Alm_CUSTOM2 | Alm_CUSTOM3 | Alm_CUSTOM4 | Alm_CUSTOM5 | Alm_CUSTOM6 | Alm_CUSTOM7 | Alm_CUSTOM8
BSR131DX01 - NPI HUB Switchroom
BMC131
BSR131 | DX01 | DIO0 | 131 | 0 | 0 | 0 |  | Chassis |  | BMEXBP1200
BSR131 | DX01 | DIO0 | 131 | 0 | 0 | 0 |  | Power |  | BMXCPS4022
BSR131 | DX01 | DIO0 | 131 | 0 | 0 | 0 | 0 | CPU |  | BMEP586040 | DX01ES01 | [5 empty] | BPL131
BSR131 | DX01 | DIO0 | 131 | 0 | 0 | 0 | 0A | MEM |  | BMXRMS004GPF
BSR131 | DX01 | DIO0 | 131 | 0 | 0 | 0 | 2 | Spare - X |  | BMXXEM010
BSR131 | DX01 | DIO0 | 131 | 0 | 0 | 0 | 3 | Comms |  | BMENOC0301 | C | [5 empty] | PLC Comms
BSR131 | DX01 | DIO0 | 131 | 0 | 0 | 0 | 4 | Comms |  | BMENOC0301 | N/C CAT6 | [5 empty] | HMI Comms
BSR131 | DX01 | DIO0 | 131 | 0 | 0 | 0 | 5 | Comms |  | BMENOC0301 | DX01ES01 | [5 empty] | I/O
BSR131 | DX01 | DIO0 | 131 | 0 | 0 | 0 | 6 | Spare - E&X |  | BMXXEM010
BSR131 | DX01 | DIO0 | 131 | 0 | 0 | 0 | 7 | Spare - E&X |  | BMXXEM010
BSR131 | DX01 | DIO0 | 131 | 0 | 0 | 0 | 8 | Spare - X |  | BMXXEM010
BSR131 | DX01 | DIO0 | 131 | 0 | 0 | 0 | 9 | Spare - E&X |  | BMXXEM010
BSR131 | DX01 | DIO0 | 131 | 0 | 0 | 0 | 10 | Spare - X |  | BMXXEM010
BSR131 | DX01 | DIO0 | 131 | 0 | 0 | 0 | 11 | Media Conv |  | BMXXEM010
BMC131
EIO node 1
BSR131 | DX01 | DIO1 | 131 | 2 | 1 | 0 | 0 | Chassis |  | BMEXBP1200
BSR131 | DX01 | DIO1 | 131 | 2 | 1 | 0 | 0 | Power |  | BMXCPS4022 |  |  | total |  | spare |  | % spare
BSR131 | DX01 | DIO1 | 131 | 2 | 1 | 0 | 0 | Comms |  | BMECRA31210 | DX1ES1 |  | 240 |  | 70 |  | 29.17% |  |  |  |  | 2.1\0.0:Comms
BSR131 | DX01 | DIO1 | 131 | 2 | 1 | 0 | 1 | 0 | BMXFCW303 | BMXDDI3202K | DI |  | 2 | BSR131BC02 | VDC02 |  | Battery Charger 110VDC Tripping Supply | Healthy | K112 | BSR131BC02 |  | 2.1\0.1:0 | BR4-1860-E-00076 | 0 | BSR131BC02-C2 IO ON HOLD BUT ADDED TO DX TERMINATIONS AS STANDARD 12PAIR (NO SPARE) | [7 empty] | F1 | 1 | 2
BSR131 | DX01 | DIO1 | 131 | 2 | 1 | 0 | 1 | 1 |  |  | DI |  | 2 | BSR131BC02 | CB02 |  | BMC131INC01 110VDC INC01 Tripping Supply Circuit Breaker | Closed | Q114 | BSR131BC02 |  | 2.1\0.1:1 | BR4-1860-E-00076 | 0 | [8 empty] | F1 | 3 | 4
BSR131 | DX01 | DIO1 | 131 | 2 | 1 | 0 | 1 | 2 |  |  | DI |  | 2 | BSR131BC02 | CB03 |  | BMC131INC02 110VDC INC02 Tripping Supply Circuit Breaker | Closed | Q117 | BSR131BC02 |  | 2.1\0.1:2 | BR4-1860-E-00076 | 0 | [8 empty] | F1 | 5 | 6
BSR131 | DX01 | DIO1 | 131 | 2 | 1 | 0 | 1 | 3 |  |  | DI |  | 2 | BSR131BC02 | CB04 |  | BMC131INC03 110VDC INC03 Tripping Supply Circuit Breaker | Closed | Q120 | BSR131BC02 |  | 2.1\0.1:3 | BR4-1860-E-00076 | 0 | [8 empty] | F1 | 7 | 8
BSR131 | DX01 | DIO1 | 131 | 2 | 1 | 0 | 1 | 4 |  |  | DI |  | 2 | BSR131BC02 | CB05 |  | RSP01 110VDC Tripping Supply Circuit Breaker | Closed | Q123 | BSR131BC02 |  | 2.1\0.1:4 | BR4-1860-E-00076 | 0 | [8 empty] | F1 | 9 | 10
BSR131 | DX01 | DIO1 | 131 | 2 | 1 | 0 | 1 | 5 |  |  | DI |  | 2 | BSR131BC02 | CB06 |  | Spare 110VDC Tripping Supply Circuit Breaker | Closed | Q126 | BSR131BC02 |  | 2.1\0.1:5 | BR4-1860-E-00076 | 0 | [8 empty] | F1 | 11 | 12
BSR131 | DX01 | DIO1 | 131 | 2 | 1 | 0 | 1 | 6 |  |  | DI |  | 2 | BSR131BC02 | CB07 |  | Spare 110VDC Tripping Supply Circuit Breaker | Closed | Q129 | BSR131BC02 |  | 2.1\0.1:6 | BR4-1860-E-00076 | 0 | [8 empty] | F1 | 13 | 14
BSR131 | DX01 | DIO1 | 131 | 2 | 1 | 0 | 1 | 7 |  |  | DI |  | 2 | BSR131BC02 | CB08 |  | Spare 110VDC Tripping Supply Circuit Breaker | Closed | Q132 | BSR131BC02 |  | 2.1\0.1:7 | BR4-1860-E-00076 | 0 | [8 empty] | F1 | 15 | 16
BSR131 | DX01 | DIO1 | 131 | 2 | 1 | 0 | 1 | 8 |  |  | DI |  | 2 | BSR131BC02 | CB09 |  | Spare 110VDC Tripping Supply Circuit Breaker | Closed | Q135 | BSR131BC02 |  | 2.1\0.1:8 | BR4-1860-E-00076 | 0 | [8 empty] | F1 | 17 | 18
BSR131 | DX01 | DIO1 | 131 | 2 | 1 | 0 | 1 | 9 |  |  | DI |  | 2 | BSR131BC02 | CB10 |  | Spare 110VDC Tripping Supply Circuit Breaker | Closed | Q138 | BSR131BC02 |  | 2.1\0.1:9 | BR4-1860-E-00076 | 0 | [8 empty] | F1 | 19 | 20
BSR131 | DX01 | DIO1 | 131 | 2 | 1 | 0 | 1 | 10 |  |  | DI |  | 2 | BSR131BC02 | CB11 |  | Spare 110VDC Tripping Supply Circuit Breaker | Closed | Q141 | BSR131BC02 |  | 2.1\0.1:10 | BR4-1860-E-00076 | 0 | [8 empty] | F1 | 21 | 22
BSR131 | DX01 | DIO1 | 131 | 2 | 1 | 0 | 1 | 11 |  |  | DI |  | 2 | BSR131BC02 | CB12 |  | Spare 110VDC Tripping Supply Circuit Breaker | Closed | Q144 | BSR131BC02 |  | 2.1\0.1:11 | BR4-1860-E-00076 | 0 | [8 empty] | F1 | 23 | 24
BSR131 | DX01 | DIO1 | 131 | 2 | 1 | 0 | 1 | 12 |  |  | DI | [10 empty] | 2.1\0.1:12 | [10 empty] | F1 | 25 | 26
BSR131 | DX01 | DIO1 | 131 | 2 | 1 | 0 | 1 | 13 |  |  | DI | [10 empty] | 2.1\0.1:13 | [10 empty] | F1 | 27 | 28
BSR131 | DX01 | DIO1 | 131 | 2 | 1 | 0 | 1 | 14 |  |  | DI | [10 empty] | 2.1\0.1:14 | [10 empty] | F1 | 29 | 30
BSR131 | DX01 | DIO1 | 131 | 2 | 1 | 0 | 1 | 15 |  |  | DI | [10 empty] | 2.1\0.1:15 | [10 empty] | F1 | 31 | 32
BSR131 | DX01 | DIO1 | 131 | 2 | 1 | 0 | 1 | 16 |  |  | DI |  | 2 | BSR131UP01SW01 | XS01 |  | UPS Surge Filter | Healthy |  | BSR131UP01 |  | 2.1\0.1:16 | BR4-1860-E-00090 | 0 | BSR131UP01SD01-C1 1 PAIR (NO SPARE) | [7 empty] | F1 | 33 | 34
BSR131 | DX01 | DIO1 | 131 | 2 | 1 | 0 | 1 | 17 |  |  | DI |  | 2 | BSR131UP01 | SW01 |  | UPS Bypassed / Test | Active |  | BSR131UP01 |  | 2.1\0.1:17 | BR4-1860-E-00090 | 0 | BSR131UP01SW01-C1 4 PAIR (NO SPARE) | [7 empty] | F1 | 35 | 36
BSR131 | DX01 | DIO1 | 131 | 2 | 1 | 0 | 1 | 18 |  |  | DI | [10 empty] | 2.1\0.1:18 | BR4-1860-E-00090 | 0 | [8 empty] | F1 | 37 | 38
BSR131 | DX01 | DIO1 | 131 | 2 | 1 | 0 | 1 | 19 |  |  | DI |  | 2 | BSR131UP01SW01 | ZS01 |  | UPS in Normal Mode | Active |  | BSR131UP01 |  | 2.1\0.1:19 | BR4-1860-E-00090 | 0 | [8 empty] | F1 | 39 | 40
BSR131 | DX01 | DIO1 | 131 | 2 | 1 | 0 | 1 | 20 |  |  | DI | [10 empty] | 2.1\0.1:20 | BR4-1860-E-00090 | 0 | [8 empty] | F1 | 41 | 42
BSR131 | DX01 | DIO1 | 131 | 2 | 1 | 0 | 1 | 21 |  |  | DI | [10 empty] | 2.1\0.1:21 | [10 empty] | F1 | 43 | 44
BSR131 | DX01 | DIO1 | 131 | 2 | 1 | 0 | 1 | 22 |  |  | DI | [10 empty] | 2.1\0.1:22 | [10 empty] | F1 | 45 | 46
BSR131 | DX01 | DIO1 | 131 | 2 | 1 | 0 | 1 | 23 |  |  | DI | [10 empty] | 2.1\0.1:23 | [10 empty] | F1 | 47 | 48
BSR131 | DX01 | DIO1 | 131 | 2 | 1 | 0 | 1 | 24 |  |  | DI | [10 empty] | 2.1\0.1:24 | [10 empty] | F1 | 49 | 50
BSR131 | DX01 | DIO1 | 131 | 2 | 1 | 0 | 1 | 25 |  |  | DI | [10 empty] | 2.1\0.1:25 | [10 empty] | F1 | 51 | 52
BSR131 | DX01 | DIO1 | 131 | 2 | 1 | 0 | 1 | 26 |  |  | DI | [10 empty] | 2.1\0.1:26 | [10 empty] | F1 | 53 | 54
BSR131 | DX01 | DIO1 | 131 | 2 | 1 | 0 | 1 | 27 |  |  | DI | [10 empty] | 2.1\0.1:27 | [10 empty] | F1 | 55 | 56
BSR131 | DX01 | DIO1 | 131 | 2 | 1 | 0 | 1 | 28 |  |  | DI | [10 empty] | 2.1\0.1:28 | [10 empty] | F1 | 57 | 58
BSR131 | DX01 | DIO1 | 131 | 2 | 1 | 0 | 1 | 29 |  |  | DI | [10 empty] | 2.1\0.1:29 | [10 empty] | F1 | 59 | 60
BSR131 | DX01 | DIO1 | 131 | 2 | 1 | 0 | 1 | 30 |  |  | DI | [10 empty] | 2.1\0.1:30 | [10 empty] | F1 | 61 | 62
BSR131 | DX01 | DIO1 | 131 | 2 | 1 | 0 | 1 | 31 |  |  | DI | [10 empty] | 2.1\0.1:31 | [10 empty] | F1 | 63 | 64
BSR131 | DX01 | DIO1 | 131 | 2 | 1 | 0 | 2 | 0 | BMXFCW303 | BMXDDI3202K | DI |  | 2 | BSR131UP01DB01 | R1 |  | DX01 Primary 240VAC UPS Circuit Breaker | Closed | R1 | BSR131UP01DB01 |  | 2.1\0.2:0 | BR4-1860-E-00086 | 0 | BSR131UP01DB01-C2 30 PAIR - 24 PAIR USED - REST TO SPARE TERMINAL STRIP | [7 empty] | F2 | 1 | 2
BSR131 | DX01 | DIO1 | 131 | 2 | 1 | 0 | 2 | 1 |  |  | DI |  | 2 | BSR131UP01DB01 | W1 |  | DX01 Secondary 240VAC UPS Circuit Breaker | Closed | W1 | BSR131UP01DB01 |  | 2.1\0.2:1 | BR4-1860-E-00086 | 0 | [8 empty] | F2 | 3 | 4
BSR131 | DX01 | DIO1 | 131 | 2 | 1 | 0 | 2 | 2 |  |  | DI |  | 2 | BSR131UP01DB01 | B1 |  | NEP130 240VAC Primary UPS Circuit Breaker | Closed | B1 | BSR131UP01DB01 |  | 2.1\0.2:2 | BR4-1860-E-00086 | 0 | [8 empty] | F2 | 5 | 6
BSR131 | DX01 | DIO1 | 131 | 2 | 1 | 0 | 2 | 3 |  |  | DI |  | 2 | BSR131UP01DB01 | R2 |  | NEP130 240VAC Secondary UPS Circuit Breaker | Closed | R2 | BSR131UP01DB01 |  | 2.1\0.2:3 | BR4-1860-E-00086 | 0 | [8 empty] | F2 | 7 | 8
BSR131 | DX01 | DIO1 | 131 | 2 | 1 | 0 | 2 | 4 |  |  | DI |  | 2 | BSR131UP01DB01 | W2 |  | DX02 240VAC UPS Circuit Breaker | Closed | W2 | BSR131UP01DB01 |  | 2.1\0.2:4 | BR4-1860-E-00086 | 0 | [8 empty] | F2 | 9 | 10
BSR131 | DX01 | DIO1 | 131 | 2 | 1 | 0 | 2 | 5 |  |  | DI |  | 2 | BSR131UP01DB01 | B2 |  | DX03 240VAC UPS Circuit Breaker | Closed | B2 | BSR131UP01DB01 |  | 2.1\0.2:5 | BR4-1860-E-00086 | 0 | [8 empty] | F2 | 11 | 12
BSR131 | DX01 | DIO1 | 131 | 2 | 1 | 0 | 2 | 6 |  |  | DI |  | 2 | BSR131UP01DB01 | R3 |  | DX04 240VAC UPS Circuit Breaker | Closed | R3 | BSR131UP01DB01 |  | 2.1\0.2:6 | BR4-1860-E-00086 | 0 | [8 empty] | F2 | 13 | 14
BSR131 | DX01 | DIO1 | 131 | 2 | 1 | 0 | 2 | 7 |  |  | DI |  | 2 | BSR131UP01DB01 | W3 |  | HVAC Panel 240VAC UPS Circuit Breaker | Closed | W3 | BSR131UP01DB01 |  | 2.1\0.2:7 | BR4-1860-E-00086 | 0 | [8 empty] | F2 | 15 | 16
BSR131 | DX01 | DIO1 | 131 | 2 | 1 | 0 | 2 | 8 |  |  | DI |  | 2 | BSR131UP01DB01 | B3 |  | BSR131FIP01 Fire Panel 240VAC UPS Circuit Breaker | Closed | B3 | BSR131UP01DB01 |  | 2.1\0.2:8 | BR4-1860-E-00086 | 0 | [8 empty] | F2 | 17 | 18
BSR131 | DX01 | DIO1 | 131 | 2 | 1 | 0 | 2 | 9 |  |  | DI |  | 2 | BSR131UP01DB01 | R4 |  | BSR131VES01 VESDA Fire Detection Panel Breaker | Closed | R4 | BSR131UP01DB01 |  | 2.1\0.2:9 | BR4-1860-E-00086 | 0 | [8 empty] | F2 | 19 | 20
BSR131 | DX01 | DIO1 | 131 | 2 | 1 | 0 | 2 | 10 |  |  | DI |  | 2 | BSR131UP01DB01 | W4 |  | Cardax 240VAC UPS Circuit Breaker | Closed | W4 | BSR131UP01DB01 |  | 2.1\0.2:10 | BR4-1860-E-00086 | 0 | [8 empty] | F2 | 21 | 22
BSR131 | DX01 | DIO1 | 131 | 2 | 1 | 0 | 2 | 11 |  |  | DI |  | 2 | BSR131UP01DB01 | B4 |  | BSR131FSS01PN01 Supression Control Panel Breaker | Closed | B4 | BSR131UP01DB01 |  | 2.1\0.2:11 | BR4-1860-E-00086 | 0 | [8 empty] | F2 | 23 | 24
BSR131 | DX01 | DIO1 | 131 | 2 | 1 | 0 | 2 | 12 |  |  | DI |  | 2 | BSR131UP01DB01 | R5 |  | BTY1502AX01 240VAC UPS Circuit Breaker | Closed | R5 | BSR131UP01DB01 |  | 2.1\0.2:12 | BR4-1860-E-00086 | 0 | [8 empty] | F2 | 25 | 26
BSR131 | DX01 | DIO1 | 131 | 2 | 1 | 0 | 2 | 13 |  |  | DI |  | 3 | BSR131UP01DB01 | W5 |  | BPQE2115MC01 Potable Water 240VAC UPS Circuit Breaker | Closed | W5 | BSR131UP01DB01 |  | 2.1\0.2:13 | BR4-1860-E-00086 | 0 | [8 empty] | F2 | 27 | 28
BSR131 | DX01 | DIO1 | 131 | 2 | 1 | 0 | 2 | 14 |  |  | DI |  | 2 | BSR131UP01DB01 | B5 |  | Spare Circuit Breaker | Closed | B5 | BSR131UP01DB01 |  | 2.1\0.2:14 | BR4-1860-E-00086 | 0 | [8 empty] | F2 | 29 | 30
BSR131 | DX01 | DIO1 | 131 | 2 | 1 | 0 | 2 | 15 |  |  | DI |  | 2 | BSR131UP01DB01 | R6 |  | Spare Circuit Breaker | Closed | R6 | BSR131UP01DB01 |  | 2.1\0.2:15 | BR4-1860-E-00086 | 0 | [8 empty] | F2 | 31 | 32
BSR131 | DX01 | DIO1 | 131 | 2 | 1 | 0 | 2 | 16 |  |  | DI |  | 2 | BSR131UP01DB01 | W6 |  | Spare Circuit Breaker | Closed | W6 | BSR131UP01DB01 |  | 2.1\0.2:16 | BR4-1860-E-00086 | 0 | [8 empty] | F2 | 33 | 34
BSR131 | DX01 | DIO1 | 131 | 2 | 1 | 0 | 2 | 17 |  |  | DI |  | 2 | BSR131UP01DB01 | B6 |  | Spare Circuit Breaker | Closed | B6 | BSR131UP01DB01 |  | 2.1\0.2:17 | BR4-1860-E-00086 | 0 | [8 empty] | F2 | 35 | 36
BSR131 | DX01 | DIO1 | 131 | 2 | 1 | 0 | 2 | 18 |  |  | DI |  | 2 | BSR131UP01DB01 | R7 |  | Spare Circuit Breaker | Closed | R7 | BSR131UP01DB01 |  | 2.1\0.2:18 | BR4-1860-E-00086 | 0 | [8 empty] | F2 | 37 | 38
BSR131 | DX01 | DIO1 | 131 | 2 | 1 | 0 | 2 | 19 |  |  | DI |  | 2 | BSR131UP01DB01 | W7 |  | Spare Circuit Breaker | Closed | W7 | BSR131UP01DB01 |  | 2.1\0.2:19 | BR4-1860-E-00086 | 0 | [8 empty] | F2 | 39 | 40
BSR131 | DX01 | DIO1 | 131 | 2 | 1 | 0 | 2 | 20 |  |  | DI |  | 2 | BSR131UP01DB01 | B7 |  | Spare Circuit Breaker | Closed | B7 | BSR131UP01DB01 |  | 2.1\0.2:20 | BR4-1860-E-00086 | 0 | [8 empty] | F2 | 41 | 42
BSR131 | DX01 | DIO1 | 131 | 2 | 1 | 0 | 2 | 21 |  |  | DI |  | 2 | BSR131UP01DB01 | R8 |  | Spare Circuit Breaker | Closed | R8 | BSR131UP01DB01 |  | 2.1\0.2:21 | BR4-1860-E-00086 | 0 | [8 empty] | F2 | 43 | 44
BSR131 | DX01 | DIO1 | 131 | 2 | 1 | 0 | 2 | 22 |  |  | DI |  | 2 | BSR131UP01DB01 | W8 |  | Spare Circuit Breaker | Closed | W8 | BSR131UP01DB01 |  | 2.1\0.2:22 | BR4-1860-E-00086 | 0 | [8 empty] | F2 | 45 | 46
BSR131 | DX01 | DIO1 | 131 | 2 | 1 | 0 | 2 | 23 |  |  | DI |  | 2 | BSR131UP01DB01 | B8 |  | Spare Circuit Breaker | Closed | B8 | BSR131UP01DB01 |  | 2.1\0.2:23 | BR4-1860-E-00086 | 0 | [8 empty] | F2 | 47 | 48
BSR131 | DX01 | DIO1 | 131 | 2 | 1 | 0 | 2 | 24 |  |  | DI | [10 empty] | 2.1\0.2:24 | [10 empty] | F2 | 49 | 50
BSR131 | DX01 | DIO1 | 131 | 2 | 1 | 0 | 2 | 25 |  |  | DI | [10 empty] | 2.1\0.2:25 | [10 empty] | F2 | 51 | 52
BSR131 | DX01 | DIO1 | 131 | 2 | 1 | 0 | 2 | 26 |  |  | DI | [10 empty] | 2.1\0.2:26 | [10 empty] | F2 | 53 | 54
BSR131 | DX01 | DIO1 | 131 | 2 | 1 | 0 | 2 | 27 |  |  | DI | [10 empty] | 2.1\0.2:27 | [10 empty] | F2 | 55 | 56
BSR131 | DX01 | DIO1 | 131 | 2 | 1 | 0 | 2 | 28 |  |  | DI | [10 empty] | 2.1\0.2:28 | [10 empty] | F2 | 57 | 58
BSR131 | DX01 | DIO1 | 131 | 2 | 1 | 0 | 2 | 29 |  |  | DI | [10 empty] | 2.1\0.2:29 | [10 empty] | F2 | 59 | 60
BSR131 | DX01 | DIO1 | 131 | 2 | 1 | 0 | 2 | 30 |  |  | DI | [10 empty] | 2.1\0.2:30 | [10 empty] | F2 | 61 | 62
BSR131 | DX01 | DIO1 | 131 | 2 | 1 | 0 | 2 | 31 |  |  | DI | [10 empty] | 2.1\0.2:31 | [10 empty] | F2 | 63 | 64
BSR131 | DX01 | DIO1 | 131 | 2 | 1 | 0 | 3 | 0 | BMXFCW303 | BMXDDI3202K | DI |  | 2 | BSR131DX01 | VDC01 |  | DX01 24VDC Control Supply Healthy | Healthy | Q110 | BSR131DX01 |  | 2.1\0.3:0 | BR4-1860-E-00092 | 0 | INTERNAL WIRING | [7 empty] | F3 | 1 | 2
BSR131 | DX01 | DIO1 | 131 | 2 | 1 | 0 | 3 | 1 |  |  | DI |  | 2 | BSR131DX01 | VDC02 |  | DX01 24VDC Output Module Control Supply | Healthy | Q170 | BSR131DX01 |  | 2.1\0.3:1 | BR4-1860-E-00092 | 0 | [8 empty] | F3 | 3 | 4
BSR131 | DX01 | DIO1 | 131 | 2 | 1 | 0 | 3 | 2 |  |  | DI |  | 2 | BSR131DX01 | VDC03 |  | BSR131UP01 24VDC Control Supply | Healthy | Q254 | BSR131DX01 |  | 2.1\0.3:2 | BR4-1860-E-00093 | 0 | [8 empty] | F3 | 5 | 6
BSR131 | DX01 | DIO1 | 131 | 2 | 1 | 0 | 3 | 3 |  |  | DI |  | 2 | BSR131DX01 | VDC04 |  | BSR131BC01DB01 24VDC Control Supply | Healthy | Q257 | BSR131DX01 |  | 2.1\0.3:3 | BR4-1860-E-00093 | 0 | [8 empty] | F3 | 7 | 8
BSR131 | DX01 | DIO1 | 131 | 2 | 1 | 0 | 3 | 4 |  |  | DI |  | 2 | BSR131DX01 | VDC05 |  | BSR131BC02DB01 24VDC Control Supply | Healthy | Q260 | BSR131DX01 |  | 2.1\0.3:4 | BR4-1860-E-00093 | 0 | [8 empty] | F3 | 9 | 10
BSR131 | DX01 | DIO1 | 131 | 2 | 1 | 0 | 3 | 5 |  |  | DI |  | 2 | BSR131DX01 | VDC06 |  | BSR131UP01DB01 24VDC Control Supply | Healthy | Q263 | BSR131DX01 |  | 2.1\0.3:5 | BR4-1860-E-00093 | 0 | [8 empty] | F3 | 11 | 12
BSR131 | DX01 | DIO1 | 131 | 2 | 1 | 0 | 3 | 6 |  |  | DI |  | 2 | BSR131DX01 | VDC07 |  | Misc Switchroom Alarms 24VDC Control Supply | Healthy | Q266 | BSR131DX01 |  | 2.1\0.3:6 | BR4-1860-E-00093 | 0 | [8 empty] | F3 | 13 | 14
BSR131 | DX01 | DIO1 | 131 | 2 | 1 | 0 | 3 | 7 |  |  | DI |  | 2 | BSR131DX01 | VDC08 |  | Spare | Healthy | Q269 | BSR131DX01 |  | 2.1\0.3:7 | BR4-1860-E-00093 | 0 | [8 empty] | F3 | 15 | 16
BSR131 | DX01 | DIO1 | 131 | 2 | 1 | 0 | 3 | 8 |  |  | DI |  | 2 | BSR131DX01 | VDC09 |  | Spare | Healthy | Q272 | BSR131DX01 |  | 2.1\0.3:8 | BR4-1860-E-00093 | 0 | [8 empty] | F3 | 17 | 18
BSR131 | DX01 | DIO1 | 131 | 2 | 1 | 0 | 3 | 9 |  |  | DI |  | 2 | BSR131DX01 | VDC10 |  | Spare | Healthy | Q275 | BSR131DX01 |  | 2.1\0.3:9 | BR4-1860-E-00093 | 0 | [8 empty] | F3 | 19 | 20
BSR131 | DX01 | DIO1 | 131 | 2 | 1 | 0 | 3 | 10 |  |  | DI |  | 2 | BSR131DX01 | VDC11 |  | Spare | Healthy | Q278 | BSR131DX01 |  | 2.1\0.3:10 | BR4-1860-E-00093 | 0 | [8 empty] | F3 | 21 | 22
BSR131 | DX01 | DIO1 | 131 | 2 | 1 | 0 | 3 | 11 |  |  | DI |  | 2 | BSR131DX01 | VDC12 |  | Spare | Healthy | Q281 | BSR131DX01 |  | 2.1\0.3:11 | BR4-1860-E-00093 | 0 | [8 empty] | F3 | 23 | 24
BSR131 | DX01 | DIO1 | 131 | 2 | 1 | 0 | 3 | 12 |  |  | DI |  | 2 | BSR131FIP01 | XS03 |  | Substation Gas | Discharged |  | BSR131FIP01 |  | 2.1\0.3:12 | BR4-1860-E-00087 | 0 | [8 empty] | F3 | 25 | 26
BSR131 | DX01 | DIO1 | 131 | 2 | 1 | 0 | 3 | 13 |  |  | DI |  | 2 | BSR131 | PB01 |  | BSR131 Shutdown Pushbutton | Healthy | SESP | BSR131 |  | 2.1\0.3:13 | BR4-1860-E-00087 | 0 | BSR131PB01-C1 1 PAIR (NO SPARE) | [7 empty] | F3 | 27 | 28
BSR131 | DX01 | DIO1 | 131 | 2 | 1 | 0 | 3 | 14 |  |  | DI |  | 2 | BSR131DX01 | XS01 |  | DX01 24VDC Power Supply 1 | Healthy | U103A | BSR131DX01 |  | 2.1\0.3:14 | BR4-1860-E-00087 | 0 | INTERNAL WIRING | [7 empty] | F3 | 29 | 30
BSR131 | DX01 | DIO1 | 131 | 2 | 1 | 0 | 3 | 15 |  |  | DI |  | 2 | BSR131DX01 | XS02 |  | DX01 24VDC Power Supply 2 | Healthy | U103B | BSR131DX01 |  | 2.1\0.3:15 | BR4-1860-E-00087 | 0 | [8 empty] | F3 | 31 | 32
BSR131 | DX01 | DIO1 | 131 | 2 | 1 | 0 | 3 | 16 |  |  | DI |  | 2 | BSR131NEP01 | CB01 |  | NEP Primary PDU Circuit Breaker | Healthy | Q130 | BSR131NEP01 |  | 2.1\0.3:16 | BR4-1860-E-00087 | 0 | BSR131NEP01-C1 4 PAIR (2PRS SPARE) | [7 empty] | F3 | 33 | 34
BSR131 | DX01 | DIO1 | 131 | 2 | 1 | 0 | 3 | 17 |  |  | DI |  | 2 | BSR131NEP01 | CB02 |  | NEP Secondary PDU Circuit Breaker | Healthy | Q180 | BSR131NEP01 |  | 2.1\0.3:17 | BR4-1860-E-00087 | 0 | [8 empty] | F3 | 35 | 36
BSR131 | DX01 | DIO1 | 131 | 2 | 1 | 0 | 3 | 18 |  |  | DI |  | 2 | BSR131FIP01 | XS01 |  | Fire Panel | Healthy |  | BSR131FIP01 |  | 2.1\0.3:18 | BR4-1860-E-00087 | 0 | BSR131FIP01-C1 4 PAIR (1PR SPARE) | [7 empty] | F3 | 37 | 38
BSR131 | DX01 | DIO1 | 131 | 2 | 1 | 0 | 3 | 19 |  |  | DI |  | 2 | BSR131FIP01 | IS01 |  | Fire Panel Isolated | Healthy |  | BSR131FIP01 |  | 2.1\0.3:19 | BR4-1860-E-00087 | 0 | [8 empty] | F3 | 39 | 40
BSR131 | DX01 | DIO1 | 131 | 2 | 1 | 0 | 3 | 20 |  |  | DI |  | 2 | BSR131FIP01 | XS02 |  | Fire Alarm | Healthy |  | BSR131FIP01 |  | 2.1\0.3:20 | BR4-1860-E-00087 | 0 | [8 empty] | F3 | 41 | 42
BSR131 | DX01 | DIO1 | 131 | 2 | 1 | 0 | 3 | 21 |  |  | DI |  | 2 | BSR131PN01 | TS01 | NPI HUB SWITCHROOM CONTROL PANEL 1 | Airlock High Temperature | Alarm |  | BSR131PN01 |  | 2.1\0.3:21 | BR4-1860-E-00087 | 0 | BSR131PN01-C2 10 PAIR (3PR SPARE) | [7 empty] | F3 | 43 | 44
BSR131 | DX01 | DIO1 | 131 | 2 | 1 | 0 | 3 | 22 |  |  | DI |  | 2 | BSR131PN01 | TS02 | NPI HUB SWITCHROOM CONTROL PANEL 1 | Fixed Plant Room High Temperature | Alarm |  | BSR131PN01 |  | 2.1\0.3:22 | BR4-1860-E-00087 | 0 | [8 empty] | F3 | 45 | 46
BSR131 | DX01 | DIO1 | 131 | 2 | 1 | 0 | 3 | 23 |  |  | DI |  | 2 | BSR131PN01 | PS01 | NPI HUB SWITCHROOM CONTROL PANEL 1 | Switchroom Pressurisation Fan Filter | Healthy |  | BSR131PN01 |  | 2.1\0.3:23 | BR4-1860-E-00087 | 0 | [8 empty] | F3 | 47 | 48
BSR131 | DX01 | DIO1 | 131 | 2 | 1 | 0 | 3 | 24 |  |  | DI |  | 2 | BSR131PN01 | XS01 | NPI HUB SWITCHROOM CONTROL PANEL 1 | Air Conditioner | Healthy |  | BSR131PN01 |  | 2.1\0.3:24 | BR4-1860-E-00087 | 0 | [8 empty] | F3 | 49 | 50
BSR131 | DX01 | DIO1 | 131 | 2 | 1 | 0 | 3 | 25 |  |  | DI |  | 2 | BSR131PN01 | XS02 | NPI HUB SWITCHROOM CONTROL PANEL 1 | Air Conditioner Filter Blocked | Alarm |  | BSR131PN01 |  | 2.1\0.3:25 | BR4-1860-E-00087 | 0 | [8 empty] | F3 | 51 | 52
BSR131 | DX01 | DIO1 | 131 | 2 | 1 | 0 | 3 | 26 |  |  | DI |  | 2 | BSR131PN01 | XS03 | NPI HUB SWITCHROOM CONTROL PANEL 1 | Air Conditioner 1 - Fixed Plant Room Fault | Alarm |  | BSR131PN01 |  | 2.1\0.3:26 | BR4-1860-E-00087 | 0 | [8 empty] | F3 | 53 | 54
BSR131 | DX01 | DIO1 | 131 | 2 | 1 | 0 | 3 | 27 |  |  | DI |  | 2 | BSR131PN01 | XS04 | NPI HUB SWITCHROOM CONTROL PANEL 1 | Air Conditioner 2 - Fixed Plant Room Fault | Alarm |  | BSR131PN01 |  | 2.1\0.3:27 | BR4-1860-E-00087 | 0 | [8 empty] | F3 | 55 | 56
BSR131 | DX01 | DIO1 | 131 | 2 | 1 | 0 | 3 | 28 |  |  | DI |  | 2 | BSR131DB01 | XS01 |  | BSR131DB01 Surge Protection | Healthy | SD106 | BSR131DB01 |  | 2.1\0.3:28 | BR4-1860-E-00087 | 0 | BSR131DB01-C2 1 PAIR (NO SPARE) | [7 empty] | F3 | 57 | 58
BSR131 | DX01 | DIO1 | 131 | 2 | 1 | 0 | 3 | 29 |  |  | DI |  | 2 | BSR131UP01DB01 | XS01 |  | BSR131UP01DB01 Surge Protection | Healthy | SD106 | BSR131UP01DB01 |  | 2.1\0.3:29 | BR4-1860-E-00087 | 0 | BSR131UP01DB01-C2 1PR OF THE 30 | [7 empty] | F3 | 59 | 60
BSR131 | DX01 | DIO1 | 131 | 2 | 1 | 0 | 3 | 30 |  |  | DI |  | 2 | BSR131PN01 | XS06 | NPI HUB SWITCHROOM CONTROL PANEL 1 | Air Conditioner 6 - Airlock Fault | Alarm |  | BSR131PN01 |  | 2.1\0.3:28 | BR4-1860-E-00087 | 0 | [8 empty] | F3 | 61 | 62
BSR131 | DX01 | DIO1 | 131 | 2 | 1 | 0 | 3 | 31 |  |  | DI |  | 2 | BSR131PN01 | XS07 | NPI HUB SWITCHROOM CONTROL PANEL 1 | Air Conditioner 7 - Airlock Fault | Alarm |  | BSR131PN01 |  | 2.1\0.3:29 | BR4-1860-E-00087 | 0 | [8 empty] | F3 | 63 | 64
BSR131 | DX01 | DIO1 | 131 | 2 | 1 | 0 | 4 | 0 | BMXFCW303 | BMXDDI3202K | DI |  | 2 | BMC131INC01 | VDC01 | PROCESS BUS INCOMER | 24VDC Control Supply | Healthy | Q267 | BMC131INC01 |  | 2.1\0.4:0 | BR4-1860-E-00063 | 0 | BMC131INC01-C1 8 PAIR (NO SPARE) | [7 empty] | F4 | 1 | 2
BSR131 | DX01 | DIO1 | 131 | 2 | 1 | 0 | 4 | 1 |  |  | DI |  | 2 | BMC131INC01 | CB02 | PROCESS BUS INCOMER | Arc Flash Supply | Healthy | Q204 | BMC131INC01 |  | 2.1\0.4:1 | BR4-1860-E-00063 | 0 | [8 empty] | F4 | 3 | 4
BSR131 | DX01 | DIO1 | 131 | 2 | 1 | 0 | 4 | 2 |  |  | DI |  | 2 | BMC131INC01 | TRP02 | PROCESS BUS INCOMER | Arc Flash Trip Alarm | Healthy | F113 | BMC131INC01 |  | 2.1\0.4:2 | BR4-1860-E-00063 | 0 | [8 empty] | F4 | 5 | 6
BSR131 | DX01 | DIO1 | 131 | 2 | 1 | 0 | 4 | 3 |  |  | DI |  | 2 | BMC131INC01 | XS02 | PROCESS BUS INCOMER | Arc Flash Relay Self Supervision | Healthy | F113 | BMC131INC01 |  | 2.1\0.4:3 | BR4-1860-E-00063 | 0 | [8 empty] | F4 | 7 | 8
BSR131 | DX01 | DIO1 | 131 | 2 | 1 | 0 | 4 | 4 |  |  | DI |  | 2 | BMC131INC01 | CB03 | PROCESS BUS INCOMER | Incomer Circuit Breaker Spring Charge Supply | OK | Q212 | BMC131INC01 |  | 2.1\0.4:4 | BR4-1860-E-00063 | 0 | [8 empty] | F4 | 9 | 10
BSR131 | DX01 | DIO1 | 131 | 2 | 1 | 0 | 4 | 5 |  |  | DI |  | 2 | BMC131INC01 | CB04 | PROCESS BUS INCOMER | Incomer Circuit Breaker Trip Supply | OK | Q220 | BMC131INC01 |  | 2.1\0.4:5 | BR4-1860-E-00063 | 0 | [8 empty] | F4 | 11 | 12
BSR131 | DX01 | DIO1 | 131 | 2 | 1 | 0 | 4 | 6 |  |  | DI |  | 2 | BMC131INC01 | CB05 | PROCESS BUS INCOMER | Incomer Circuit Breaker 24VDC Cubicle Bus Supply | Healthy | Q256 | BMC131INC01 |  | 2.1\0.4:6 | BR4-1860-E-00063 | 0 | [8 empty] | F4 | 13 | 14
BSR131 | DX01 | DIO1 | 131 | 2 | 1 | 0 | 4 | 7 |  |  | DI |  | 2 | BMC131INC01 | XS03 | PROCESS BUS INCOMER | Surge Protection Relay | Healthy | SD144-146 | BMC131INC01 |  | 2.1\0.4:7 | BR4-1860-E-00063 | 0 | [8 empty] | F4 | 15 | 16
BSR131 | DX01 | DIO1 | 131 | 2 | 1 | 0 | 4 | 8 |  |  | DI |  | 2 | BMC131INC01 | CB06 | PROCESS BUS INCOMER | 110VDC/24VDC Power Supply | Healthy | Q215 | BMC131INC01 |  | 2.1\0.4:8 | BR4-1860-E-00063 | 0 | [8 empty] | F4 | 17 | 18
BSR131 | DX01 | DIO1 | 131 | 2 | 1 | 0 | 4 | 9 |  |  | DI |  | 2 | BMC131INC01 | TRP03 |  | Upstream Intertrip | Active | K294 | BMC131INC01 |  | 2.1\0.4:9 | BR4-1860-E-00063 | 0 | [8 empty] | F4 | 19 | 20
BSR131 | DX01 | DIO1 | 131 | 2 | 1 | 0 | 4 | 10 |  |  | DI |  | 2 | BMC131INC02 | VDC01 | ESSENTIAL BUS INCOMER | 24VDC Control Supply | Healthy | Q267 | BMC131INC02 |  | 2.1\0.4:10 | BR4-1860-E-00065 | 0 | BMC131INC02-C1 8 PAIR (3 PR SPARE) | [7 empty] | F4 | 21 | 22
BSR131 | DX01 | DIO1 | 131 | 2 | 1 | 0 | 4 | 11 |  |  | DI |  | 2 | BMC131INC02 | CB03 | ESSENTIAL BUS INCOMER | Incomer Circuit Breaker Spring Charge Supply | OK | Q212 | BMC131INC02 |  | 2.1\0.4:11 | BR4-1860-E-00065 | 0 | [8 empty] | F4 | 23 | 24
BSR131 | DX01 | DIO1 | 131 | 2 | 1 | 0 | 4 | 12 |  |  | DI |  | 2 | BMC131INC02 | CB04 | ESSENTIAL BUS INCOMER | Incomer Circuit Breaker Trip Supply | OK | Q220 | BMC131INC02 |  | 2.1\0.4:12 | BR4-1860-E-00065 | 0 | [8 empty] | F4 | 25 | 26
BSR131 | DX01 | DIO1 | 131 | 2 | 1 | 0 | 4 | 13 |  |  | DI |  | 2 | BMC131INC02 | CB05 | ESSENTIAL BUS INCOMER | Incomer Circuit Breaker 24VDC Cubicle Bus Supply | Healthy | Q256 | BMC131INC02 |  | 2.1\0.4:13 | BR4-1860-E-00065 | 0 | [8 empty] | F4 | 27 | 28
BSR131 | DX01 | DIO1 | 131 | 2 | 1 | 0 | 4 | 14 |  |  | DI |  | 2 | BMC131INC02 | XS03 | ESSENTIAL BUS INCOMER | Surge Protection Relay | Healthy | SD144-146 | BMC131INC02 |  | 2.1\0.4:14 | BR4-1860-E-00065 | 0 | [8 empty] | F4 | 29 | 30
BSR131 | DX01 | DIO1 | 131 | 2 | 1 | 0 | 4 | 15 |  |  | DI |  | 2 | BMC131INC02 | CB06 | ESSENTIAL BUS INCOMER | 110VDC/24VDC Power Supply | Healthy | Q215 | BMC131INC02 |  | 2.1\0.4:15 | BR4-1860-E-00065 | 0 | [8 empty] | F4 | 31 | 32
BSR131 | DX01 | DIO1 | 131 | 2 | 1 | 0 | 4 | 16 |  |  | DI |  | 2 | BMC131INC03 | VDC01 | GENERATOR INCOMER | 24VDC Control Supply | Healthy | Q267 | BMC131INC03 |  | 2.1\0.4:16 | BR4-1860-E-00067 | 0 | BMC131INC03-C1 8 PAIR (2 PR SPARE) | [7 empty] | F4 | 33 | 34
BSR131 | DX01 | DIO1 | 131 | 2 | 1 | 0 | 4 | 17 |  |  | DI |  | 2 | BMC131INC03 | TRP02 | GENERATOR INCOMER | Arc Flash Trip Alarm | Healthy | F110 | BMC131INC03 |  | 2.1\0.4:17 | BR4-1860-E-00067 | 0 | [8 empty] | F4 | 35 | 36
BSR131 | DX01 | DIO1 | 131 | 2 | 1 | 0 | 4 | 18 |  |  | DI |  | 2 | BMC131INC03 | CB03 | GENERATOR INCOMER | Incomer Circuit Breaker Spring Charge Supply | OK | Q212 | BMC131INC03 |  | 2.1\0.4:18 | BR4-1860-E-00067 | 0 | [8 empty] | F4 | 37 | 38
BSR131 | DX01 | DIO1 | 131 | 2 | 1 | 0 | 4 | 19 |  |  | DI |  | 2 | BMC131INC03 | CB04 | GENERATOR INCOMER | Incomer Circuit Breaker Trip Supply | OK | Q220 | BMC131INC03 |  | 2.1\0.4:19 | BR4-1860-E-00067 | 0 | [8 empty] | F4 | 39 | 40
BSR131 | DX01 | DIO1 | 131 | 2 | 1 | 0 | 4 | 20 |  |  | DI |  | 2 | BMC131INC03 | CB05 | GENERATOR INCOMER | Incomer Circuit Breaker 24VDC Cubicle Bus Supply | Healthy | Q256 | BMC131INC03 |  | 2.1\0.4:20 | BR4-1860-E-00067 | 0 | [8 empty] | F4 | 41 | 42
BSR131 | DX01 | DIO1 | 131 | 2 | 1 | 0 | 4 | 21 |  |  | DI |  | 2 | BMC131INC03 | CB06 | GENERATOR INCOMER | Arc Flash Expansion Module 24VDC Supply | Healthy | Q258 | BMC131INC03 |  | 2.1\0.4:21 | BR4-1860-E-00067 | 0 | [8 empty] | F4 | 43 | 44
BSR131 | DX01 | DIO1 | 131 | 2 | 1 | 0 | 4 | 22 |  |  | DI |  | 2 | BMC131INC03 | CB07 | GENERATOR INCOMER | 110VDC/24VDC Power Supply | Healthy | Q215 | BMC131INC03 |  | 2.1\0.4:22 | BR4-1860-E-00067 | 0 | [8 empty] | F4 | 45 | 46
BSR131 | DX01 | DIO1 | 131 | 2 | 1 | 0 | 4 | 23 |  |  | DI | [10 empty] | 2.1\0.4:23 | [10 empty] | F4 | 47 | 48
BSR131 | DX01 | DIO1 | 131 | 2 | 1 | 0 | 4 | 24 |  |  | DI | [10 empty] | 2.1\0.4:24 | [10 empty] | F4 | 49 | 50
BSR131 | DX01 | DIO1 | 131 | 2 | 1 | 0 | 4 | 25 |  |  | DI | [10 empty] | 2.1\0.4:25 | [10 empty] | F4 | 51 | 52
BSR131 | DX01 | DIO1 | 131 | 2 | 1 | 0 | 4 | 26 |  |  | DI |  | 2 | BPQE2101PN01 | VDC01 | NPI & PRIMARY CRUSHING FIRE WATER PUMP CONTAINER PUMP CONTROL PANEL | 24VDC Control Supply | Healthy | Q155 | BPQE2101PN01 |  | 2.1\0.4:26 | BR4-1860-E-00051 | 0 | BPQE2101PN01-C1 2 PAIR (IC SPARE) | [7 empty] | F4 | 53 | 54
BSR131 | DX01 | DIO1 | 131 | 2 | 1 | 0 | 4 | 27 |  |  | DI |  | 2 | BPQE2101PN01 | CB01 | NPI & PRIMARY CRUSHING FIRE WATER PUMP CONTAINER PUMP CONTROL PANEL | Main Circuit Breaker | Closed | Q103 | BPQE2101PN01 |  | 2.1\0.4:27 | BR4-1860-E-00051 | 0 | [8 empty] | F4 | 55 | 56
BSR131 | DX01 | DIO1 | 131 | 2 | 1 | 0 | 4 | 28 |  |  | DI |  | 2 | BPQE2101PN01 | TRP01 | NPI & PRIMARY CRUSHING FIRE WATER PUMP CONTAINER PUMP CONTROL PANEL | Main Circuit Breaker | Tripped | Q103 | BPQE2101PN01 |  | 2.1\0.4:28 | BR4-1860-E-00051 | 0 | [8 empty] | F4 | 57 | 58
BSR131 | DX01 | DIO1 | 131 | 2 | 1 | 0 | 4 | 29 |  |  | DI |  | 2 | BPQE2101DB01 | VDC01 | NPI & PRIMARY CRUSHING FIRE WATER PUMP CONTAINER PUMP DB | 24VDC Control Supply | Healthy | Q155 | BPQE2101DB01 |  | 2.1\0.4:29 | BR4-1860-E-00109 | 0 | BPQE2101DB01-C1 2 PAIR (IC SPARE) | [7 empty] | F4 | 59 | 60
BSR131 | DX01 | DIO1 | 131 | 2 | 1 | 0 | 4 | 30 |  |  | DI |  | 2 | BPQE2101DB01 | CB01 | NPI & PRIMARY CRUSHING FIRE WATER PUMP CONTAINER PUMP DB | Main Circuit Breaker | Closed | Q103 | BPQE2101DB01 |  | 2.1\0.4:30 | BR4-1860-E-00109 | 0 | [8 empty] | F4 | 61 | 62
BSR131 | DX01 | DIO1 | 131 | 2 | 1 | 0 | 4 | 31 |  |  | DI |  | 2 | BPQE2101DB01 | TRP01 | NPI & PRIMARY CRUSHING FIRE WATER PUMP CONTAINER PUMP DB | Main Circuit Breaker | Tripped | Q103 | BPQE2101DB01 |  | 2.1\0.4:31 | BR4-1860-E-00109 | 0 | [8 empty] | F4 | 63 | 64
BSR131 | DX01 | DIO1 | 131 | 2 | 1 | 0 | 5 | 0 | BMXFCW303 | BMXDDI3202K | DI |  | 2 | BSR131BC01 | VDC01 | UTILITIES TRIPPING AND CLOSING SUPPLY BATTERY CHARGER | 24VDC Control Supply | Healthy | Q155 | BSR131BC01 |  | 2.1\0.5:0 | BR4-1860-E-00052 | 0 | BSR131BC01-C1 2 PAIR (IC SPARE) | [7 empty] | F5 | 1 | 2
BSR131 | DX01 | DIO1 | 131 | 2 | 1 | 0 | 5 | 1 |  |  | DI |  | 2 | BSR131BC01 | CB01 | UTILITIES TRIPPING AND CLOSING SUPPLY BATTERY CHARGER | Main Circuit Breaker | Closed | Q103 | BSR131BC01 |  | 2.1\0.5:1 | BR4-1860-E-00052 | 0 | [8 empty] | F5 | 3 | 4
BSR131 | DX01 | DIO1 | 131 | 2 | 1 | 0 | 5 | 2 |  |  | DI |  | 2 | BSR131BC01 | TRP01 | UTILITIES TRIPPING AND CLOSING SUPPLY BATTERY CHARGER | Main Circuit Breaker | Tripped | Q103 | BSR131BC01 |  | 2.1\0.5:2 | BR4-1860-E-00052 | 0 | [8 empty] | F5 | 5 | 6
BSR131 | DX01 | DIO1 | 131 | 2 | 1 | 0 | 5 | 3 |  |  | DI |  | 2 | BSR131BC02 | VDC01 | FIXED PLANT TRIPPING AND CLOSING SUPPLY BATTERY CHARGER | 24VDC Control Supply | Healthy | Q155 | BSR131BC02 |  | 2.1\0.5:3 | BR4-1860-E-00053 | 0 | BSR131BC02-C1 2 PAIR (IC SPARE) | [7 empty] | F5 | 7 | 8
BSR131 | DX01 | DIO1 | 131 | 2 | 1 | 0 | 5 | 4 |  |  | DI |  | 2 | BSR131BC02 | CB01 | FIXED PLANT TRIPPING AND CLOSING SUPPLY BATTERY CHARGER | Main Circuit Breaker | Closed | Q103 | BSR131BC02 |  | 2.1\0.5:4 | BR4-1860-E-00053 | 0 | [8 empty] | F5 | 9 | 10
BSR131 | DX01 | DIO1 | 131 | 2 | 1 | 0 | 5 | 5 |  |  | DI |  | 2 | BSR131BC02 | TRP01 | FIXED PLANT TRIPPING AND CLOSING SUPPLY BATTERY CHARGER | Main Circuit Breaker | Tripped | Q103 | BSR131BC02 |  | 2.1\0.5:5 | BR4-1860-E-00053 | 0 | [8 empty] | F5 | 11 | 12
BSR131 | DX01 | DIO1 | 131 | 2 | 1 | 0 | 5 | 6 |  |  | DI |  | 2 | BSR131UP01 | VDC01 | UNINTERRUPTIBLE POWER SUPPLY | 24VDC Control Supply | Healthy | Q155 | BSR131UP01 |  | 2.1\0.5:6 | BR4-1860-E-00056 | 0 | BSR131UP01-C1 2 PAIR (IC SPARE) | [7 empty] | F5 | 13 | 14
BSR131 | DX01 | DIO1 | 131 | 2 | 1 | 0 | 5 | 7 |  |  | DI |  | 2 | BSR131UP01 | CB01 | UNINTERRUPTIBLE POWER SUPPLY | Main Circuit Breaker | Closed | Q103 | BSR131UP01 |  | 2.1\0.5:7 | BR4-1860-E-00056 | 0 | [8 empty] | F5 | 15 | 16
BSR131 | DX01 | DIO1 | 131 | 2 | 1 | 0 | 5 | 8 |  |  | DI |  | 2 | BSR131UP01 | TRP01 | UNINTERRUPTIBLE POWER SUPPLY | Main Circuit Breaker | Tripped | Q103 | BSR131UP01 |  | 2.1\0.5:8 | BR4-1860-E-00056 | 0 | [8 empty] | F5 | 17 | 18
BSR131 | DX01 | DIO1 | 131 | 2 | 1 | 0 | 5 | 9 |  |  | DI |  | 2 | BSR131AC01 | VDC01 | AIR CONDITIONER UNIT NO.1 | 24VDC Control Supply | Healthy | Q155 | BSR131AC01 |  | 2.1\0.5:9 | BR4-1860-E-00054 | 0 | BSR131AC01-C1 2 PAIR (IC SPARE) | [7 empty] | F5 | 19 | 20
BSR131 | DX01 | DIO1 | 131 | 2 | 1 | 0 | 5 | 10 |  |  | DI |  | 2 | BSR131AC01 | CB01 | AIR CONDITIONER UNIT NO.1 | Main Circuit Breaker | Closed | Q103 | BSR131AC01 |  | 2.1\0.5:10 | BR4-1860-E-00054 | 0 | [8 empty] | F5 | 21 | 22
BSR131 | DX01 | DIO1 | 131 | 2 | 1 | 0 | 5 | 11 |  |  | DI |  | 2 | BSR131AC01 | TRP01 | AIR CONDITIONER UNIT NO.1 | Main Circuit Breaker | Tripped | Q103 | BSR131AC01 |  | 2.1\0.5:11 | BR4-1860-E-00054 | 0 | [8 empty] | F5 | 23 | 24
BSR131 | DX01 | DIO1 | 131 | 2 | 1 | 0 | 5 | 12 |  |  | DI |  | 2 | BSR131AC02 | VDC01 | AIR CONDITIONER UNIT NO.2 | 24VDC Control Supply | Healthy | Q155 | BSR131AC02 |  | 2.1\0.5:12 | BR4-1860-E-00055 | 0 | BSR131AC02-C1 2 PAIR (IC SPARE) | [7 empty] | F5 | 25 | 26
BSR131 | DX01 | DIO1 | 131 | 2 | 1 | 0 | 5 | 13 |  |  | DI |  | 2 | BSR131AC02 | CB01 | AIR CONDITIONER UNIT NO.2 | Main Circuit Breaker | Closed | Q103 | BSR131AC02 |  | 2.1\0.5:13 | BR4-1860-E-00055 | 0 | [8 empty] | F5 | 27 | 28
BSR131 | DX01 | DIO1 | 131 | 2 | 1 | 0 | 5 | 14 |  |  | DI |  | 2 | BSR131AC02 | TRP01 | AIR CONDITIONER UNIT NO.2 | Main Circuit Breaker | Tripped | Q103 | BSR131AC02 |  | 2.1\0.5:14 | BR4-1860-E-00055 | 0 | [8 empty] | F5 | 29 | 30
BSR131 | DX01 | DIO1 | 131 | 2 | 1 | 0 | 5 | 15 |  |  | DI |  | 2 | BSR131DB01 | VDC01 | SWITCHROOM 415V LIGHTING AND SMALL POWER DB | 24VDC Control Supply | Healthy | Q155 | BSR131DB01 |  | 2.1\0.5:15 | BR4-1860-E-00057 | 0 | BSR131DB01-C1 2 PAIR (IC SPARE) | [7 empty] | F5 | 31 | 32
BSR131 | DX01 | DIO1 | 131 | 2 | 1 | 0 | 5 | 16 |  |  | DI |  | 2 | BSR131DB01 | CB01 | SWITCHROOM 415V LIGHTING AND SMALL POWER DB | Main Circuit Breaker | Closed | Q103 | BSR131DB01 |  | 2.1\0.5:16 | BR4-1860-E-00057 | 0 | [8 empty] | F5 | 33 | 34
BSR131 | DX01 | DIO1 | 131 | 2 | 1 | 0 | 5 | 17 |  |  | DI |  | 2 | BSR131DB01 | TRP01 | SWITCHROOM 415V LIGHTING AND SMALL POWER DB | Main Circuit Breaker | Tripped | Q103 | BSR131DB01 |  | 2.1\0.5:17 | BR4-1860-E-00057 | 0 | [8 empty] | F5 | 35 | 36
BSR131 | DX01 | DIO1 | 131 | 2 | 1 | 0 | 5 | 18 |  |  | DI |  | 2 | BSR131DB02 | VDC01 | 415V WEST TURKEYS NEST AREA AND DEWATERING DB | 24VDC Control Supply | Healthy | Q155 | BSR131DB02 |  | 2.1\0.5:18 | BR4-1860-E-00058 | 0 | BSR131DB02-C1 2 PAIR (IC SPARE) | [7 empty] | F5 | 37 | 38
BSR131 | DX01 | DIO1 | 131 | 2 | 1 | 0 | 5 | 19 |  |  | DI |  | 2 | BSR131DB02 | CB01 | 415V WEST TURKEYS NEST AREA AND DEWATERING DB | Main Circuit Breaker | Closed | Q103 | BSR131DB02 |  | 2.1\0.5:19 | BR4-1860-E-00058 | 0 | [8 empty] | F5 | 39 | 40
BSR131 | DX01 | DIO1 | 131 | 2 | 1 | 0 | 5 | 20 |  |  | DI |  | 2 | BSR131DB02 | TRP01 | 415V WEST TURKEYS NEST AREA AND DEWATERING DB | Main Circuit Breaker | Tripped | Q103 | BSR131DB02 |  | 2.1\0.5:20 | BR4-1860-E-00058 | 0 | [8 empty] | F5 | 41 | 42
BSR131 | DX01 | DIO1 | 131 | 2 | 1 | 0 | 5 | 21 |  |  | DI |  | 2 | BSR131DB03 | VDC01 | 415V HME REFUEL AND WATER RECYCLE AREA DB | 24VDC Control Supply | Healthy | Q155 | BSR131DB03 |  | 2.1\0.5:21 | BR4-1860-E-00059 | 0 | BSR131DB03-C1 2 PAIR (IC SPARE) | [7 empty] | F5 | 43 | 44
BSR131 | DX01 | DIO1 | 131 | 2 | 1 | 0 | 5 | 22 |  |  | DI |  | 2 | BSR131DB03 | CB01 | 415V HME REFUEL AND WATER RECYCLE AREA DB | Main Circuit Breaker | Closed | Q103 | BSR131DB03 |  | 2.1\0.5:22 | BR4-1860-E-00059 | 0 | [8 empty] | F5 | 45 | 46
BSR131 | DX01 | DIO1 | 131 | 2 | 1 | 0 | 5 | 23 |  |  | DI |  | 2 | BSR131DB03 | TRP01 | 415V HME REFUEL AND WATER RECYCLE AREA DB | Main Circuit Breaker | Tripped | Q103 | BSR131DB03 |  | 2.1\0.5:23 | BR4-1860-E-00059 | 0 | [8 empty] | F5 | 47 | 48
BSR131 | DX01 | DIO1 | 131 | 2 | 1 | 0 | 5 | 24 |  |  | DI |  | 2 | BPQE2115MC01 | VDC01 | POTABLE WATER TREATMENT PLANT AND RECYCLE WATER MCC | 24VDC Control Supply (PWTP) | Healthy | Q155 | BPQE2115MC01 |  | 2.1\0.5:24 | BR4-1860-E-00060 | 0 | BPQE2115MC01-C1 2 PAIR (IC SPARE) | [7 empty] | F5 | 49 | 50
BSR131 | DX01 | DIO1 | 131 | 2 | 1 | 0 | 5 | 25 |  |  | DI |  | 2 | BPQE2115MC01 | CB01 | POTABLE WATER TREATMENT PLANT AND RECYCLE WATER MCC | Main Circuit Breaker (PWTP) | Closed | Q103 | BPQE2115MC01 |  | 2.1\0.5:25 | BR4-1860-E-00060 | 0 | [8 empty] | F5 | 51 | 52
BSR131 | DX01 | DIO1 | 131 | 2 | 1 | 0 | 5 | 26 |  |  | DI |  | 2 | BPQE2115MC01 | TRP01 | POTABLE WATER TREATMENT PLANT AND RECYCLE WATER MCC | Main Circuit Breaker (PWTP) | Tripped | Q103 | BPQE2115MC01 |  | 2.1\0.5:26 | BR4-1860-E-00060 | 0 | [8 empty] | F5 | 53 | 54
BSR131 | DX01 | DIO1 | 131 | 2 | 1 | 0 | 5 | 27 |  |  | DI |  | 2 | BMC1311 | VDC01 | HME REFUELLING MCC | 24VDC Control Supply | Healthy | Q155 | BMC1311 |  | 2.1\0.5:27 | BR4-1860-E-00061 | 0 | BMC1311-C1 2 PAIR (IC SPARE) | [7 empty] | F5 | 55 | 56
BSR131 | DX01 | DIO1 | 131 | 2 | 1 | 0 | 5 | 28 |  |  | DI |  | 2 | BMC1311 | CB01 | HME REFUELLING MCC | Main Circuit Breaker | Closed | Q103 | BMC1311 |  | 2.1\0.5:28 | BR4-1860-E-00061 | 0 | [8 empty] | F5 | 57 | 58
BSR131 | DX01 | DIO1 | 131 | 2 | 1 | 0 | 5 | 29 |  |  | DI |  | 2 | BMC1311 | TRP01 | HME REFUELLING MCC | Main Circuit Breaker | Tripped | Q103 | BMC1311 |  | 2.1\0.5:29 | BR4-1860-E-00061 | 0 | [8 empty] | F5 | 59 | 60
BSR131 | DX01 | DIO1 | 131 | 2 | 1 | 0 | 5 | 30 |  |  | DI | [10 empty] | 2.1\0.5:30 | [10 empty] | F5 | 61 | 62
BSR131 | DX01 | DIO1 | 131 | 2 | 1 | 0 | 5 | 31 |  |  | DI | [10 empty] | 2.1\0.5:31 | [10 empty] | F5 | 63 | 64
BSR131 | DX01 | DIO1 | 131 | 2 | 1 | 0 | 6 | 0 | BMXFCW303 | BMXDDI3202K | DI |  | 2 | BPP1101 | VDC01 | PRODUCTION PLANT & NPI WATER SUPPLY PUMP 1 (DUTY) | 24VDC Control Supply | Healthy | Q155 | BPP1101 |  | 2.1\0.6:0 | BR4-1860-E-00068 | 0 | BPP1101EM01-C1 2 PAIR (NO SPARE) | [7 empty] | F6 | 1 | 2
BSR131 | DX01 | DIO1 | 131 | 2 | 1 | 0 | 6 | 1 |  |  | DI |  | 2 | BPP1101 | SYS01 | PRODUCTION PLANT & NPI WATER SUPPLY PUMP 1 (DUTY) | Safety Relay | Healthy | K161 | BPP1101 |  | 2.1\0.6:1 | BR4-1860-E-00068 | 0 | [8 empty] | F6 | 3 | 4
BSR131 | DX01 | DIO1 | 131 | 2 | 1 | 0 | 6 | 2 |  |  | DI |  | 2 | BPP1101 | CB01 | PRODUCTION PLANT & NPI WATER SUPPLY PUMP 1 (DUTY) | Main Circuit Breaker | Closed | Q103 | BPP1101 |  | 2.1\0.6:2 | BR4-1860-E-00068 | 0 | [8 empty] | F6 | 5 | 6
BSR131 | DX01 | DIO1 | 131 | 2 | 1 | 0 | 6 | 3 |  |  | DI |  | 2 | BPP1101 | TRP01 | PRODUCTION PLANT & NPI WATER SUPPLY PUMP 1 (DUTY) | Main Circuit Breaker | Tripped | Q103 | BPP1101 |  | 2.1\0.6:3 | BR4-1860-E-00068 | 0 | [8 empty] | F6 | 7 | 8
BSR131 | DX01 | DIO1 | 131 | 2 | 1 | 0 | 6 | 4 |  |  | DI |  | 2 | BPP1102 | VDC01 | PRODUCTION PLANT & NPI WATER SUPPLY PUMP 2 (STANDBY) | 24VDC Control Supply | Healthy | Q155 | BPP1102 |  | 2.1\0.6:4 | BR4-1860-E-00069 | 0 | BPP1102EM01-C1 2 PAIR (NO SPARE) | [7 empty] | F6 | 9 | 10
BSR131 | DX01 | DIO1 | 131 | 2 | 1 | 0 | 6 | 5 |  |  | DI |  | 2 | BPP1102 | SYS01 | PRODUCTION PLANT & NPI WATER SUPPLY PUMP 2 (STANDBY) | Safety Relay | Healthy | K161 | BPP1102 |  | 2.1\0.6:5 | BR4-1860-E-00069 | 0 | [8 empty] | F6 | 11 | 12
BSR131 | DX01 | DIO1 | 131 | 2 | 1 | 0 | 6 | 6 |  |  | DI |  | 2 | BPP1102 | CB01 | PRODUCTION PLANT & NPI WATER SUPPLY PUMP 2 (STANDBY) | Main Circuit Breaker | Tripped | Q103 | BPP1102 |  | 2.1\0.6:6 | BR4-1860-E-00069 | 0 | [8 empty] | F6 | 13 | 14
BSR131 | DX01 | DIO1 | 131 | 2 | 1 | 0 | 6 | 7 |  |  | DI |  | 2 | BPP1102 | TRP01 | PRODUCTION PLANT & NPI WATER SUPPLY PUMP 2 (STANDBY) | Main Circuit Breaker | Healthy | Q103 | BPP1102 |  | 2.1\0.6:7 | BR4-1860-E-00069 | 0 | [8 empty] | F6 | 15 | 16
BSR131 | DX01 | DIO1 | 131 | 2 | 1 | 0 | 6 | 8 |  |  | DI |  | 2 | BPP1103 | VDC01 | WATER TRANSFER PUMP 1 (DUTY) | 24VDC Control Supply | Healthy | Q155 | BPP1103 |  | 2.1\0.6:8 | BR4-1860-E-00072 | 0 | BPP1103EM01-C1 2 PAIR (NO SPARE) | [7 empty] | F6 | 17 | 18
BSR131 | DX01 | DIO1 | 131 | 2 | 1 | 0 | 6 | 9 |  |  | DI |  | 2 | BPP1103 | SYS01 | WATER TRANSFER PUMP 1 (DUTY) | Safety Relay | Healthy | K161 | BPP1103 |  | 2.1\0.6:9 | BR4-1860-E-00072 | 0 | [8 empty] | F6 | 19 | 20
BSR131 | DX01 | DIO1 | 131 | 2 | 1 | 0 | 6 | 10 |  |  | DI |  | 2 | BPP1103 | CB01 | WATER TRANSFER PUMP 1 (DUTY) | Main Circuit Breaker | Closed | Q103 | BPP1103 |  | 2.1\0.6:10 | BR4-1860-E-00072 | 0 | [8 empty] | F6 | 21 | 22
BSR131 | DX01 | DIO1 | 131 | 2 | 1 | 0 | 6 | 11 |  |  | DI |  | 2 | BPP1103 | TRP01 | WATER TRANSFER PUMP 1 (DUTY) | Main Circuit Breaker | Tripped | Q103 | BPP1103 |  | 2.1\0.6:11 | BR4-1860-E-00072 | 0 | [8 empty] | F6 | 23 | 24
BSR131 | DX01 | DIO1 | 131 | 2 | 1 | 0 | 6 | 12 |  |  | DI |  | 2 | BPP1104 | VDC01 | WATER TRANSFER PUMP 2 (DUTY) | 24VDC Control Supply | Healthy | Q155 | BPP1104 |  | 2.1\0.6:12 | BR4-1860-E-00073 | 0 | BPP1104EM01-C1 2 PAIR (NO SPARE) | [7 empty] | F6 | 25 | 26
BSR131 | DX01 | DIO1 | 131 | 2 | 1 | 0 | 6 | 13 |  |  | DI |  | 2 | BPP1104 | SYS01 | WATER TRANSFER PUMP 2 (DUTY) | Safety Relay | Healthy | K161 | BPP1104 |  | 2.1\0.6:13 | BR4-1860-E-00073 | 0 | [8 empty] | F6 | 27 | 28
BSR131 | DX01 | DIO1 | 131 | 2 | 1 | 0 | 6 | 14 |  |  | DI |  | 2 | BPP1104 | CB01 | WATER TRANSFER PUMP 2 (DUTY) | Main Circuit Breaker | Tripped | Q103 | BPP1104 |  | 2.1\0.6:14 | BR4-1860-E-00073 | 0 | [8 empty] | F6 | 29 | 30
BSR131 | DX01 | DIO1 | 131 | 2 | 1 | 0 | 6 | 15 |  |  | DI |  | 2 | BPP1104 | TRP01 | WATER TRANSFER PUMP 2 (DUTY) | Main Circuit Breaker | Healthy | Q103 | BPP1104 |  | 2.1\0.6:15 | BR4-1860-E-00073 | 0 | [8 empty] | F6 | 31 | 32
BSR131 | DX01 | DIO1 | 131 | 2 | 1 | 0 | 6 | 16 |  |  | DI |  | 2 | BPP1105 | VDC01 | WATER TRANSFER PUMP 3 (STANDBY) | 24VDC Control Supply | Healthy | Q155 | BPP1105 |  | 2.1\0.6:16 | BR4-1860-E-00074 | 0 | BPP1105EM01-C1 2 PAIR (NO SPARE) | [7 empty] | F6 | 33 | 34
BSR131 | DX01 | DIO1 | 131 | 2 | 1 | 0 | 6 | 17 |  |  | DI |  | 2 | BPP1105 | SYS01 | WATER TRANSFER PUMP 3 (STANDBY) | Safety Relay | Healthy | K161 | BPP1105 |  | 2.1\0.6:17 | BR4-1860-E-00074 | 0 | [8 empty] | F6 | 35 | 36
BSR131 | DX01 | DIO1 | 131 | 2 | 1 | 0 | 6 | 18 |  |  | DI |  | 2 | BPP1105 | CB01 | WATER TRANSFER PUMP 3 (STANDBY) | Main Circuit Breaker | Closed | Q103 | BPP1105 |  | 2.1\0.6:18 | BR4-1860-E-00074 | 0 | [8 empty] | F6 | 37 | 38
BSR131 | DX01 | DIO1 | 131 | 2 | 1 | 0 | 6 | 19 |  |  | DI |  | 2 | BPP1105 | TRP01 | WATER TRANSFER PUMP 3 (STANDBY) | Main Circuit Breaker | Tripped | Q103 | BPP1105 |  | 2.1\0.6:19 | BR4-1860-E-00074 | 0 | [8 empty] | F6 | 39 | 40
BSR131 | DX01 | DIO1 | 131 | 2 | 1 | 0 | 6 | 20 |  |  | DI |  | 2 | BPP1106 | VDC01 | HME AND LME STANDPIPE PUMP 3 (DUTY) | 24VDC Control Supply | Healthy | Q155 | BPP1106 |  | 2.1\0.6:20 | BR4-1860-E-00070 | 0 | BPP1106EM01-C1 2 PAIR (NO SPARE) | [7 empty] | F6 | 41 | 42
BSR131 | DX01 | DIO1 | 131 | 2 | 1 | 0 | 6 | 21 |  |  | DI |  | 2 | BPP1106 | SYS01 | HME AND LME STANDPIPE PUMP 3 (DUTY) | Safety Relay | Healthy | K161 | BPP1106 |  | 2.1\0.6:21 | BR4-1860-E-00070 | 0 | [8 empty] | F6 | 43 | 44
BSR131 | DX01 | DIO1 | 131 | 2 | 1 | 0 | 6 | 22 |  |  | DI |  | 2 | BPP1106 | CB01 | HME AND LME STANDPIPE PUMP 3 (DUTY) | Main Circuit Breaker | Tripped | Q103 | BPP1106 |  | 2.1\0.6:22 | BR4-1860-E-00070 | 0 | [8 empty] | F6 | 45 | 46
BSR131 | DX01 | DIO1 | 131 | 2 | 1 | 0 | 6 | 23 |  |  | DI |  | 2 | BPP1106 | TRP01 | HME AND LME STANDPIPE PUMP 3 (DUTY) | Main Circuit Breaker | Healthy | Q103 | BPP1106 |  | 2.1\0.6:23 | BR4-1860-E-00070 | 0 | [8 empty] | F6 | 47 | 48
BSR131 | DX01 | DIO1 | 131 | 2 | 1 | 0 | 6 | 24 |  |  | DI |  | 2 | BPP1107 | VDC01 | HME AND LME STANDPIPE PUMP 4 (STANDBY) | 24VDC Control Supply | Healthy | Q155 | BPP1107 |  | 2.1\0.6:24 | BR4-1860-E-00071 | 0 | BPP1107EM01-C1 2 PAIR (NO SPARE) | [7 empty] | F6 | 49 | 50
BSR131 | DX01 | DIO1 | 131 | 2 | 1 | 0 | 6 | 25 |  |  | DI |  | 2 | BPP1107 | SYS01 | HME AND LME STANDPIPE PUMP 4 (STANDBY) | Safety Relay | Healthy | K161 | BPP1107 |  | 2.1\0.6:25 | BR4-1860-E-00071 | 0 | [8 empty] | F6 | 51 | 52
BSR131 | DX01 | DIO1 | 131 | 2 | 1 | 0 | 6 | 26 |  |  | DI |  | 2 | BPP1107 | CB01 | HME AND LME STANDPIPE PUMP 4 (STANDBY) | Main Circuit Breaker | Closed | Q103 | BPP1107 |  | 2.1\0.6:26 | BR4-1860-E-00071 | 0 | [8 empty] | F6 | 53 | 54
BSR131 | DX01 | DIO1 | 131 | 2 | 1 | 0 | 6 | 27 |  |  | DI |  | 2 | BPP1107 | TRP01 | HME AND LME STANDPIPE PUMP 4 (STANDBY) | Main Circuit Breaker | Tripped | Q103 | BPP1107 |  | 2.1\0.6:27 | BR4-1860-E-00071 | 0 | [8 empty] | F6 | 55 | 56
BSR131 | DX01 | DIO1 | 131 | 2 | 1 | 0 | 6 | 28 |  |  | DI |  | 4 | BSR131DB04 | VDC01 | 415V LAYDOWN AREA DB | 24VDC Control Supply | Healthy | Q155 | BSR131DB04 |  | 2.1\0.6:28 | BR4-1860-E-00106 | 0 | BSR131DB04-C1 2 PAIR (IC SPARE) | [7 empty] | F6 | 57 | 58
BSR131 | DX01 | DIO1 | 131 | 2 | 1 | 0 | 6 | 29 |  |  | DI |  | 4 | BSR131DB04 | CB01 | 415V LAYDOWN AREA DB | Main Circuit Breaker | Closed | Q103 | BSR131DB04 |  | 2.1\0.6:29 | BR4-1860-E-00106 | 0 | [8 empty] | F6 | 59 | 60
BSR131 | DX01 | DIO1 | 131 | 2 | 1 | 0 | 6 | 30 |  |  | DI |  | 4 | BSR131DB04 | TRP01 | 415V LAYDOWN AREA DB | Main Circuit Breaker | Tripped | Q103 | BSR131DB04 |  | 2.1\0.6:30 | BR4-1860-E-00106 | 0 | [8 empty] | F6 | 61 | 62
BSR131 | DX01 | DIO1 | 131 | 2 | 1 | 0 | 6 | 31 |  |  | DI | [10 empty] | 2.1\0.6:31 | [10 empty] | F6 | 63 | 64
BSR131 | DX01 | DIO1 | 131 | 2 | 1 | 0 | 7 | 0 | BMXFCW303 | BMXDDI3202K | DI |  | 2 | BPP1101VS01 | VDC01 |  | BPP1101VS01 Control Supply | Healthy | Q204 | BPP1101VS01 |  | 2.1\0.7:0 | BR4-1860-E-00093 | 0 | [8 empty] | F7 | 1 | 2
BSR131 | DX01 | DIO1 | 131 | 2 | 1 | 0 | 7 | 1 |  |  | DI |  | 2 | BPP1102VS01 | VDC01 |  | BPP1102VS01 Control Supply | Healthy | Q207 | BPP1102VS01 |  | 2.1\0.7:1 | BR4-1860-E-00093 | 0 | [8 empty] | F7 | 3 | 4
BSR131 | DX01 | DIO1 | 131 | 2 | 1 | 0 | 7 | 2 |  |  | DI |  | 2 | BPP1103VS01 | VDC01 |  | BPP1103VS01 Control Supply | Healthy | Q210 | BPP1103VS01 |  | 2.1\0.7:2 | BR4-1860-E-00093 | 0 | [8 empty] | F7 | 5 | 6
BSR131 | DX01 | DIO1 | 131 | 2 | 1 | 0 | 7 | 3 |  |  | DI |  | 2 | BPP1104VS01 | VDC01 |  | BPP1104VS01 Control Supply | Healthy | Q213 | BPP1104VS01 |  | 2.1\0.7:3 | BR4-1860-E-00093 | 0 | [8 empty] | F7 | 7 | 8
BSR131 | DX01 | DIO1 | 131 | 2 | 1 | 0 | 7 | 4 |  |  | DI |  | 2 | BPP1105VS01 | VDC01 |  | BPP1105VS01 Control Supply | Healthy | Q216 | BPP1105VS01 |  | 2.1\0.7:4 | BR4-1860-E-00093 | 0 | [8 empty] | F7 | 9 | 10
BSR131 | DX01 | DIO1 | 131 | 2 | 1 | 0 | 7 | 5 |  |  | DI |  | 2 | BPP1106VS01 | VDC01 |  | BPP1106VS01 Control Supply | Healthy | Q219 | BPP1106VS01 |  | 2.1\0.7:5 | BR4-1860-E-00093 | 0 | [8 empty] | F7 | 11 | 12
BSR131 | DX01 | DIO1 | 131 | 2 | 1 | 0 | 7 | 6 |  |  | DI |  | 2 | BPP1107VS01 | VDC01 |  | BPP1107VS01 Control Supply | Healthy | Q222 | BPP1107VS01 |  | 2.1\0.7:6 | BR4-1860-E-00093 | 0 |  |  | ` | [5 empty] | F7 | 13 | 14
BSR131 | DX01 | DIO1 | 131 | 2 | 1 | 0 | 7 | 7 |  |  | DI | [10 empty] | 2.1\0.7:7 | [10 empty] | F7 | 15 | 16
BSR131 | DX01 | DIO1 | 131 | 2 | 1 | 0 | 7 | 8 |  |  | DI | [10 empty] | 2.1\0.7:8 | [10 empty] | F7 | 17 | 18
BSR131 | DX01 | DIO1 | 131 | 2 | 1 | 0 | 7 | 9 |  |  | DI | [10 empty] | 2.1\0.7:9 | [10 empty] | F7 | 19 | 20
BSR131 | DX01 | DIO1 | 131 | 2 | 1 | 0 | 7 | 10 |  |  | DI | [10 empty] | 2.1\0.7:10 | [10 empty] | F7 | 21 | 22
BSR131 | DX01 | DIO1 | 131 | 2 | 1 | 0 | 7 | 11 |  |  | DI | [10 empty] | 2.1\0.7:11 | [10 empty] | F7 | 23 | 24
BSR131 | DX01 | DIO1 | 131 | 2 | 1 | 0 | 7 | 12 |  |  | DI | [10 empty] | 2.1\0.7:12 | [10 empty] | F7 | 25 | 26
BSR131 | DX01 | DIO1 | 131 | 2 | 1 | 0 | 7 | 13 |  |  | DI | [10 empty] | 2.1\0.7:13 | [10 empty] | F7 | 27 | 28
BSR131 | DX01 | DIO1 | 131 | 2 | 1 | 0 | 7 | 14 |  |  | DI | [10 empty] | 2.1\0.7:14 | [10 empty] | F7 | 29 | 30
BSR131 | DX01 | DIO1 | 131 | 2 | 1 | 0 | 7 | 15 |  |  | DI | [10 empty] | 2.1\0.7:15 | [10 empty] | F7 | 31 | 32
BSR131 | DX01 | DIO1 | 131 | 2 | 1 | 0 | 7 | 16 |  |  | DI | [10 empty] | 2.1\0.7:16 | [10 empty] | F7 | 33 | 34
BSR131 | DX01 | DIO1 | 131 | 2 | 1 | 0 | 7 | 17 |  |  | DI | [10 empty] | 2.1\0.7:17 | [10 empty] | F7 | 35 | 36
BSR131 | DX01 | DIO1 | 131 | 2 | 1 | 0 | 7 | 18 |  |  | DI | [10 empty] | 2.1\0.7:18 | [10 empty] | F7 | 37 | 38
BSR131 | DX01 | DIO1 | 131 | 2 | 1 | 0 | 7 | 19 |  |  | DI | [10 empty] | 2.1\0.7:19 | [10 empty] | F7 | 39 | 40
BSR131 | DX01 | DIO1 | 131 | 2 | 1 | 0 | 7 | 20 |  |  | DI | [10 empty] | 2.1\0.7:20 | [10 empty] | F7 | 41 | 42
BSR131 | DX01 | DIO1 | 131 | 2 | 1 | 0 | 7 | 21 |  |  | DI | [10 empty] | 2.1\0.7:21 | [10 empty] | F7 | 43 | 44
BSR131 | DX01 | DIO1 | 131 | 2 | 1 | 0 | 7 | 22 |  |  | DI | [10 empty] | 2.1\0.7:22 | [10 empty] | F7 | 45 | 46
BSR131 | DX01 | DIO1 | 131 | 2 | 1 | 0 | 7 | 23 |  |  | DI | [10 empty] | 2.1\0.7:23 | [10 empty] | F7 | 47 | 48
BSR131 | DX01 | DIO1 | 131 | 2 | 1 | 0 | 7 | 24 |  |  | DI | [10 empty] | 2.1\0.7:24 | [10 empty] | F7 | 49 | 50
BSR131 | DX01 | DIO1 | 131 | 2 | 1 | 0 | 7 | 25 |  |  | DI | [10 empty] | 2.1\0.7:25 | [10 empty] | F7 | 51 | 52
BSR131 | DX01 | DIO1 | 131 | 2 | 1 | 0 | 7 | 26 |  |  | DI | [10 empty] | 2.1\0.7:26 | [10 empty] | F7 | 53 | 54
BSR131 | DX01 | DIO1 | 131 | 2 | 1 | 0 | 7 | 27 |  |  | DI | [10 empty] | 2.1\0.7:27 | [10 empty] | F7 | 55 | 56
BSR131 | DX01 | DIO1 | 131 | 2 | 1 | 0 | 7 | 28 |  |  | DI | [10 empty] | 2.1\0.7:28 | [10 empty] | F7 | 57 | 58
BSR131 | DX01 | DIO1 | 131 | 2 | 1 | 0 | 7 | 29 |  |  | DI | [10 empty] | 2.1\0.7:29 | [10 empty] | F7 | 59 | 60
BSR131 | DX01 | DIO1 | 131 | 2 | 1 | 0 | 7 | 30 |  |  | DI | [10 empty] | 2.1\0.7:30 | [10 empty] | F7 | 61 | 62
BSR131 | DX01 | DIO1 | 131 | 2 | 1 | 0 | 7 | 31 |  |  | DI | [10 empty] | 2.1\0.7:31 | [10 empty] | F7 | 63 | 64
BSR131 | DX01 | DIO1 | 131 | 2 | 1 | 0 | 8 | 0 | BMXFTB2010 | BMXDDO1602 | DO |  | 2 | BSR131DB01 | SR01 | SWITCHROOM 415V LIGHTING AND SMALL POWER DB | Lightning Control Relay | Enabled |  | BSR131DB01 |  | 2.1\0.8:0 | BR4-1860-E-00078 | 0 | BSR131DB01-C1 1 PAIR (BK CR SPARE) | [7 empty] | F8 | 1 | 2
BSR131 | DX01 | DIO1 | 131 | 2 | 1 | 0 | 8 | 1 |  |  | DO |  | 4 | BSR131DB04 | SR01 | LAYDOWN AREA 415V LIGHTING AND SMALL POWER DB | Lightning Control Relay | Enabled |  | BSR131DB04 |  | 2.1\0.8:1 | BR4-1860-E-00084 | 0 | BSR131DB04-C1 1 PAIR (BK CR SPARE) | [7 empty] | F8 | 3 | 4
BSR131 | DX01 | DIO1 | 131 | 2 | 1 | 0 | 8 | 2 |  |  | DO | [10 empty] | 2.1\0.8:2 | [10 empty] | F8 | 5 | 6
BSR131 | DX01 | DIO1 | 131 | 2 | 1 | 0 | 8 | 3 |  |  | DO | [10 empty] | 2.1\0.8:3 | [10 empty] | F8 | 7 | 8
BSR131 | DX01 | DIO1 | 131 | 2 | 1 | 0 | 8 | 4 |  |  | DO | [10 empty] | 2.1\0.8:4 | [10 empty] | F8 | 9 | 10
BSR131 | DX01 | DIO1 | 131 | 2 | 1 | 0 | 8 | 5 |  |  | DO | [10 empty] | 2.1\0.8:5 | [10 empty] | F8 | 11 | 12
BSR131 | DX01 | DIO1 | 131 | 2 | 1 | 0 | 8 | 6 |  |  | DO | [10 empty] | 2.1\0.8:6 | [10 empty] | F8 | 13 | 14
BSR131 | DX01 | DIO1 | 131 | 2 | 1 | 0 | 8 | 7 |  |  | DO | [10 empty] | 2.1\0.8:7 | [10 empty] | F8 | 15 | 16
BSR131 | DX01 | DIO1 | 131 | 2 | 1 | 0 | 8 | 8 |  |  | DO | [10 empty] | 2.1\0.8:8 | [10 empty] | F8 | 17 | 18
BSR131 | DX01 | DIO1 | 131 | 2 | 1 | 0 | 8 | 9 |  |  | DO | [10 empty] | 2.1\0.8:9 | [10 empty] | F8 | 19 | 20
BSR131 | DX01 | DIO1 | 131 | 2 | 1 | 0 | 8 | 10 |  |  | DO | [10 empty] | 2.1\0.8:10 | [10 empty] | F8 | 21 | 22
BSR131 | DX01 | DIO1 | 131 | 2 | 1 | 0 | 8 | 11 |  |  | DO | [10 empty] | 2.1\0.8:11 | [10 empty] | F8 | 23 | 24
BSR131 | DX01 | DIO1 | 131 | 2 | 1 | 0 | 8 | 12 |  |  | DO | [10 empty] | 2.1\0.8:12 | [10 empty] | F8 | 25 | 26
BSR131 | DX01 | DIO1 | 131 | 2 | 1 | 0 | 8 | 13 |  |  | DO | [10 empty] | 2.1\0.8:13 | [10 empty] | F8 | 27 | 28
BSR131 | DX01 | DIO1 | 131 | 2 | 1 | 0 | 8 | 14 |  |  | DO | [10 empty] | 2.1\0.8:14 | [10 empty] | F8 | 29 | 30
BSR131 | DX01 | DIO1 | 131 | 2 | 1 | 0 | 8 | 15 |  |  | DO | [10 empty] | 2.1\0.8:15 | [10 empty] | F8 | 31 | 32
BSR131 | DX01 | DIO1 | 131 | 2 | 1 | 0 | 9 | 0 |  | BMXXEM010 | [11 empty] | 2.1\0.9:0
BSR131 | DX01 | DIO1 | 131 | 2 | 1 | 0 | 9 | 1 | [13 empty] | 2.1\0.9:1
BSR131 | DX01 | DIO1 | 131 | 2 | 1 | 0 | 9 | 2 | [13 empty] | 2.1\0.9:2
BSR131 | DX01 | DIO1 | 131 | 2 | 1 | 0 | 9 | 3 | [13 empty] | 2.1\0.9:3
BSR131 | DX01 | DIO1 | 131 | 2 | 1 | 0 | 10 | 0 |  | BMXXEM010 | [11 empty] | 2.1\0.10:0
BSR131 | DX01 | DIO1 | 131 | 2 | 1 | 0 | 10 | 1 | [13 empty] | 2.1\0.10:1
BSR131 | DX01 | DIO1 | 131 | 2 | 1 | 0 | 10 | 2 | [13 empty] | 2.1\0.10:2
BSR131 | DX01 | DIO1 | 131 | 2 | 1 | 0 | 10 | 3 | [13 empty] | 2.1\0.10:3
BSR131 | DX01 | DIO1 | 131 | 2 | 1 | 0 | 11 | 0 |  | BMXXEM010 | [11 empty] | 2.1\0.11:0
BSR131 | DX01 | DIO1 | 131 | 2 | 1 | 0 | 11 | 1 | [13 empty] | 2.1\0.11:1
BSR131 | DX01 | DIO1 | 131 | 2 | 1 | 0 | 11 | 2 | [13 empty] | 2.1\0.11:2
BSR131 | DX01 | DIO1 | 131 | 2 | 1 | 0 | 11 | 3 | [13 empty] | 2.1\0.11:3
[17 empty] | BPP1101 Field LOS To MCC Bucket |  | field link | [5 empty] | BTY1502DX02-C1 (10 PAIR) | [7 empty] | F12 | 1 | 2 | 3 | 4
[17 empty] | BPP1102 Field LOS To MCC Bucket |  | field link | [13 empty] | F12 | 5 | 6 | 7 | 8
[17 empty] | BPP1106 Field LOS To MCC Bucket |  | field link | [13 empty] | F12 | 9 | 10 | 11 | 12
[17 empty] | BPP1107 Field LOS To MCC Bucket |  | field link | [13 empty] | F12 | 13 | 14 | 15 | 16
[17 empty] | BPP1103 Field LOS To MCC Bucket |  | field link | [5 empty] | BTY1502DX03-C1 (10 PAIR) | [7 empty] | F12 | 17 | 18 | 19 | 20
[17 empty] | BPP1104 Field LOS To MCC Bucket |  | field link | [13 empty] | F12 | 21 | 22 | 23 | 24
[17 empty] | BPP1105 Field LOS To MCC Bucket |  | field link | [13 empty] | F12 | 25 | 26 | 27 | 28
[33 empty] | F12 | 29 | 30 | 31 | 32
[33 empty] | F12 | 33 | 34 | 35 | 36
[33 empty] | F12 | 37 | 38 | 39 | 40
[33 empty] | F12 | 41 | 42 | 43 | 44
[33 empty] | F12 | 45 | 46 | 47 | 48
[33 empty] | F12 | 49 | 50 | 51 | 52
[33 empty] | F12 | 53 | 54 | 55 | 56
[33 empty] | F12 | 57 | 58 | 59 | 60
[33 empty] | F12 | 61 | 62 | 63 | 64
|  | ACS880 |  |  |  |  | 1 | 1 | XDI:1 | ACS880 | DI
[7 empty] | 1 | 2 | XDI:2 |  | DI
[7 empty] | 1 | 3 | XDI:3 |  | DI |  | 2 |  | IS01 |  | Drive Isolator | Closed |  | BPP1101 |  |  | BR4-1860-E-00068 | 0
[7 empty] | 1 | 6 | XDI:6 |  | DI
[7 empty] | 1 |  | STO |  |  |  | 2 |  | VS01SY01 |  | STO Relay | Healthy |  | BPP1101
|  | ACS880 |  |  |  |  | 1 | 1 | XDI:1 | ACS880 | DI
[7 empty] | 1 | 2 | XDI:2 |  | DI
[7 empty] | 1 | 3 | XDI:3 |  | DI |  | 2 |  | IS01 |  | Drive Isolator | Closed |  | BPP1102 |  |  | BR4-1860-E-00069 | 0
[7 empty] | 1 | 6 | XDI:6 |  | DI
[7 empty] | 1 |  | STO |  |  |  | 2 |  | VS01SY01 |  | STO Relay | Healthy |  | BPP1102
|  | ACS880 |  |  |  |  | 1 | 1 | XDI:1 | ACS880 | DI
[7 empty] | 1 | 2 | XDI:2 |  | DI
[7 empty] | 1 | 3 | XDI:3 |  | DI |  | 2 |  | IS01 |  | Drive Isolator | Closed |  | BPP1103 |  |  | BR4-1860-E-00072 | 0
[7 empty] | 1 | 6 | XDI:6 |  | DI
[7 empty] | 1 |  | STO |  |  |  | 2 |  | VS01SY01 |  | STO Relay | Healthy |  | BPP1103
|  | ACS880 |  |  |  |  | 1 | 1 | XDI:1 | ACS880 | DI
[7 empty] | 1 | 2 | XDI:2 |  | DI
[7 empty] | 1 | 3 | XDI:3 |  | DI |  | 2 |  | IS01 |  | Drive Isolator | Closed |  | BPP1104 |  |  | BR4-1860-E-00073 | 0
[7 empty] | 1 | 6 | XDI:6 |  | DI
[7 empty] | 1 |  | STO |  |  |  | 2 |  | VS01SY01 |  | STO Relay | Healthy |  | BPP1104
|  | ACS880 |  |  |  |  | 1 | 1 | XDI:1 | ACS880 | DI
[7 empty] | 1 | 2 | XDI:2 |  | DI
[7 empty] | 1 | 3 | XDI:3 |  | DI |  | 2 |  | IS01 |  | Drive Isolator | Closed |  | BPP1105 |  |  | BR4-1860-E-00074 | 0
[7 empty] | 1 | 6 | XDI:6 |  | DI
[7 empty] | 1 |  | STO |  |  |  | 2 |  | VS01SY01 |  | STO Relay | Healthy |  | BPP1105
|  | ACS880 |  |  |  |  | 1 | 1 | XDI:1 | ACS880 | DI
[7 empty] | 1 | 2 | XDI:2 |  | DI
[7 empty] | 1 | 3 | XDI:3 |  | DI |  | 2 |  | IS01 |  | Drive Isolator | Closed |  | BPP1106 |  |  | BR4-1860-E-00070 | 0
[7 empty] | 1 | 6 | XDI:6 |  | DI
[7 empty] | 1 |  | STO |  |  |  | 2 |  | VS01SY01 |  | STO Relay | Healthy |  | BPP1106
|  | ACS880 |  |  |  |  | 1 | 1 | XDI:1 | ACS880 | DI
[7 empty] | 1 | 2 | XDI:2 |  | DI
[7 empty] | 1 | 3 | XDI:3 |  | DI |  | 2 |  | IS01 |  | Drive Isolator | Closed |  | BPP1107 |  |  | BR4-1860-E-00071 | 0
[7 empty] | 1 | 6 | XDI:6 |  | DI
[7 empty] | 1 |  | STO |  |  |  | 2 |  | VS01SY01 |  | STO Relay | Healthy |  | BPP1107
|  | PR |  |  |  |  | 1 |  |  | MASTERPACT_VAMP |  |  | 2 | [6 empty] | BMC131INC01 |  |  | BR4-1860-E-00062 | 0 | Process Bus A Incomer
|  | PR |  |  |  |  | 1 |  | VAMP RJ45 | DX01ES01 |  |  | 2
|  | PR |  |  |  |  | 1 |  | CUB RJ45 | DX01ES01 |  |  | 2
|  | PR |  |  |  |  | 1 |  |  | MASTERPACT |  |  | 2 | [6 empty] | BMC131INC02 |  |  | BR4-1860-E-00064 | 0 | Essential Bus Incomer
|  | PR |  |  |  |  | 1 | [5 empty] | 2
|  | PR |  |  |  |  | 1 |  | CUB RJ45 | DX01ES01 |  |  | 2
|  | PR |  |  |  |  | 1 |  |  | MASTERPACT |  |  | 2 | [6 empty] | BMC131INC03 |  |  | BR4-1860-E-00066 | 0 | Generator Incomer
|  | PR |  |  |  |  | 1 | [5 empty] | 2
|  | PR |  |  |  |  | 1 |  | CUB RJ45 | DX01ES01 |  |  | 2

## Field IO Assignment
Item | Box | Node | PLC | Bus | Drop | Rack | Slot | Ch | Terminal | Node Type | IO Type | Rev | Instrument Tag | Device | Instrument List Description | Desc2 | State | Location | Drive | Datatype | Address | Drawing | Rev | Notes | FAT | SAT | Raw_Zero | Raw_Full | Eng_Zero | Eng_Full | Format | T S | T1 | T2 | T3 | T4 | Alm_AREA | Alm_PRIV | Alm_HELP | Alm_CATEGORY | Alm_CUSTOM1 | Alm_CUSTOM2 | Alm_CUSTOM3 | Alm_CUSTOM4 | Alm_CUSTOM5 | Alm_CUSTOM6 | Alm_CUSTOM7 | Alm_CUSTOM8
BTY1502DX02 - West Turkeys Nest
EIO node #2 | DX02 | DIO1 | 131 | 2 | 2 | 0
BTY1502 | DX02 | DIO1 | 131 | 2 | 2 | 0 |  | Chassis |  | BMEXBP1200
BTY1502 | DX02 | DIO1 | 131 | 2 | 2 | 0 |  | Power |  | BMXCPS4022 |  | total |  | spare |  | % spare
BTY1502 | DX02 | DIO1 | 131 | 2 | 2 | 0 | 0 | Comms |  | BMECRA31210 | I/O1 | 140 |  | 69 |  | 49.29%
BTY1502 | DX02 | DIO1 | 131 | 2 | 2 | 0 | 1 | 0 | BMXFCW303 | BMXDDI3202K | DI | 2 | BTY1502DX02 | CB01 | 24VDC BPP1106 Field Supply | 240VAC BTY1502AX01 Control Supply Circuit Breaker | Closed | Q106 | BTY1502DX02 |  | 2.2\0.1:0 | BR4-1860-E-00097 | 0 |  | D | [6 empty] | F1 |  | 1
BTY1502 | DX02 | DIO1 | 131 | 2 | 2 | 0 | 1 | 1 |  |  | DI | 2 | BTY1502DX02 | VDC01 | 24VDC BPP1107 Field Supply | 24VDC Output Control Supply | Healthy | Q143 | BTY1502DX02 |  | 2.2\0.1:1 | BR4-1860-E-00097 | 0 |  | D | [6 empty] | F1 |  | 2
BTY1502 | DX02 | DIO1 | 131 | 2 | 2 | 0 | 1 | 2 |  |  | DI | 2 | BTY1502DX02 | VDC02 | 24VDC BPP1101 Field Supply | 24VDC GW1 Control Supply | Healthy | Q157 | BTY1502DX02 |  | 2.2\0.1:2 | BR4-1860-E-00097 | 0 |  | D | [6 empty] | F1 |  | 3
BTY1502 | DX02 | DIO1 | 131 | 2 | 2 | 0 | 1 | 3 |  |  | DI | 2 | BTY1502DX02 | VDC03 | 24VDC BPP1102 Field Supply | 24VDC Instrument Control Supply | Healthy | Q164 | BTY1502DX02 |  | 2.2\0.1:3 | BR4-1860-E-00097 | 0 |  | D | [6 empty] | F1 |  | 4
BTY1502 | DX02 | DIO1 | 131 | 2 | 2 | 0 | 1 | 4 |  |  | DI | 2 | BTY1502DX02 | VDC04 | 24VDC BSTD1106 Field Supply | 24VDC Transmitter Control Supply | Healthy | Q168 | BTY1502DX02 |  | 2.2\0.1:4 | BR4-1860-E-00097 | 0 |  | D | [6 empty] | F1 |  | 5
BTY1502 | DX02 | DIO1 | 131 | 2 | 2 | 0 | 1 | 5 |  |  | DI | 2 | BTY1502DX02 | VDC05 | 24VDC BSTD1107 Field Supply | 24VDC Process Water Control Supply | Healthy | Q172 | BTY1502DX02 |  | 2.2\0.1:5 | BR4-1860-E-00097 | 0 |  | D | [6 empty] | F1 |  | 6
BTY1502 | DX02 | DIO1 | 131 | 2 | 2 | 0 | 1 | 6 |  |  | DI | 2 | BTY1502DX02 | VDC06 |  | 24VDC BPP1101 Control Supply | Healthy | Q176 | BTY1502DX02 |  | 2.2\0.1:6 | BR4-1860-E-00097 | 0 |  | D | [6 empty] | F1 |  | 7
BTY1502 | DX02 | DIO1 | 131 | 2 | 2 | 0 | 1 | 7 |  |  | DI | 2 | BTY1502DX02 | VDC07 |  | 24VDC BPP1102 Control Supply | Healthy | Q180 | BTY1502DX02 |  | 2.2\0.1:7 | BR4-1860-E-00097 | 0 |  | D | [6 empty] | F1 |  | 8
BTY1502 | DX02 | DIO1 | 131 | 2 | 2 | 0 | 1 | 8 |  |  | DI | 2 | BTY1502DX02 | VDC08 |  | 24VDC BPP1106 Control Supply | Healthy | Q184 | BTY1502DX02 |  | 2.2\0.1:8 | BR4-1860-E-00097 | 0 |  | D | [6 empty] | F1 |  | 9
BTY1502 | DX02 | DIO1 | 131 | 2 | 2 | 0 | 1 | 9 |  |  | DI | 2 | BTY1502DX02 | VDC09 |  | 24VDC BPP1107 Control Supply | Healthy | Q188 | BTY1502DX02 |  | 2.2\0.1:9 | BR4-1860-E-00097 | 0 |  | D | [6 empty] | F1 |  | 10
BTY1502 | DX02 | DIO1 | 131 | 2 | 2 | 0 | 1 | 10 |  |  | DI | 2 | BTY1502DX02 | VDC10 |  | 24VDC BSTD1106 Control Supply | Healthy | Q192 | BTY1502DX02 |  | 2.2\0.1:10 | BR4-1860-E-00097 | 0 |  | D | [6 empty] | F1 |  | 11
BTY1502 | DX02 | DIO1 | 131 | 2 | 2 | 0 | 1 | 11 |  |  | DI | 2 | BTY1502DX02 | VDC11 |  | 24VDC BSTD1107 Control Supply | Healthy | Q196 | BTY1502DX02 |  | 2.2\0.1:11 | BR4-1860-E-00097 | 0 |  | D | [6 empty] | F1 |  | 12
BTY1502 | DX02 | DIO1 | 131 | 2 | 2 | 0 | 1 | 12 |  |  | DI | [9 empty] | 2.2\0.1:12 |  |  |  | S | [6 empty] | F1 |  | 13
BTY1502 | DX02 | DIO1 | 131 | 2 | 2 | 0 | 1 | 13 |  |  | DI | [9 empty] | 2.2\0.1:13 |  |  |  | S | [6 empty] | F1 |  | 14
BTY1502 | DX02 | DIO1 | 131 | 2 | 2 | 0 | 1 | 14 |  |  | DI | [9 empty] | 2.2\0.1:14 |  |  |  | S | [6 empty] | F1 |  | 15
BTY1502 | DX02 | DIO1 | 131 | 2 | 2 | 0 | 1 | 15 |  |  | DI | [9 empty] | 2.2\0.1:15 |  |  |  | S | [6 empty] | F1 |  | 16
BTY1502 | DX02 | DIO1 | 131 | 2 | 2 | 0 | 1 | 16 |  |  | DI | 2 | BPP1101LCS01 | STT01 | PRODUCTION PLANT & NPI WATER SUPPLY PUMP 1 (DUTY) | Start Pushbutton | Activated |  | BPP1101 |  | 2.2\0.1:16 | BR4-1860-E-00068 | 0 |  | S | [6 empty] | F1 | 17 | 18
BTY1502 | DX02 | DIO1 | 131 | 2 | 2 | 0 | 1 | 17 |  |  | DI | 2 | BPP1101LCS01 | STP01 | PRODUCTION PLANT & NPI WATER SUPPLY PUMP 1 (DUTY) | Stop Pushbutton | Activated |  | BPP1101 |  | 2.2\0.1:17 | BR4-1860-E-00068 | 0 |  | S | [6 empty] | F1 | 19 | 20
BTY1502 | DX02 | DIO1 | 131 | 2 | 2 | 0 | 1 | 18 |  |  | DI | 2 | BPP1102LCS02 | STT01 | PRODUCTION PLANT & NPI WATER SUPPLY PUMP 2 (STANDBY) | Start Pushbutton | Activated |  | BPP1102 |  | 2.2\0.1:18 | BR4-1860-E-00069 | 0 |  | S | [6 empty] | F1 | 21 | 22
BTY1502 | DX02 | DIO1 | 131 | 2 | 2 | 0 | 1 | 19 |  |  | DI | 2 | BPP1102LCS02 | STP01 | PRODUCTION PLANT & NPI WATER SUPPLY PUMP 2 (STANDBY) | Stop Pushbutton | Activated |  | BPP1102 |  | 2.2\0.1:19 | BR4-1860-E-00069 | 0 |  | S | [6 empty] | F1 | 23 | 24
BTY1502 | DX02 | DIO1 | 131 | 2 | 2 | 0 | 1 | 20 |  |  | DI | 2 | BPP1106LCS06 | STT01 | HME AND LME STANDPIPE PUMP 3 (DUTY) | Start Pushbutton | Activated |  | BPP1106 |  | 2.2\0.1:20 | BR4-1860-E-00070 | 0 |  | S | [6 empty] | F1 | 25 | 26
BTY1502 | DX02 | DIO1 | 131 | 2 | 2 | 0 | 1 | 21 |  |  | DI | 2 | BPP1106LCS06 | STP01 | HME AND LME STANDPIPE PUMP 3 (DUTY) | Stop Pushbutton | Activated |  | BPP1106 |  | 2.2\0.1:21 | BR4-1860-E-00070 | 0 |  | S | [6 empty] | F1 | 27 | 28
BTY1502 | DX02 | DIO1 | 131 | 2 | 2 | 0 | 1 | 22 |  |  | DI | 2 | BPP1107LCS07 | STT01 | HME AND LME STANDPIPE PUMP 4 (STANDBY) | Start Pushbutton | Activated |  | BPP1107 |  | 2.2\0.1:22 | BR4-1860-E-00071 | 0 |  | S | [6 empty] | F1 | 29 | 30
BTY1502 | DX02 | DIO1 | 131 | 2 | 2 | 0 | 1 | 23 |  |  | DI | 2 | BPP1107LCS07 | STP01 | HME AND LME STANDPIPE PUMP 4 (STANDBY) | Stop Pushbutton | Activated |  | BPP1107 |  | 2.2\0.1:23 | BR4-1860-E-00071 | 0 |  | S | [6 empty] | F1 | 31 | 32
BTY1502 | DX02 | DIO1 | 131 | 2 | 2 | 0 | 1 | 24 |  |  | DI | 2 | BSTD1106LCS01 | STT01 | LME STANDPIPE | Start Pushbutton | Activated |  | BSTD1106 |  | 2.2\0.1:24 | BR4-1860-E-00101 | 0 |  | S | [6 empty] | F1 | 33 | 34
BTY1502 | DX02 | DIO1 | 131 | 2 | 2 | 0 | 1 | 25 |  |  | DI | 2 | BSTD1106LCS01 | STP01 | LME STANDPIPE | Stop Pushbutton | Activated |  | BSTD1106 |  | 2.2\0.1:25 | BR4-1860-E-00101 | 0 |  | S | [6 empty] | F1 | 35 | 36
BTY1502 | DX02 | DIO1 | 131 | 2 | 2 | 0 | 1 | 26 |  |  | DI | 2 | BSTD1106LCS01 | STT02 | LME STANDPIPE | Elsema Start Button | Healthy |  | BSTD1106 |  | 2.2\0.1:26 | BR4-1860-E-00101 | 0 |  | S | [6 empty] | F1 | 37 | 38
BTY1502 | DX02 | DIO1 | 131 | 2 | 2 | 0 | 1 | 27 |  |  | DI | 2 | BSTD1107LCS01 | STT01 | HME STANDPIPE | Start Pushbutton | Activated |  | BSTD1107 |  | 2.2\0.1:27 | BR4-1860-E-00101 | 0 |  | S | [6 empty] | F1 | 39 | 40
BTY1502 | DX02 | DIO1 | 131 | 2 | 2 | 0 | 1 | 28 |  |  | DI | 2 | BSTD1107LCS01 | STP01 | HME STANDPIPE | Stop Pushbutton | Activated |  | BSTD1107 |  | 2.2\0.1:28 | BR4-1860-E-00101 | 0 |  | S | [6 empty] | F1 | 41 | 42
BTY1502 | DX02 | DIO1 | 131 | 2 | 2 | 0 | 1 | 29 |  |  | DI | 2 | BSTD1107LCS01 | STT02 | HME STANDPIPE | Elsema Start Button | Healthy |  | BSTD1107 |  | 2.2\0.1:29 | BR4-1860-E-00101 | 0 |  | S | [6 empty] | F1 | 43 | 44
BTY1502 | DX02 | DIO1 | 131 | 2 | 2 | 0 | 1 | 30 |  |  | DI | [9 empty] | 2.2\0.1:30 |  |  |  | S | [6 empty] | F1 | 45 | 46
BTY1502 | DX02 | DIO1 | 131 | 2 | 2 | 0 | 1 | 31 |  |  | DI | [9 empty] | 2.2\0.1:31 |  |  |  | S | [6 empty] | F1 | 47 | 48
BTY1502 | DX02 | DIO1 | 131 | 2 | 2 | 0 | 2 | 0 | BMXFCW303 | BMXDDI3202K | DI | 2 | BPP1106 | THR01 | HME AND LME STANDPIPE PUMP 3 (DUTY) | HME And LME Standpipe Pump 3 (Duty) | Healthy | K190 | BPP1106 |  | 2.2\0.2:0 | BR4-1860-E-00070 | 0 |  | S | [6 empty] | F2 | 1 | 2
BTY1502 | DX02 | DIO1 | 131 | 2 | 2 | 0 | 2 | 1 |  |  | DI | 2 | BPP1107 | THR01 | HME AND LME STANDPIPE PUMP 4 (STANDBY) | HME And LME Standpipe Pump 4 (Standby) | Healthy | K190 | BPP1107 |  | 2.2\0.2:1 | BR4-1860-E-00071 | 0 |  | S | [6 empty] | F2 | 3 | 4
BTY1502 | DX02 | DIO1 | 131 | 2 | 2 | 0 | 2 | 2 |  |  | DI | 2 | BPP1101 | THR01 | PRODUCTION PLANT & NPI WATER SUPPLY PUMP 1 (DUTY) | Production Plant & NPI Water Supply Pump 1 (Duty) | Healthy | K190 | BPP1101 |  | 2.2\0.2:2 | BR4-1860-E-00068 | 0 |  | S | [6 empty] | F2 | 5 | 6
BTY1502 | DX02 | DIO1 | 131 | 2 | 2 | 0 | 2 | 3 |  |  | DI | 2 | BPP1102 | THR01 | PRODUCTION PLANT & NPI WATER SUPPLY PUMP 2 (STANDBY) | Production Plant & NPI Water Supply Pump 2 (Standby) | Healthy | K190 | BPP1102 |  | 2.2\0.2:3 | BR4-1860-E-00069 | 0 |  | S | [6 empty] | F2 | 7 | 8
BTY1502 | DX02 | DIO1 | 131 | 2 | 2 | 0 | 2 | 4 |  |  | DI | 2 | BPP1106FS07 | FS07 | HME AND LME STANDPIPE PUMP 3 | HME And LME Standpipe Pump 3 Flow | Low |  | BPP1106 |  | 2.2\0.2:4 | BR4-1860-E-00102 | 0 |  | S | [6 empty] | F2 | 9 | 10
BTY1502 | DX02 | DIO1 | 131 | 2 | 2 | 0 | 2 | 5 |  |  | DI | 2 | BPP1107FS08 | FS08 | HME AND LME STANDPIPE PUMP 4 | HME And LME Standpipe Pump 4 Flow | Low |  | BPP1107 |  | 2.2\0.2:5 | BR4-1860-E-00102 | 0 |  | S | [6 empty] | F2 | 11 | 12
BTY1502 | DX02 | DIO1 | 131 | 2 | 2 | 0 | 2 | 6 |  |  | DI | 2 | BSTD1106FIT03 | FQ03 | LME STANDPIPE | LME Standpipe | Pulse |  | BSTD1106 |  | 2.2\0.2:6 | BR4-1860-E-00100 | 0 |  | S | [6 empty] | F2 | 13 | 14
BTY1502 | DX02 | DIO1 | 131 | 2 | 2 | 0 | 2 | 7 |  |  | DI | 2 | BSTD1107FIT02 | FQ02 | HME STANDPIPE | HME Standpipe | Pulse |  | BSTD1107 |  | 2.2\0.2:7 | BR4-1860-E-00100 | 0 |  | S | [6 empty] | F2 | 15 | 16
BTY1502 | DX02 | DIO1 | 131 | 2 | 2 | 0 | 2 | 8 |  |  | DI | [9 empty] | 2.2\0.2:8 |  |  |  | S | [6 empty] | F2 | 17 | 18
BTY1502 | DX02 | DIO1 | 131 | 2 | 2 | 0 | 2 | 9 |  |  | DI | 2 | BTY1502FIT01 | FQ01 | RAW WATER FROM EAST PIT | Raw Water From East Pit | Pulse |  | BTY1502 |  | 2.2\0.2:9 | BR4-1860-E-00098 | 0 |  | S | [6 empty] | F2 | 19 | 20
BTY1502 | DX02 | DIO1 | 131 | 2 | 2 | 0 | 2 | 10 |  |  | DI | 2 | BTY1502FIT03 | FQ03 | RAW WATER FROM WEST PIT | Raw Water From West Pit | Pulse |  | BTY1502 |  | 2.2\0.2:10 | BR4-1860-E-00098 | 0 |  | S | [6 empty] | F2 | 21 | 22
BTY1502 | DX02 | DIO1 | 131 | 2 | 2 | 0 | 2 | 11 |  |  | DI | 2 | BTY1502LS01 | LS01 | WEST TURKEYS NEST | West Turkeys Nest | Healthy |  | BTY1502 |  | 2.2\0.2:11 | BR4-1860-E-00099 | 0 |  | S | [6 empty] | F2 | 23 | 24
BTY1502 | DX02 | DIO1 | 131 | 2 | 2 | 0 | 2 | 12 |  |  | DI | [9 empty] | 2.2\0.2:12 |  |  |  | S | [6 empty] | F2 | 25 | 26
BTY1502 | DX02 | DIO1 | 131 | 2 | 2 | 0 | 2 | 13 |  |  | DI | 2 | BPP1101FS09 | FS09 | PRODUCTION PLANT & NPI WATER SUPPLY PUMP 1 (DUTY) | Production Plant & NPI Water Supply Pump 1 (Duty) Flow | Low |  | BPP1101 |  | 2.2\0.2:13 | BR4-1860-E-00102 | 0 |  | S | [6 empty] | F2 | 27 | 28
BTY1502 | DX02 | DIO1 | 131 | 2 | 2 | 0 | 2 | 14 |  |  | DI | 2 | BPP1102FS10 | FS10 | PRODUCTION PLANT & NPI WATER SUPPLY PUMP 2 (STANDBY) | Production Plant & NPI Water Supply Pump 2 (Standby) Flow | Low |  | BPP1102 |  | 2.2\0.2:14 | BR4-1860-E-00102 | 0 |  | S | [6 empty] | F2 | 29 | 30
BTY1502 | DX02 | DIO1 | 131 | 2 | 2 | 0 | 2 | 15 |  |  | DI | 2 | BPP1101FIT03 | FQ03 | PRODUCTION PLANT & NPI WATER SUPPLY | Production Plant & NPI Water Supply | Pulse |  | BPP1101 |  | 2.2\0.2:15 | BR4-1860-E-00098 | 0 |  | S | [6 empty] | F2 | 31 | 32
BTY1502 | DX02 | DIO1 | 131 | 2 | 2 | 0 | 2 | 16 |  |  | DI | 2 | BTY1502FIT02 | FQ02 | WEST TURKEYS NEST | West Turkeys Nest | Pulse |  | BTY1502 |  | 2.2\0.2:16 | BR4-1860-E-00098 | 0 |  | S | [6 empty] | F3 | 1 | 2
BTY1502 | DX02 | DIO1 | 131 | 2 | 2 | 0 | 2 | 17 |  |  | DI | [9 empty] | 2.2\0.2:17 |  |  |  | S | [6 empty] | F3 | 3 | 4
BTY1502 | DX02 | DIO1 | 131 | 2 | 2 | 0 | 2 | 18 |  |  | DI | [9 empty] | 2.2\0.2:18 |  |  |  | S | [6 empty] | F3 | 5 | 6
BTY1502 | DX02 | DIO1 | 131 | 2 | 2 | 0 | 2 | 19 |  |  | DI | [9 empty] | 2.2\0.2:19 |  |  |  | S | [6 empty] | F3 | 7 | 8
BTY1502 | DX02 | DIO1 | 131 | 2 | 2 | 0 | 2 | 20 |  |  | DI | [9 empty] | 2.2\0.2:20 |  |  |  | S | [6 empty] | F3 | 9 | 10
BTY1502 | DX02 | DIO1 | 131 | 2 | 2 | 0 | 2 | 21 |  |  | DI | [9 empty] | 2.2\0.2:21 |  |  |  | S | [6 empty] | F3 | 11 | 12
BTY1502 | DX02 | DIO1 | 131 | 2 | 2 | 0 | 2 | 22 |  |  | DI | [9 empty] | 2.2\0.2:22 |  |  |  | S | [6 empty] | F3 | 13 | 14
BTY1502 | DX02 | DIO1 | 131 | 2 | 2 | 0 | 2 | 23 |  |  | DI | [9 empty] | 2.2\0.2:23 |  |  |  | S | [6 empty] | F3 | 15 | 16
BTY1502 | DX02 | DIO1 | 131 | 2 | 2 | 0 | 2 | 24 |  |  | DI | [9 empty] | 2.2\0.2:24 |  |  |  | S | [6 empty] | F3 | 17 | 18
BTY1502 | DX02 | DIO1 | 131 | 2 | 2 | 0 | 2 | 25 |  |  | DI | [9 empty] | 2.2\0.2:25 |  |  |  | S | [6 empty] | F3 | 19 | 20
BTY1502 | DX02 | DIO1 | 131 | 2 | 2 | 0 | 2 | 26 |  |  | DI | [9 empty] | 2.2\0.2:26 |  |  |  | S | [6 empty] | F3 | 21 | 22
BTY1502 | DX02 | DIO1 | 131 | 2 | 2 | 0 | 2 | 27 |  |  | DI | [9 empty] | 2.2\0.2:27 |  |  |  | S | [6 empty] | F3 | 23 | 24
BTY1502 | DX02 | DIO1 | 131 | 2 | 2 | 0 | 2 | 28 |  |  | DI | [9 empty] | 2.2\0.2:28 |  |  |  | S | [6 empty] | F3 | 25 | 26
BTY1502 | DX02 | DIO1 | 131 | 2 | 2 | 0 | 2 | 29 |  |  | DI | [9 empty] | 2.2\0.2:29 |  |  |  | S | [6 empty] | F3 | 27 | 28
BTY1502 | DX02 | DIO1 | 131 | 2 | 2 | 0 | 2 | 30 |  |  | DI | [9 empty] | 2.2\0.2:30 |  |  |  | S | [6 empty] | F3 | 29 | 30
BTY1502 | DX02 | DIO1 | 131 | 2 | 2 | 0 | 2 | 31 |  |  | DI | [9 empty] | 2.2\0.2:31 |  |  |  | S | [6 empty] | F3 | 31 | 32
BTY1502 | DX02 | DIO1 | 131 | 2 | 2 | 0 | 3 | 0 | BMXFCW303 | BMXDDI3202K | DI | 2 | BSTD1106FV03 | ZS01 | LME STANDPIPE | Flow Valve | Open |  | BSTD1106FV03 |  | 2.2\0.3:0 | BR4-1860-E-00099 | 0 |  | S | [6 empty] | F4 | 1 | 2
BTY1502 | DX02 | DIO1 | 131 | 2 | 2 | 0 | 3 | 1 |  |  | DI | 2 | BSTD1106FV03 | ZS02 | LME STANDPIPE | Flow Valve | Closed |  | BSTD1106FV03 |  | 2.2\0.3:1 | BR4-1860-E-00099 | 0 |  | S | [6 empty] | F4 | 3 | 4
BTY1502 | DX02 | DIO1 | 131 | 2 | 2 | 0 | 3 | 2 |  |  | DI | 2 | BSTD1106FV03 | SW01 | LME STANDPIPE | Flow Valve Local Mode | Selected |  | BSTD1106FV03 |  | 2.2\0.3:2 | BR4-1860-E-00099 | 0 |  | S | [6 empty] | F4 | 5 | 6
BTY1502 | DX02 | DIO1 | 131 | 2 | 2 | 0 | 3 | 3 |  |  | DI | 2 | BSTD1106FV03 | XS01 | LME STANDPIPE | Flow Valve | Fault |  | BSTD1106FV03 |  | 2.2\0.3:3 | BR4-1860-E-00099 | 0 |  | S | [6 empty] | F4 | 7 | 8
BTY1502 | DX02 | DIO1 | 131 | 2 | 2 | 0 | 3 | 4 |  |  | DI | 2 | BSTD1106FV03 | CB01 | LME STANDPIPE | 240VAC Flow Valve Power Circuit Breaker | Closed |  | BSTD1106FV03 |  | 2.2\0.3:4 | BR4-1860-E-00099 | 0 |  | S | [6 empty] | F4 | 9 | 10
BTY1502 | DX02 | DIO1 | 131 | 2 | 2 | 0 | 3 | 5 |  |  | DI | 2 | BSTD1107FV02 | ZS01 | HME STANDPIPE | Flow Valve | Open |  | BSTD1107FV02 |  | 2.2\0.3:5 | BR4-1860-E-00099 | 0 |  | S | [6 empty] | F4 | 11 | 12
BTY1502 | DX02 | DIO1 | 131 | 2 | 2 | 0 | 3 | 6 |  |  | DI | 2 | BSTD1107FV02 | ZS02 | HME STANDPIPE | Flow Valve | Closed |  | BSTD1107FV02 |  | 2.2\0.3:6 | BR4-1860-E-00099 | 0 |  | S | [6 empty] | F4 | 13 | 14
BTY1502 | DX02 | DIO1 | 131 | 2 | 2 | 0 | 3 | 7 |  |  | DI | 2 | BSTD1107FV02 | SW01 | HME STANDPIPE | Flow Valve Local Mode | Selected |  | BSTD1107FV02 |  | 2.2\0.3:7 | BR4-1860-E-00099 | 0 |  | S | [6 empty] | F4 | 15 | 16
BTY1502 | DX02 | DIO1 | 131 | 2 | 2 | 0 | 3 | 8 |  |  | DI | 2 | BSTD1107FV02 | XS01 | HME STANDPIPE | Flow Valve | Fault |  | BSTD1107FV02 |  | 2.2\0.3:8 | BR4-1860-E-00099 | 0 |  | S | [6 empty] | F4 | 17 | 18
BTY1502 | DX02 | DIO1 | 131 | 2 | 2 | 0 | 3 | 9 |  |  | DI | 2 | BSTD1107FV02 | CB01 | HME STANDPIPE | 240VAC Flow Valve Power Circuit Breaker | Closed |  | BSTD1107FV02 |  | 2.2\0.3:9 | BR4-1860-E-00099 | 0 |  | S | [6 empty] | F4 | 19 | 20
BTY1502 | DX02 | DIO1 | 131 | 2 | 2 | 0 | 3 | 10 |  |  | DI | 2 | BTY1502FV01 | ZS01 | WEST TURKEYS NEST | Flow Valve | Open |  | BTY1502FV01 |  | 2.2\0.3:10 | BR4-1860-E-00099 | 0 |  | S | [6 empty] | F4 | 21 | 22
BTY1502 | DX02 | DIO1 | 131 | 2 | 2 | 0 | 3 | 11 |  |  | DI | 2 | BTY1502FV01 | ZS02 | WEST TURKEYS NEST | Flow Valve | Closed |  | BTY1502FV01 |  | 2.2\0.3:11 | BR4-1860-E-00099 | 0 |  | S | [6 empty] | F4 | 23 | 24
BTY1502 | DX02 | DIO1 | 131 | 2 | 2 | 0 | 3 | 12 |  |  | DI | 2 | BTY1502FV01 | SW01 | WEST TURKEYS NEST | Flow Valve Local Mode | Selected |  | BTY1502FV01 |  | 2.2\0.3:12 | BR4-1860-E-00099 | 0 |  | S | [6 empty] | F4 | 25 | 26
BTY1502 | DX02 | DIO1 | 131 | 2 | 2 | 0 | 3 | 13 |  |  | DI | 2 | BTY1502FV01 | XS01 | WEST TURKEYS NEST | Flow Valve | Fault |  | BTY1502FV01 |  | 2.2\0.3:13 | BR4-1860-E-00099 | 0 |  | S | [6 empty] | F4 | 27 | 28
BTY1502 | DX02 | DIO1 | 131 | 2 | 2 | 0 | 3 | 14 |  |  | DI | 2 | BTY1502FV01 | CB01 | WEST TURKEYS NEST | 240VAC Flow Valve Power Circuit Breaker | Closed |  | BTY1502FV01 |  | 2.2\0.3:14 | BR4-1860-E-00099 | 0 |  | S | [6 empty] | F4 | 29 | 30
BTY1502 | DX02 | DIO1 | 131 | 2 | 2 | 0 | 3 | 15 |  |  | DI | [9 empty] | 2.2\0.3:15 |  |  |  | S | [6 empty] | F4 | 31 | 32
BTY1502 | DX02 | DIO1 | 131 | 2 | 2 | 0 | 3 | 16 |  |  | DI | [9 empty] | 2.2\0.3:16 |  |  |  | S | [6 empty] | F6 | 1 | 2
BTY1502 | DX02 | DIO1 | 131 | 2 | 2 | 0 | 3 | 17 |  |  | DI | [9 empty] | 2.2\0.3:17 |  |  |  | S | [6 empty] | F6 | 3 | 4
BTY1502 | DX02 | DIO1 | 131 | 2 | 2 | 0 | 3 | 18 |  |  | DI | [9 empty] | 2.2\0.3:18 |  |  |  | S | [6 empty] | F6 | 5 | 6
BTY1502 | DX02 | DIO1 | 131 | 2 | 2 | 0 | 3 | 19 |  |  | DI | [9 empty] | 2.2\0.3:19 |  |  |  | S | [6 empty] | F6 | 7 | 8
BTY1502 | DX02 | DIO1 | 131 | 2 | 2 | 0 | 3 | 20 |  |  | DI | [9 empty] | 2.2\0.3:20 |  |  |  | S | [6 empty] | F6 | 9 | 10
BTY1502 | DX02 | DIO1 | 131 | 2 | 2 | 0 | 3 | 21 |  |  | DI | [9 empty] | 2.2\0.3:21 |  |  |  | S | [6 empty] | F6 | 11 | 12
BTY1502 | DX02 | DIO1 | 131 | 2 | 2 | 0 | 3 | 22 |  |  | DI | [9 empty] | 2.2\0.3:22 |  |  |  | S | [6 empty] | F6 | 13 | 14
BTY1502 | DX02 | DIO1 | 131 | 2 | 2 | 0 | 3 | 23 |  |  | DI | [9 empty] | 2.2\0.3:23 |  |  |  | S | [6 empty] | F6 | 15 | 16
BTY1502 | DX02 | DIO1 | 131 | 2 | 2 | 0 | 3 | 24 |  |  | DI | [9 empty] | 2.2\0.3:24 |  |  |  | S | [6 empty] | F6 | 17 | 18
BTY1502 | DX02 | DIO1 | 131 | 2 | 2 | 0 | 3 | 25 |  |  | DI | [9 empty] | 2.2\0.3:25 |  |  |  | S | [6 empty] | F6 | 19 | 20
BTY1502 | DX02 | DIO1 | 131 | 2 | 2 | 0 | 3 | 26 |  |  | DI | [9 empty] | 2.2\0.3:26 |  |  |  | S | [6 empty] | F6 | 21 | 22
BTY1502 | DX02 | DIO1 | 131 | 2 | 2 | 0 | 3 | 27 |  |  | DI | [9 empty] | 2.2\0.3:27 |  |  |  | S | [6 empty] | F6 | 23 | 24
BTY1502 | DX02 | DIO1 | 131 | 2 | 2 | 0 | 3 | 28 |  |  | DI | [9 empty] | 2.2\0.3:28 |  |  |  | S | [6 empty] | F6 | 25 | 26
BTY1502 | DX02 | DIO1 | 131 | 2 | 2 | 0 | 3 | 29 |  |  | DI | [9 empty] | 2.2\0.3:29 |  |  |  | S | [6 empty] | F6 | 27 | 28
BTY1502 | DX02 | DIO1 | 131 | 2 | 2 | 0 | 3 | 30 |  |  | DI | [9 empty] | 2.2\0.3:30 |  |  |  | S | [6 empty] | F6 | 29 | 30
BTY1502 | DX02 | DIO1 | 131 | 2 | 2 | 0 | 3 | 31 |  |  | DI | [9 empty] | 2.2\0.3:31 |  |  |  | S | [6 empty] | F6 | 31 | 32
BTY1502 | DX02 | DIO1 | 131 | 2 | 2 | 0 | 4 | 0 | BMXFTB2010 | BMXDDO1602 | DO | 2 | BSTD1106LCS01 | IL01 | LME STANDPIPE | Standpipe | Running |  | BSTD1106 |  | 2.2\0.4:0 | BR4-1860-E-00101 | 0 |  | S | [6 empty] | F3 | 33 | 34
BTY1502 | DX02 | DIO1 | 131 | 2 | 2 | 0 | 4 | 1 |  |  | DO | 2 | BSTD1106LCS01 | IL02 | LME STANDPIPE | Standpipe | Fault |  | BSTD1106 |  | 2.2\0.4:1 | BR4-1860-E-00101 | 0 |  | S | [6 empty] | F3 | 35 | 36
BTY1502 | DX02 | DIO1 | 131 | 2 | 2 | 0 | 4 | 2 |  |  | DO | 2 | BSTD1106LCS01 | IL03 | LME STANDPIPE | Standpipe | Ready |  | BSTD1106 |  | 2.2\0.4:2 | BR4-1860-E-00101 | 0 |  | S | [6 empty] | F3 | 37 | 38
BTY1502 | DX02 | DIO1 | 131 | 2 | 2 | 0 | 4 | 3 |  |  | DO | 2 | BSTD1107LCS01 | IL01 | HME STANDPIPE | Standpipe | Running |  | BSTD1107 |  | 2.2\0.4:3 | BR4-1860-E-00101 | 0 |  | S | [6 empty] | F3 | 39 | 40
BTY1502 | DX02 | DIO1 | 131 | 2 | 2 | 0 | 4 | 4 |  |  | DO | 2 | BSTD1107LCS01 | IL02 | HME STANDPIPE | Standpipe | Fault |  | BSTD1107 |  | 2.2\0.4:4 | BR4-1860-E-00101 | 0 |  | S | [6 empty] | F3 | 41 | 42
BTY1502 | DX02 | DIO1 | 131 | 2 | 2 | 0 | 4 | 5 |  |  | DO | 2 | BSTD1107LCS01 | IL03 | HME STANDPIPE | Standpipe | Ready |  | BSTD1107 |  | 2.2\0.4:5 | BR4-1860-E-00101 | 0 |  | S | [6 empty] | F3 | 43 | 44
BTY1502 | DX02 | DIO1 | 131 | 2 | 2 | 0 | 4 | 6 |  |  | DO | [9 empty] | 2.2\0.4:6 |  |  |  | S | [6 empty] | F3 | 45 | 46
BTY1502 | DX02 | DIO1 | 131 | 2 | 2 | 0 | 4 | 7 |  |  | DO | [9 empty] | 2.2\0.4:7 |  |  |  | S | [6 empty] | F3 | 47 | 48
BTY1502 | DX02 | DIO1 | 131 | 2 | 2 | 0 | 4 | 8 |  |  | DO | [9 empty] | 2.2\0.4:8 |  |  |  | S | [6 empty] | F4 | 33 | 34
BTY1502 | DX02 | DIO1 | 131 | 2 | 2 | 0 | 4 | 9 |  |  | DO | [9 empty] | 2.2\0.4:9 |  |  |  | S | [6 empty] | F4 | 35 | 36
BTY1502 | DX02 | DIO1 | 131 | 2 | 2 | 0 | 4 | 10 |  |  | DO | [9 empty] | 2.2\0.4:10 |  |  |  | S | [6 empty] | F4 | 37 | 38
BTY1502 | DX02 | DIO1 | 131 | 2 | 2 | 0 | 4 | 11 |  |  | DO | [9 empty] | 2.2\0.4:11 |  |  |  | S | [6 empty] | F4 | 39 | 40
BTY1502 | DX02 | DIO1 | 131 | 2 | 2 | 0 | 4 | 12 |  |  | DO | [9 empty] | 2.2\0.4:12 |  |  |  | S | [6 empty] | F4 | 41 | 42
BTY1502 | DX02 | DIO1 | 131 | 2 | 2 | 0 | 4 | 13 |  |  | DO | [9 empty] | 2.2\0.4:13 |  |  |  | S | [6 empty] | F4 | 43 | 44
BTY1502 | DX02 | DIO1 | 131 | 2 | 2 | 0 | 4 | 14 |  |  | DO | [9 empty] | 2.2\0.4:14 |  |  |  | S | [6 empty] | F4 | 45 | 46
BTY1502 | DX02 | DIO1 | 131 | 2 | 2 | 0 | 4 | 15 |  |  | DO | 2 | BSR131DB02 | SR01 | TURKEY'S NEST 415V LIGHTING AND SMALL POWER DB | Lightning Control Relay | Enabled |  | BSR131DB02 |  | 2.2\0.4:15 |  |  |  | S | [6 empty] | F4 | 47 | 48
BTY1502 | DX02 | DIO1 | 131 | 2 | 2 | 0 | 5 | 0 | BMXFTW301S | BMEAHI0812 | AI | 2 | BTY1502FIT01 | FT01 | RAW WATER FROM EAST PIT | Flow Rate |  | m3/h | BTY1502 | REAL | 2.2\0.5:0 | BR4-1860-E-00098 | 0 | Located in BTY1502AX02 | S |  | 0 | 1000 | 0 | 1000 | # EU | F5 | 1 | 2
BTY1502 | DX02 | DIO1 | 131 | 2 | 2 | 0 | 5 | 1 |  |  | AI | 2 | BTY1502FIT03 | FT03 | RAW WATER FROM WEST PIT | Flow Rate |  | m3/h | BTY1502 | REAL | 2.2\0.5:1 | BR4-1860-E-00098 | 0 | Located in BTY1502AX02 | S |  | 0 | 1200 | 0 | 1200 | # EU | F5 | 3 | 4
BTY1502 | DX02 | DIO1 | 131 | 2 | 2 | 0 | 5 | 2 |  |  | AI | 2 | BTY1502PT01 | PT01 | RAW WATER FROM EAST PIT | Pressure |  | kPa | BTY1502 | REAL | 2.2\0.5:2 | BR4-1860-E-00102 | 0 |  | S |  | 0 | 2000 | 0 | 2000 | # EU | F5 | 5 | 6
BTY1502 | DX02 | DIO1 | 131 | 2 | 2 | 0 | 5 | 3 |  |  | AI | 2 | BTY1502PT03 | PT03 | RAW WATER FROM WEST PIT | Pressure |  | kPa | BTY1502 | REAL | 2.2\0.5:3 | BR4-1860-E-00102 | 0 |  | S |  | 0 | 2000 | 0 | 2000 | # EU | F5 | 7 | 8
BTY1502 | DX02 | DIO1 | 131 | 2 | 2 | 0 | 5 | 4 |  |  | AI | [9 empty] | 2.2\0.5:4 |  |  |  | S | [6 empty] | F5 | 9 | 10
BTY1502 | DX02 | DIO1 | 131 | 2 | 2 | 0 | 5 | 5 |  |  | AI | [9 empty] | 2.2\0.5:5 |  |  |  | S | [6 empty] | F5 | 11 | 12
BTY1502 | DX02 | DIO1 | 131 | 2 | 2 | 0 | 5 | 6 |  |  | AI | [9 empty] | 2.2\0.5:6 |  |  |  | S | [6 empty] | F5 | 13 | 14
BTY1502 | DX02 | DIO1 | 131 | 2 | 2 | 0 | 5 | 7 |  |  | AI | [9 empty] | 2.2\0.5:7 |  |  |  | S | [6 empty] | F5 | 15 | 16
BTY1502 | DX02 | DIO1 | 131 | 2 | 2 | 0 | 6 | 0 | BMXFTW301S | BMEAHI0812 | AI | 2 | BSTD1106FIT03 | FT03 | LME STANDPIPE | Flow Rate |  | m3/h | BSTD1106 | REAL | 2.2\0.6:0 | BR4-1860-E-00100 | 0 | Located in BTY1502AX01 | S |  | 0 | 850 | 0 | 850 | # EU | F5 | 17 | 18
BTY1502 | DX02 | DIO1 | 131 | 2 | 2 | 0 | 6 | 1 |  |  | AI | 2 | BSTD1107FIT02 | FT02 | HME STANDPIPE | Flow Rate |  | m3/h | BSTD1107 | REAL | 2.2\0.6:1 | BR4-1860-E-00100 | 0 | Located in BTY1502AX01 | S |  | 0 | 850 | 0 | 850 | # EU | F5 | 19 | 20
BTY1502 | DX02 | DIO1 | 131 | 2 | 2 | 0 | 6 | 2 |  |  | AI | 2 | BSTD1106FV03 | ZT01 | LME STANDPIPE | Flow Valve Position |  | % | BSTD1106FV03 | REAL | 2.2\0.6:2 | BR4-1860-E-00099 | 0 |  | S |  | 0 | 100 | 0 | 100 | #.# EU | F5 | 21 | 22
BTY1502 | DX02 | DIO1 | 131 | 2 | 2 | 0 | 6 | 3 |  |  | AI | 2 | BSTD1107FV02 | ZT01 | HME STANDPIPE | Flow Valve Position |  | % | BSTD1107FV02 | REAL | 2.2\0.6:3 | BR4-1860-E-00099 | 0 |  | S |  | 0 | 100 | 0 | 100 | #.# EU | F5 | 23 | 24
BTY1502 | DX02 | DIO1 | 131 | 2 | 2 | 0 | 6 | 4 |  |  | AI | 2 | BPP1106PIT01 | PT01 | HME AND LME STANDPIPE PUMP BPP1106 | Pressure |  | kPa | BPP1106 | REAL | 2.2\0.6:4 | BR4-1860-E-00102 | 0 |  | S |  | 0 | 750 | 0 | 750 | # EU | F5 | 25 | 26
BTY1502 | DX02 | DIO1 | 131 | 2 | 2 | 0 | 6 | 5 |  |  | AI | 2 | BPP1107PIT02 | PT02 | HME AND LME STANDPIPE PUMP BPP1107 | Pressure |  | kPa | BPP1107 | REAL | 2.2\0.6:5 | BR4-1860-E-00102 | 0 |  | S |  | 0 | 750 | 0 | 750 | # EU | F5 | 27 | 28
BTY1502 | DX02 | DIO1 | 131 | 2 | 2 | 0 | 6 | 6 |  |  | AI | [9 empty] | 2.2\0.6:6 |  |  |  | S | [6 empty] | F5 | 29 | 30
BTY1502 | DX02 | DIO1 | 131 | 2 | 2 | 0 | 6 | 7 |  |  | AI | [9 empty] | 2.2\0.6:7 |  |  |  | S | [6 empty] | F5 | 31 | 32
BTY1502 | DX02 | DIO1 | 131 | 2 | 2 | 0 | 7 | 0 | BMXFTW301S | BMEAHI0812 | AI | 2 | BPP1101PT03 | PT03 | PRODUCTION PLANT & NPI WATER SUPPLY PUMP 1 (DUTY) | Discharge Pressure |  | kPa | BPP1101 | REAL | 2.2\0.7:0 | BR4-1860-E-00102 | 0 |  | S |  | 0 | 1500 | 0 | 1500 | # EU | F5 | 33 | 34
BTY1502 | DX02 | DIO1 | 131 | 2 | 2 | 0 | 7 | 1 |  |  | AI | 2 | BPP1102PT04 | PT04 | PRODUCTION PLANT & NPI WATER SUPPLY PUMP 2 (STANDBY) | Discharge Pressure |  | kPa | BPP1102 | REAL | 2.2\0.7:1 | BR4-1860-E-00102 | 0 |  | S |  | 0 | 1500 | 0 | 1500 | # EU | F5 | 35 | 36
BTY1502 | DX02 | DIO1 | 131 | 2 | 2 | 0 | 7 | 2 |  |  | AI | 2 | BPP1101FIT03 | FT01 | PRIMARY CRUSHER AND NPI HUB TANKS | Flow Rate |  | m3/h | BPP1101 | REAL | 2.2\0.7:2 | BR4-1860-E-00098 | 0 | Located in BTY1502AX01 | S |  | 0 | 400 | 0 | 400 | # EU | F5 | 37 | 38
BTY1502 | DX02 | DIO1 | 131 | 2 | 2 | 0 | 7 | 3 |  |  | AI | 2 | BTY1502FIT02 | FT02 | WEST TURKEYS NEST | Flow Rate |  | m3/h | BTY1502 | REAL | 2.2\0.7:3 | BR4-1860-E-00098 | 0 | Located in BTY1502AX01 | S |  | 0 | 100 | 0 | 100 | # EU | F5 | 39 | 40
BTY1502 | DX02 | DIO1 | 131 | 2 | 2 | 0 | 7 | 4 |  |  | AI | 2 | BTY1502FV01 | ZT01 | WEST TURKEYS NEST | Flow Valve Position |  | % | BTY1502FV01 | REAL | 2.2\0.7:4 | BR4-1860-E-00099 | 0 |  | S |  | 0 | 100 | 0 | 100 | #.# EU | F5 | 41 | 42
BTY1502 | DX02 | DIO1 | 131 | 2 | 2 | 0 | 7 | 5 |  |  | AI | 2 | BPP1101PIT10 | PT10 | BPP1101 AND BPP1102 COMMON DISCHARGE HEADER | Discharge Pressure 1 |  | kPa | BPP1101 | REAL | 2.2\0.7:5 | BR4-1860-E-00102 | 0 |  | S |  | 0 | 1500 | 0 | 1500 | # EU | F5 | 43 | 44
BTY1502 | DX02 | DIO1 | 131 | 2 | 2 | 0 | 7 | 6 |  |  | AI | 2 | BPP1101PIT11 | PT11 | BPP1101 AND BPP1102 COMMON DISCHARGE HEADER | Discharge Pressure 2 |  | kPa | BPP1101 | REAL | 2.2\0.7:6 | BR4-1860-E-00102 | 0 |  | S |  | 0 | 1500 | 0 | 1500 | # EU | F5 | 45 | 46
BTY1502 | DX02 | DIO1 | 131 | 2 | 2 | 0 | 7 | 7 |  |  | AI | [9 empty] | 2.2\0.7:7 |  |  |  | S | [6 empty] | F5 | 47 | 48
BTY1502 | DX02 | DIO1 | 131 | 2 | 2 | 0 | 8 |  |  | BMXXEM010 | [10 empty] | 2.2\0.8:
BTY1502 | DX02 | DIO1 | 131 | 2 | 2 | 0 | 8 | [13 empty] | 2.2\0.8:
BTY1502 | DX02 | DIO1 | 131 | 2 | 2 | 0 | 8 | [13 empty] | 2.2\0.8:
BTY1502 | DX02 | DIO1 | 131 | 2 | 2 | 0 | 8 | [13 empty] | 2.2\0.8:
BTY1502 | DX02 | DIO1 | 131 | 2 | 2 | 0 | 9 | 0 | BMXFTW301S | BMEAHO0412 | AO | 2 | BSTD1106FV03 | FV03 | LME STANDPIPE | Flow Valve Position Reference |  | % | BSTD1106 | REAL | 2.2\0.9:0 | BR4-1860-E-00099 | 0 |  | S |  | 0 | 110 | 0 | 110 | # EU | F2 | 33 | 34
BTY1502 | DX02 | DIO1 | 131 | 2 | 2 | 0 | 9 | 1 |  |  | AO | 2 | BSTD1107FV02 | FV02 | HME STANDPIPE | Flow Valve Position Reference |  | % | BSTD1107 | REAL | 2.2\0.9:1 | BR4-1860-E-00099 | 0 |  | S |  | 0 | 110 | 0 | 110 | # EU | F2 | 35 | 36
BTY1502 | DX02 | DIO1 | 131 | 2 | 2 | 0 | 9 | 2 |  |  | AO | 2 | BTY1502FV01 | FV01 | WEST TURKEYS NEST | Flow Valve Position Reference |  | % | BTY1502 | REAL | 2.2\0.9:2 | BR4-1860-E-00099 | 0 |  | S |  | 0 | 110 | 0 | 110 | # EU | F2 | 37 | 38
BTY1502 | DX02 | DIO1 | 131 | 2 | 2 | 0 | 9 | 3 |  |  | AO | [9 empty] | 2.2\0.9:3 |  |  |  | S | [6 empty] | F2 | 39 | 40
BTY1502 | DX02 | DIO1 | 131 | 2 | 2 | 0 | 10 |  |  | BMXXEM010 | [10 empty] | 2.2\0.10:
BTY1502 | DX02 | DIO1 | 131 | 2 | 2 | 0 | 10 | [13 empty] | 2.2\0.10:
BTY1502 | DX02 | DIO1 | 131 | 2 | 2 | 0 | 10 | [13 empty] | 2.2\0.10:
BTY1502 | DX02 | DIO1 | 131 | 2 | 2 | 0 | 10 | [13 empty] | 2.2\0.10:
BTY1502 | DX02 | DIO1 | 131 | 2 | 2 | 0 | 11 |  |  | BMXXEM010 | [10 empty] | 2.2\0.11:
BTY1502 | DX02 | DIO1 | 131 | 2 | 2 | 0 | 11 | [13 empty] | 2.2\0.11:
BTY1502 | DX02 | DIO1 | 131 | 2 | 2 | 0 | 11 | [13 empty] | 2.2\0.11:
BTY1502 | DX02 | DIO1 | 131 | 2 | 2 | 0 | 11 | [13 empty] | 2.2\0.11:
[13 empty] | BPP1101LCS01 | SY01 | PRODUCTION PLANT & NPI WATER SUPPLY PUMP 1 (DUTY) | Emergency Stop Relay |  | SUB LINK | BPP1101LCS01 |  |  | BR4-1860-E-00068 | [9 empty] | F7 | 1 | 2 | 3 | 4
[13 empty] | BPP1102LCS02 | SY01 | PRODUCTION PLANT & NPI WATER SUPPLY PUMP 2 (STANDBY) | Emergency Stop Relay |  | SUB LINK | BPP1102LCS02 |  |  | BR4-1860-E-00069 | [9 empty] | F7 | 5 | 6 | 7 | 8
[13 empty] | BPP1106LCS06 | SY01 | HME AND LME STANDPIPE PUMP 3 (DUTY) | Emergency Stop Relay |  | SUB LINK | BPP1106LCS06 |  |  | BR4-1860-E-00070 | [9 empty] | F7 | 9 | 10 | 11 | 12
[13 empty] | BPP1107LCS07 | SY01 | HME AND LME STANDPIPE PUMP 4 (STANDBY) | Emergency Stop Relay |  | SUB LINK | BPP1107LCS07 |  |  | BR4-1860-E-00071 | [9 empty] | F7 | 13 | 14 | 15 | 16
[32 empty] | F7 | 17 | 18 | 19 | 20
[32 empty] | F7 | 21 | 22 | 23 | 24
[32 empty] | F7 | 25 | 26 | 27 | 28
[32 empty] | F7 | 29 | 30 | 31 | 32
[32 empty] | F7 | 33 | 34 | 35 | 36
[32 empty] | F7 | 37 | 38 | 39 | 40
[32 empty] | F7 | 41 | 42 | 43 | 44
[32 empty] | F7 | 45 | 46 | 47 | 48
BTY1502DX03 - West Turkeys Nest
EIO node #3 | DX03 | DIO1 | 131 | 2 | 3 | 0
BTY1502 | DX03 | DIO1 | 131 | 2 | 3 | 0 |  | Chassis |  | BMEXBP1200
BTY1502 | DX03 | DIO1 | 131 | 2 | 3 | 0 |  | Power |  | BMXCPS4022 |  | total |  | spare |  | % spare
BTY1502 | DX03 | DIO1 | 131 | 2 | 3 | 0 | 0 | Comms |  | BMECRA31210 | I/O1 | 48 |  | 45 |  | 93.75%
BTY1502 | DX03 | DIO1 | 131 | 2 | 3 | 0 | 1 | 0 | BMXFCW303 | BMXDDI3202K | DI | 2 | BTY1502DX03 | CB01 | 24VDC BPP1103 Field Supply | 240VAC Circuit Breaker | Closed | Q106 | BTY1502DX03 |  | 2.3\0.1:0 | BR4-1860-E-00262 | 0 |  | D | [6 empty] | F1 |  | 1
BTY1502 | DX03 | DIO1 | 131 | 2 | 3 | 0 | 1 | 1 |  |  | DI | 2 | BTY1502DX03 | VDC01 | 24VDC BPP1104 Field Supply | 24VDC Output Control Supply | Healthy | Q143 | BTY1502DX03 |  | 2.3\0.1:1 | BR4-1860-E-00262 | 0 |  | D | [6 empty] | F1 |  | 2
BTY1502 | DX03 | DIO1 | 131 | 2 | 3 | 0 | 1 | 2 |  |  | DI | 2 | BTY1502DX03 | VDC02 | 24VDC BPP1105 Field Supply | 24VDC GW1 Control Supply | Healthy | Q157 | BTY1502DX03 |  | 2.3\0.1:2 | BR4-1860-E-00262 | 0 |  | D | [6 empty] | F1 |  | 3
BTY1502 | DX03 | DIO1 | 131 | 2 | 3 | 0 | 1 | 3 |  |  | DI | 2 | BTY1502DX03 | VDC03 |  | 24VDC Instrument Control Supply | Healthy | Q164 | BTY1502DX03 |  | 2.3\0.1:3 | BR4-1860-E-00262 | 0 |  | D | [6 empty] | F1 |  | 4
BTY1502 | DX03 | DIO1 | 131 | 2 | 3 | 0 | 1 | 4 |  |  | DI | 2 | BTY1502DX03 | VDC04 |  | 24VDC Transmitter Control Supply | Healthy | Q168 | BTY1502DX03 |  | 2.3\0.1:4 | BR4-1860-E-00262 | 0 |  | D | [6 empty] | F1 |  | 5
BTY1502 | DX03 | DIO1 | 131 | 2 | 3 | 0 | 1 | 5 |  |  | DI | 2 | BTY1502DX03 | VDC05 |  | 24VDC BTY1502DX03 Field Control Supply | Healthy | Q172 | BTY1502DX03 |  | 2.3\0.1:5 | BR4-1860-E-00262 | 0 |  | D | [6 empty] | F1 |  | 6
BTY1502 | DX03 | DIO1 | 131 | 2 | 3 | 0 | 1 | 6 |  |  | DI | 2 | BTY1502DX03 | VDC06 |  | 24VDC BPP1103 Field Control Supply | Healthy | Q176 | BTY1502DX03 |  | 2.3\0.1:6 | BR4-1860-E-00262 | 0 |  | D | [6 empty] | F1 |  | 7
BTY1502 | DX03 | DIO1 | 131 | 2 | 3 | 0 | 1 | 7 |  |  | DI | 2 | BTY1502DX03 | VDC07 |  | 24VDC BPP1104 Field Control Supply | Healthy | Q180 | BTY1502DX03 |  | 2.3\0.1:7 | BR4-1860-E-00262 | 0 |  | D | [6 empty] | F1 |  | 8
BTY1502 | DX03 | DIO1 | 131 | 2 | 3 | 0 | 1 | 8 |  |  | DI | 2 | BTY1502DX03 | VDC08 |  | 24VDC BPP1105 Field Control Supply | Healthy | Q184 | BTY1502DX03 |  | 2.3\0.1:8 | BR4-1860-E-00262 | 0 |  | D | [6 empty] | F1 |  | 9
BTY1502 | DX03 | DIO1 | 131 | 2 | 3 | 0 | 1 | 9 |  |  | DI | 2 | BTY1502DX03 | VDC09 |  | 24VDC Spare Control Supply | Healthy | Q188 | BTY1502DX03 |  | 2.3\0.1:9 | BR4-1860-E-00262 | 0 |  | D | [6 empty] | F1 |  | 10
BTY1502 | DX03 | DIO1 | 131 | 2 | 3 | 0 | 1 | 10 |  |  | DI | 2 | BTY1502DX03 | VDC10 |  | 24VDC Spare Control Supply | Healthy | Q192 | BTY1502DX03 |  | 2.3\0.1:10 | BR4-1860-E-00262 | 0 |  | D | [6 empty] | F1 |  | 11
BTY1502 | DX03 | DIO1 | 131 | 2 | 3 | 0 | 1 | 11 |  |  | DI | 2 | BTY1502DX03 | VDC11 |  | 24VDC Spare Control Supply | Healthy | Q196 | BTY1502DX03 |  | 2.3\0.1:11 | BR4-1860-E-00262 | 0 |  | D | [6 empty] | F1 |  | 12
BTY1502 | DX03 | DIO1 | 131 | 2 | 3 | 0 | 1 | 12 |  |  | DI | [9 empty] | 2.3\0.1:12 |  |  |  | S | [6 empty] | F1 |  | 13
BTY1502 | DX03 | DIO1 | 131 | 2 | 3 | 0 | 1 | 13 |  |  | DI | [9 empty] | 2.3\0.1:13 |  |  |  | S | [6 empty] | F1 |  | 14
BTY1502 | DX03 | DIO1 | 131 | 2 | 3 | 0 | 1 | 14 |  |  | DI | [9 empty] | 2.3\0.1:14 |  |  |  | S | [6 empty] | F1 |  | 15
BTY1502 | DX03 | DIO1 | 131 | 2 | 3 | 0 | 1 | 15 |  |  | DI | [9 empty] | 2.3\0.1:15 |  |  |  | S | [6 empty] | F1 |  | 16
BTY1502 | DX03 | DIO1 | 131 | 2 | 3 | 0 | 1 | 16 |  |  | DI | 2 | BPP1103LCS03 | STT01 | WATER TRANSFER PUMP 1 (DUTY) | Start Pushbutton | Activated |  | BPP1103 |  | 2.3\0.1:16 | BR4-1860-E-00072 | 0 |  | S | [6 empty] | F1 | 17 | 18
BTY1502 | DX03 | DIO1 | 131 | 2 | 3 | 0 | 1 | 17 |  |  | DI | 2 | BPP1103LCS03 | STP01 | WATER TRANSFER PUMP 1 (DUTY) | Stop Pushbutton | Activated |  | BPP1103 |  | 2.3\0.1:17 | BR4-1860-E-00072 | 0 |  | S | [6 empty] | F1 | 19 | 20
BTY1502 | DX03 | DIO1 | 131 | 2 | 3 | 0 | 1 | 18 |  |  | DI | 2 | BPP1104LCS04 | STT01 | WATER TRANSFER PUMP 2 (DUTY) | Start Pushbutton | Activated |  | BPP1104 |  | 2.3\0.1:18 | BR4-1860-E-00073 | 0 |  | S | [6 empty] | F1 | 21 | 22
BTY1502 | DX03 | DIO1 | 131 | 2 | 3 | 0 | 1 | 19 |  |  | DI | 2 | BPP1104LCS04 | STP01 | WATER TRANSFER PUMP 2 (DUTY) | Stop Pushbutton | Activated |  | BPP1104 |  | 2.3\0.1:19 | BR4-1860-E-00073 | 0 |  | S | [6 empty] | F1 | 23 | 24
BTY1502 | DX03 | DIO1 | 131 | 2 | 3 | 0 | 1 | 20 |  |  | DI | 2 | BPP1105LCS05 | STT01 | WATER TRANSFER PUMP 3 (STANDBY) | Start Pushbutton | Activated |  | BPP1105 |  | 2.3\0.1:20 | BR4-1860-E-00074 | 0 |  | S | [6 empty] | F1 | 25 | 26
BTY1502 | DX03 | DIO1 | 131 | 2 | 3 | 0 | 1 | 21 |  |  | DI | 2 | BPP1105LCS05 | STP01 | WATER TRANSFER PUMP 3 (STANDBY) | Stop Pushbutton | Activated |  | BPP1105 |  | 2.3\0.1:21 | BR4-1860-E-00074 | 0 |  | S | [6 empty] | F1 | 27 | 28
BTY1502 | DX03 | DIO1 | 131 | 2 | 3 | 0 | 1 | 22 |  |  | DI | 2 | BPP1103 | THR01 | WATER TRANSFER PUMP 1 (DUTY) | Thermistor Relay | Healthy | K190 | BPP1103 |  | 2.3\0.1:22 | BR4-1860-E-00072 | 0 |  | S | [6 empty] | F1 | 29 | 30
BTY1502 | DX03 | DIO1 | 131 | 2 | 3 | 0 | 1 | 23 |  |  | DI | 2 | BPP1104 | THR01 | WATER TRANSFER PUMP 2 (DUTY) | Thermistor Relay | Healthy | K190 | BPP1104 |  | 2.3\0.1:23 | BR4-1860-E-00073 | 0 |  | S | [6 empty] | F1 | 31 | 32
BTY1502 | DX03 | DIO1 | 131 | 2 | 3 | 0 | 1 | 24 |  |  | DI | 2 | BPP1105 | THR01 | WATER TRANSFER PUMP 3 (STANDBY) | Thermistor Relay | Healthy | K190 | BPP1105 |  | 2.3\0.1:24 | BR4-1860-E-00074 | 0 |  | S | [6 empty] | F1 | 33 | 34
BTY1502 | DX03 | DIO1 | 131 | 2 | 3 | 0 | 1 | 25 |  |  | DI | 2 | BPP1103FIT03 | FQ03 | WATER TRANSFER PUMP 1 (DUTY) | Flow Totaliser | Pulse |  | BPP1103 |  | 2.3\0.1:25 | BR4-1860-E-00263 | 0 |  | S | [6 empty] | F1 | 35 | 36
BTY1502 | DX03 | DIO1 | 131 | 2 | 3 | 0 | 1 | 26 |  |  | DI | 2 | BPP1104FIT04 | FQ04 | WATER TRANSFER PUMP 2 (DUTY) | Flow Totaliser | Pulse |  | BPP1104 |  | 2.3\0.1:26 | BR4-1860-E-00263 | 0 |  | S | [6 empty] | F1 | 37 | 38
BTY1502 | DX03 | DIO1 | 131 | 2 | 3 | 0 | 1 | 27 |  |  | DI | 2 | BPP1105FIT05 | FQ05 | WATER TRANSFER PUMP 3 (STANDBY) | Flow Totaliser | Pulse |  | BPP1105 |  | 2.3\0.1:27 | BR4-1860-E-00263 | 0 |  | S | [6 empty] | F1 | 39 | 40
BTY1502 | DX03 | DIO1 | 131 | 2 | 3 | 0 | 1 | 28 |  |  | DI | 2 | BPP1103FIT06 | FQ06 | SURPLUS WATER TRANSFER SYSTEM | Flow Totaliser | Pulse |  | BPP1103 |  | 2.3\0.1:28 | BR4-1860-E-00263 | 0 |  | S | [6 empty] | F1 | 41 | 42
BTY1502 | DX03 | DIO1 | 131 | 2 | 3 | 0 | 1 | 29 |  |  | DI | [9 empty] | 2.3\0.1:29 |  |  |  | S | [6 empty] | F1 | 43 | 44
BTY1502 | DX03 | DIO1 | 131 | 2 | 3 | 0 | 1 | 30 |  |  | DI | [9 empty] | 2.3\0.1:30 |  |  |  | S | [6 empty] | F1 | 45 | 46
BTY1502 | DX03 | DIO1 | 131 | 2 | 3 | 0 | 1 | 31 |  |  | DI | [9 empty] | 2.3\0.1:31 |  |  |  | S | [6 empty] | F1 | 47 | 48
BTY1502 | DX03 | DIO1 | 131 | 2 | 3 | 0 | 2 |  |  | BMXXEM010 | [10 empty] | 2.3\0.2:
BTY1502 | DX03 | DIO1 | 131 | 2 | 3 | 0 | 2 | [13 empty] | 2.3\0.2:
BTY1502 | DX03 | DIO1 | 131 | 2 | 3 | 0 | 2 | [13 empty] | 2.3\0.2:
BTY1502 | DX03 | DIO1 | 131 | 2 | 3 | 0 | 2 | [13 empty] | 2.3\0.2:
BTY1502 | DX03 | DIO1 | 131 | 2 | 3 | 0 | 3 | 0 | BMXFTW301S | BMEAHI0812 | AI | 2 | BPP1103FIT03 | FT03 | WATER TRANSFER PUMP 1 (DUTY) | Flow Rate |  | m3/h | BPP1103 | REAL | 2.3\0.3:0 | BR4-1860-E-00263 | 0 | Located in BTY1502AX01 | S |  | 0 | 1000 | 0 | 1000 | # EU | F5 | 1 | 2
BTY1502 | DX03 | DIO1 | 131 | 2 | 3 | 0 | 3 | 1 |  |  | AI | 2 | BPP1103PT05 | PT05 | WATER TRANSFER PUMP 1 (DUTY) | Discharge Pressure |  | kPa | BPP1103 | REAL | 2.3\0.3:1 | BR4-1860-E-00264 | 0 |  | S |  | 0 | 700 | 0 | 700 | # EU | F5 | 3 | 4
BTY1502 | DX03 | DIO1 | 131 | 2 | 3 | 0 | 3 | 2 |  |  | AI | 2 | BPP1104FIT04 | FT04 | WATER TRANSFER PUMP 2 (DUTY) | Flow Rate |  | m3/h | BPP1104 | REAL | 2.3\0.3:2 | BR4-1860-E-00263 | 0 | Located in BTY1502AX01 | S |  | 0 | 1000 | 0 | 1000 | # EU | F5 | 5 | 6
BTY1502 | DX03 | DIO1 | 131 | 2 | 3 | 0 | 3 | 3 |  |  | AI | 2 | BPP1104PT06 | PT06 | WATER TRANSFER PUMP 2 (DUTY) | Discharge Pressure |  | kPa | BPP1104 | REAL | 2.3\0.3:3 | BR4-1860-E-00264 | 0 |  | S |  | 0 | 700 | 0 | 700 | # EU | F5 | 7 | 8
BTY1502 | DX03 | DIO1 | 131 | 2 | 3 | 0 | 3 | 4 |  |  | AI | 2 | BPP1105FIT05 | FT05 | WATER TRANSFER PUMP 3 (STANDBY) | Flow Rate |  | m3/h | BPP1105 | REAL | 2.3\0.3:4 | BR4-1860-E-00263 | 0 | Located in BTY1502AX01 | S |  | 0 | 1000 | 0 | 1000 | # EU | F5 | 9 | 10
BTY1502 | DX03 | DIO1 | 131 | 2 | 3 | 0 | 3 | 5 |  |  | AI | 2 | BPP1105PT07 | PT07 | WATER TRANSFER PUMP 3 (STANDBY) | Discharge Pressure |  | kPa | BPP1105 | REAL | 2.3\0.3:5 | BR4-1860-E-00264 | 0 |  | S |  | 0 | 700 | 0 | 700 | # EU | F5 | 11 | 12
BTY1502 | DX03 | DIO1 | 131 | 2 | 3 | 0 | 3 | 6 |  |  | AI | [9 empty] | 2.3\0.3:6 |  |  |  | S | [6 empty] | F5 | 13 | 14
BTY1502 | DX03 | DIO1 | 131 | 2 | 3 | 0 | 3 | 7 |  |  | AI | [9 empty] | 2.3\0.3:7 |  |  |  | S | [6 empty] | F5 | 15 | 16
BTY1502 | DX03 | DIO1 | 131 | 2 | 3 | 0 | 4 | 0 | BMXFTW301S | BMEAHI0812 | AI | 2 | BPP1103FIT06 | FT06 | SURPLUS WATER TRANSFER SYSTEM | Flow Rate |  | m3/h | BPP1103 | REAL | 2.3\0.4:0 | BR4-1860-E-00263 | 0 | Located in BTY1502AX01 | S |  | 0 | 2000 | 0 | 2000 | # EU | F5 | 17 | 18
BTY1502 | DX03 | DIO1 | 131 | 2 | 3 | 0 | 4 | 1 |  |  | AI | 2 | BPP1103PT08 | PT08 | SURPLUS WATER TRANSFER SYSTEM | Discharge Pressure |  | kPa | BPP1103 | REAL | 2.3\0.4:1 | BR4-1860-E-00264 | 0 |  | S |  | 0 | 700 | 0 | 700 | # EU | F5 | 19 | 20
BTY1502 | DX03 | DIO1 | 131 | 2 | 3 | 0 | 4 | 2 |  |  | AI | 2 | BTY1502LT01 | LT01 | WEST TURKEYS NEST | Level 1 |  | mm | BTY1502 | REAL | 2.3\0.4:2 | BR4-1860-E-00264 | 0 |  | S |  | 0 | 4800 | 0 | 4800 | ## EU | F5 | 21 | 22
BTY1502 | DX03 | DIO1 | 131 | 2 | 3 | 0 | 4 | 3 |  |  | AI | 2 | BTY1502LT02 | LT02 | WEST TURKEYS NEST | Level 2 |  | mm | BTY1502 | REAL | 2.3\0.4:3 | BR4-1860-E-00264 | 0 |  | S |  | 0 | 4800 | 0 | 4800 | ## EU | F5 | 23 | 24
BTY1502 | DX03 | DIO1 | 131 | 2 | 3 | 0 | 4 | 4 |  |  | AI | [9 empty] | 2.3\0.4:4 |  |  |  | S | [6 empty] | F5 | 25 | 26
BTY1502 | DX03 | DIO1 | 131 | 2 | 3 | 0 | 4 | 5 |  |  | AI | [9 empty] | 2.3\0.4:5 |  |  |  | S | [6 empty] | F5 | 27 | 28
BTY1502 | DX03 | DIO1 | 131 | 2 | 3 | 0 | 4 | 6 |  |  | AI | [9 empty] | 2.3\0.4:6 |  |  |  | S | [6 empty] | F5 | 29 | 30
BTY1502 | DX03 | DIO1 | 131 | 2 | 3 | 0 | 4 | 7 |  |  | AI | [9 empty] | 2.3\0.4:7 |  |  |  | S | [6 empty] | F5 | 31 | 32
BTY1502 | DX03 | DIO1 | 131 | 2 | 3 | 0 | 5 |  |  | BMXXEM010 | [10 empty] | 2.3\0.5:
BTY1502 | DX03 | DIO1 | 131 | 2 | 3 | 0 | 5 | [13 empty] | 2.3\0.5:
BTY1502 | DX03 | DIO1 | 131 | 2 | 3 | 0 | 5 | [13 empty] | 2.3\0.5:
BTY1502 | DX03 | DIO1 | 131 | 2 | 3 | 0 | 5 | [13 empty] | 2.3\0.5:
BTY1502 | DX03 | DIO1 | 131 | 2 | 3 | 0 | 6 |  |  | BMXXEM010 | [10 empty] | 2.3\0.6:
BTY1502 | DX03 | DIO1 | 131 | 2 | 3 | 0 | 6 | [13 empty] | 2.3\0.6:
BTY1502 | DX03 | DIO1 | 131 | 2 | 3 | 0 | 6 | [13 empty] | 2.3\0.6:
BTY1502 | DX03 | DIO1 | 131 | 2 | 3 | 0 | 6 | [13 empty] | 2.3\0.6:
BTY1502 | DX03 | DIO1 | 131 | 2 | 3 | 0 | 7 |  |  | BMXXEM010 | [10 empty] | 2.3\0.7:
BTY1502 | DX03 | DIO1 | 131 | 2 | 3 | 0 | 7 | [13 empty] | 2.3\0.7:
BTY1502 | DX03 | DIO1 | 131 | 2 | 3 | 0 | 7 | [13 empty] | 2.3\0.7:
BTY1502 | DX03 | DIO1 | 131 | 2 | 3 | 0 | 7 | [13 empty] | 2.3\0.7:
BTY1502 | DX03 | DIO1 | 131 | 2 | 3 | 0 | 8 |  |  | BMXXEM010 | [10 empty] | 2.3\0.8:
BTY1502 | DX03 | DIO1 | 131 | 2 | 3 | 0 | 8 | [13 empty] | 2.3\0.8:
BTY1502 | DX03 | DIO1 | 131 | 2 | 3 | 0 | 8 | [13 empty] | 2.3\0.8:
BTY1502 | DX03 | DIO1 | 131 | 2 | 3 | 0 | 8 | [13 empty] | 2.3\0.8:
BTY1502 | DX03 | DIO1 | 131 | 2 | 3 | 0 | 9 |  |  | BMXXEM010 | [10 empty] | 2.3\0.9:
BTY1502 | DX03 | DIO1 | 131 | 2 | 3 | 0 | 9 | [13 empty] | 2.3\0.9:
BTY1502 | DX03 | DIO1 | 131 | 2 | 3 | 0 | 9 | [13 empty] | 2.3\0.9:
BTY1502 | DX03 | DIO1 | 131 | 2 | 3 | 0 | 9 | [13 empty] | 2.3\0.9:
BTY1502 | DX03 | DIO1 | 131 | 2 | 3 | 0 | 10 |  |  | BMXXEM010 | [10 empty] | 2.3\0.10:
BTY1502 | DX03 | DIO1 | 131 | 2 | 3 | 0 | 10 | [13 empty] | 2.3\0.10:
BTY1502 | DX03 | DIO1 | 131 | 2 | 3 | 0 | 10 | [13 empty] | 2.3\0.10:
BTY1502 | DX03 | DIO1 | 131 | 2 | 3 | 0 | 10 | [13 empty] | 2.3\0.10:
BTY1502 | DX03 | DIO1 | 131 | 2 | 3 | 0 | 11 |  |  | BMXXEM010 | [10 empty] | 2.3\0.11:
BTY1502 | DX03 | DIO1 | 131 | 2 | 3 | 0 | 11 | [13 empty] | 2.3\0.11:
BTY1502 | DX03 | DIO1 | 131 | 2 | 3 | 0 | 11 | [13 empty] | 2.3\0.11:
BTY1502 | DX03 | DIO1 | 131 | 2 | 3 | 0 | 11 | [13 empty] | 2.3\0.11:
[13 empty] | BPP1103LCS03 | SY01 | WATER TRANSFER PUMP 1 (DUTY) | Emergency Stop Relay |  | SUB LINK | BPP1103LCS03 |  |  | BR4-1860-E-00072 | [9 empty] | F7 | 1 | 2 | 3 | 4
[13 empty] | BPP1104LCS04 | SY01 | WATER TRANSFER PUMP 2 (DUTY) | Emergency Stop Relay |  | SUB LINK | BPP1104LCS04 |  |  | BR4-1860-E-00073 | [9 empty] | F7 | 5 | 6 | 7 | 8
[13 empty] | BPP1105LCS05 | SY01 | WATER TRANSFER PUMP 3 (STANDBY) | Emergency Stop Relay |  | SUB LINK | BPP1105LCS05 |  |  | BR4-1860-E-00074 | [9 empty] | F7 | 9 | 10 | 11 | 12
[32 empty] | F7 | 13 | 14 | 15 | 16
[32 empty] | F7 | 17 | 18 | 19 | 20
[32 empty] | F7 | 21 | 22 | 23 | 24
[32 empty] | F7 | 25 | 26 | 27 | 28
[32 empty] | F7 | 29 | 30 | 31 | 32
[32 empty] | F7 | 33 | 34 | 35 | 36
[32 empty] | F7 | 37 | 38 | 39 | 40
[32 empty] | F7 | 41 | 42 | 43 | 44
[32 empty] | F7 | 45 | 46 | 47 | 48
BTK2101DX04 - NPI Fire Water Tank 1
EIO node #4 | DX04 | DIO1 | 131 | 2 | 4 | 0
BTK2101 | DX04 | DIO1 | 131 | 2 | 4 | 0 |  | Chassis |  | BMEXBP1200
BTK2101 | DX04 | DIO1 | 131 | 2 | 4 | 0 |  | Power |  | BMXCPS4022 |  | total |  | spare |  | % spare
BTK2101 | DX04 | DIO1 | 131 | 2 | 4 | 0 | 0 | Comms |  | BMECRA31210 | I/O1 | 40 |  | 55 |  | 137.5%
BTK2101 | DX04 | DIO1 | 131 | 2 | 4 | 0 | 1 | 0 | BMXFCW303 | BMXDDI3202K | DI | 2 | BTK2101DX04 | CB01 |  | 240VAC Circuit Breaker | Closed | Q106 | BTK2101DX04 |  | 2.4\0.1:0 | BR4-1860-E-00103 |  |  | D | [6 empty] | F1 |  | 1
BTK2101 | DX04 | DIO1 | 131 | 2 | 4 | 0 | 1 | 1 |  |  | DI | 2 | BTK2101DX04 | VDC01 |  | 24VDC Output Control Supply | Healthy | Q143 | BTK2101DX04 |  | 2.4\0.1:1 | BR4-1860-E-00103 |  |  | D | [6 empty] | F1 |  | 2
BTK2101 | DX04 | DIO1 | 131 | 2 | 4 | 0 | 1 | 2 |  |  | DI | 2 | BTK2101DX04 | VDC02 |  | 24VDC GW1 Control Supply | Healthy | Q157 | BTK2101DX04 |  | 2.4\0.1:2 | BR4-1860-E-00103 |  |  | D | [6 empty] | F1 |  | 3
BTK2101 | DX04 | DIO1 | 131 | 2 | 4 | 0 | 1 | 3 |  |  | DI | 2 | BTK2101DX04 | VDC03 |  | 24VDC Instrument Control Supply | Healthy | Q164 | BTK2101DX04 |  | 2.4\0.1:3 | BR4-1860-E-00103 |  |  | D | [6 empty] | F1 |  | 4
BTK2101 | DX04 | DIO1 | 131 | 2 | 4 | 0 | 1 | 4 |  |  | DI | 2 | BTK2101DX04 | VDC04 |  | 24VDC Transmitter Control Supply | Healthy | Q168 | BTK2101DX04 |  | 2.4\0.1:4 | BR4-1860-E-00103 |  |  | D | [6 empty] | F1 |  | 5
BTK2101 | DX04 | DIO1 | 131 | 2 | 4 | 0 | 1 | 5 |  |  | DI | 2 | BTK2101DX04 | VDC05 |  | 24VDC BTK2101DX04 Control Supply | Healthy | Q172 | BTK2101DX04 |  | 2.4\0.1:5 | BR4-1860-E-00103 |  |  | D | [6 empty] | F1 |  | 6
BTK2101 | DX04 | DIO1 | 131 | 2 | 4 | 0 | 1 | 6 |  |  | DI | 2 | BTK2101DX04 | VDC06 |  | 24VDC Spare Control Supply | Healthy | Q176 | BTK2101DX04 |  | 2.4\0.1:6 | BR4-1860-E-00103 |  |  | D | [6 empty] | F1 |  | 7
BTK2101 | DX04 | DIO1 | 131 | 2 | 4 | 0 | 1 | 7 |  |  | DI | 2 | BTK2101DX04 | VDC07 |  | 24VDC Spare Control Supply | Healthy | Q180 | BTK2101DX04 |  | 2.4\0.1:7 | BR4-1860-E-00103 |  |  | D | [6 empty] | F1 |  | 8
BTK2101 | DX04 | DIO1 | 131 | 2 | 4 | 0 | 1 | 8 |  |  | DI | 2 | BTK2101DX04 | VDC08 |  | 24VDC Spare Control Supply | Healthy | Q184 | BTK2101DX04 |  | 2.4\0.1:8 | BR4-1860-E-00103 |  |  | D | [6 empty] | F1 |  | 9
BTK2101 | DX04 | DIO1 | 131 | 2 | 4 | 0 | 1 | 9 |  |  | DI | 2 | BTK2101DX04 | VDC09 |  | 24VDC Spare Control Supply | Healthy | Q188 | BTK2101DX04 |  | 2.4\0.1:9 | BR4-1860-E-00103 |  |  | D | [6 empty] | F1 |  | 10
BTK2101 | DX04 | DIO1 | 131 | 2 | 4 | 0 | 1 | 10 |  |  | DI | 2 | BTK2101DX04 | VDC10 |  | 24VDC Spare Control Supply | Healthy | Q192 | BTK2101DX04 |  | 2.4\0.1:10 | BR4-1860-E-00103 |  |  | D | [6 empty] | F1 |  | 11
BTK2101 | DX04 | DIO1 | 131 | 2 | 4 | 0 | 1 | 11 |  |  | DI | 2 | BTK2101DX04 | VDC11 |  | 24VDC Spare Control Supply | Healthy | Q196 | BTK2101DX04 |  | 2.4\0.1:11 | BR4-1860-E-00103 |  |  | D | [6 empty] | F1 |  | 12
BTK2101 | DX04 | DIO1 | 131 | 2 | 4 | 0 | 1 | 12 |  |  | DI | [9 empty] | 2.4\0.1:12 |  |  |  | S | [6 empty] | F1 |  | 13
BTK2101 | DX04 | DIO1 | 131 | 2 | 4 | 0 | 1 | 13 |  |  | DI | [9 empty] | 2.4\0.1:13 |  |  |  | S | [6 empty] | F1 |  | 14
BTK2101 | DX04 | DIO1 | 131 | 2 | 4 | 0 | 1 | 14 |  |  | DI | [9 empty] | 2.4\0.1:14 |  |  |  | S | [6 empty] | F1 |  | 15
BTK2101 | DX04 | DIO1 | 131 | 2 | 4 | 0 | 1 | 15 |  |  | DI | [9 empty] | 2.4\0.1:15 |  |  |  | S | [6 empty] | F1 |  | 16
BTK2101 | DX04 | DIO1 | 131 | 2 | 4 | 0 | 1 | 16 |  |  | DI | 2 | BPP1101FIT01 | FQ01 | FIREWATER TANKS | Flow Totaliser | Pulse |  | BPP1101 |  | 2.4\0.1:16 | BR4-1860-E-00104 | 0 |  | S | [6 empty] | F1 | 17 | 18
BTK2101 | DX04 | DIO1 | 131 | 2 | 4 | 0 | 1 | 17 |  |  | DI | 2 | BPP1101FIT02 | FQ02 | HME WORKSHOP/WASHDOWN/TYRE CHANGE/REFUELLING | Flow Totaliser | Pulse |  | BPP1101 |  | 2.4\0.1:17 | BR4-1860-E-00104 | 0 |  | S | [6 empty] | F1 | 19 | 20
BTK2101 | DX04 | DIO1 | 131 | 2 | 4 | 0 | 1 | 18 |  |  | DI | 4 | BTK2101FIP01 | XS01 | FIRE WATER PUMP SKID | Fire Panel Fault | Healthy |  | BTK2101FIP01 |  | 2.4\0.1:18 |  |  | JIMMY Removed 6/8/2026. Hardwired signals no longer required. Will be sent to ESO and read by SCADA via modbus comms | S | [6 empty] | F1 | 21 | 22
BTK2101 | DX04 | DIO1 | 131 | 2 | 4 | 0 | 1 | 19 |  |  | DI | 4 | BTK2101FIP01 | IS01 | FIRE WATER PUMP SKID | Fire Panel Isolated | Healthy |  | BTK2101FIP01 |  | 2.4\0.1:19 |  |  | JIMMY Removed 6/8/2026. Hardwired signals no longer required. Will be sent to ESO and read by SCADA via modbus comms | S | [6 empty] | F1 | 23 | 24
BTK2101 | DX04 | DIO1 | 131 | 2 | 4 | 0 | 1 | 20 |  |  | DI | 4 | BTK2101FIP01 | XS02 | FIRE WATER PUMP SKID | Fire Alarm | Healthy |  | BTK2101FIP01 |  | 2.4\0.1:20 |  |  | JIMMY Removed 6/8/2026. Hardwired signals no longer required. Will be sent to ESO and read by SCADA via modbus comms | S | [6 empty] | F1 | 25 | 26
BTK2101 | DX04 | DIO1 | 131 | 2 | 4 | 0 | 1 | 21 |  |  | DI | 2 | [8 empty] | 2.4\0.1:21 |  |  |  | S | [6 empty] | F1 | 27 | 28
BTK2101 | DX04 | DIO1 | 131 | 2 | 4 | 0 | 1 | 22 |  |  | DI | 2 | [8 empty] | 2.4\0.1:22 |  |  |  | S | [6 empty] | F1 | 29 | 30
BTK2101 | DX04 | DIO1 | 131 | 2 | 4 | 0 | 1 | 23 |  |  | DI | 2 | [8 empty] | 2.4\0.1:23 |  |  |  | S | [6 empty] | F1 | 31 | 32
BTK2101 | DX04 | DIO1 | 131 | 2 | 4 | 0 | 1 | 24 |  |  | DI | 2 | [8 empty] | 2.4\0.1:24 |  |  |  | S | [6 empty] | F1 | 33 | 34
BTK2101 | DX04 | DIO1 | 131 | 2 | 4 | 0 | 1 | 25 |  |  | DI | 2 | [8 empty] | 2.4\0.1:25 |  |  |  | S | [6 empty] | F1 | 35 | 36
BTK2101 | DX04 | DIO1 | 131 | 2 | 4 | 0 | 1 | 26 |  |  | DI | 2 | [8 empty] | 2.4\0.1:26 |  |  |  | S | [6 empty] | F1 | 37 | 38
BTK2101 | DX04 | DIO1 | 131 | 2 | 4 | 0 | 1 | 27 |  |  | DI | 2 | [8 empty] | 2.4\0.1:27 |  |  |  | S | [6 empty] | F1 | 39 | 40
BTK2101 | DX04 | DIO1 | 131 | 2 | 4 | 0 | 1 | 28 |  |  | DI | 2 | [8 empty] | 2.4\0.1:28 |  |  |  | S | [6 empty] | F1 | 41 | 42
BTK2101 | DX04 | DIO1 | 131 | 2 | 4 | 0 | 1 | 29 |  |  | DI | 2 | [8 empty] | 2.4\0.1:29 |  |  |  | S | [6 empty] | F1 | 43 | 44
BTK2101 | DX04 | DIO1 | 131 | 2 | 4 | 0 | 1 | 30 |  |  | DI | [9 empty] | 2.4\0.1:30 |  |  |  | S | [6 empty] | F1 | 45 | 46
BTK2101 | DX04 | DIO1 | 131 | 2 | 4 | 0 | 1 | 31 |  |  | DI | [9 empty] | 2.4\0.1:31 |  |  |  | S | [6 empty] | F1 | 47 | 48
BTK2101 | DX04 | DIO1 | 131 | 2 | 4 | 0 | 2 |  |  | BMXXEM010 | [10 empty] | 2.4\0.2:
BTK2101 | DX04 | DIO1 | 131 | 2 | 4 | 0 | 2 | [13 empty] | 2.4\0.2:
BTK2101 | DX04 | DIO1 | 131 | 2 | 4 | 0 | 2 | [13 empty] | 2.4\0.2:
BTK2101 | DX04 | DIO1 | 131 | 2 | 4 | 0 | 2 | [13 empty] | 2.4\0.2:
BTK2101 | DX04 | DIO1 | 131 | 2 | 4 | 0 | 3 | 0 | BMXFTW301S | BMEAHI0812 | AI | 2 | BTK2101LIT01 | LT01 | NPI FIRE WATER TANK 1 | Tank Level |  | % | BTK2101 | REAL | 2.4\0.3:0 | BR4-1860-E-00104 | 0 | Located in BTK2101DX04 | S |  | 0 | 100 | 0 | 100 | #.# EU | F5 | 1 | 2
BTK2101 | DX04 | DIO1 | 131 | 2 | 4 | 0 | 3 | 1 |  |  | AI | 2 | BTK2102LIT01 | LT01 | NPI FIRE WATER TANK 2 | Tank Level |  | % | BTK2102 | REAL | 2.4\0.3:1 | BR4-1860-E-00104 | 0 | Located in BTK2101DX04 | S |  | 0 | 100 | 0 | 100 | #.# EU | F5 | 3 | 4
BTK2101 | DX04 | DIO1 | 131 | 2 | 4 | 0 | 3 | 2 |  |  | AI | [9 empty] | 2.4\0.3:2 |  |  |  | S |  | 0 | 100 | 0 | 100 | #.# EU | F5 | 5 | 6
BTK2101 | DX04 | DIO1 | 131 | 2 | 4 | 0 | 3 | 3 |  |  | AI | [9 empty] | 2.4\0.3:3 |  |  |  | S |  | 0 | 100 | 0 | 100 | #.# EU | F5 | 7 | 8
BTK2101 | DX04 | DIO1 | 131 | 2 | 4 | 0 | 3 | 4 |  |  | AI | [9 empty] | 2.4\0.3:4 |  |  |  | S |  | 0 | 100 | 0 | 100 | #.# EU | F5 | 9 | 10
BTK2101 | DX04 | DIO1 | 131 | 2 | 4 | 0 | 3 | 5 |  |  | AI | [9 empty] | 2.4\0.3:5 |  |  |  | S |  | 0 | 100 | 0 | 100 | #.# EU | F5 | 11 | 12
BTK2101 | DX04 | DIO1 | 131 | 2 | 4 | 0 | 3 | 6 |  |  | AI | 2 | BPP1101FIT01 | FT01 | FIRE WATER TANKS | Flow Rate |  | m3/h | BPP1101 | REAL | 2.4\0.3:6 | BR4-1860-E-00104 | 0 | Located in BTK2101DX04 | S |  | 0 | 400 | 0 | 400 | # EU | F5 | 13 | 14
BTK2101 | DX04 | DIO1 | 131 | 2 | 4 | 0 | 3 | 7 |  |  | AI | 2 | BPP1101FIT02 | FT02 | HME WORKSHOP/WASHDOWN/TYRE CHANGE/REFUELLING | Flow Rate |  | m3/h | BPP1101 | REAL | 2.4\0.3:7 | BR4-1860-E-00104 | 0 | Located in BTK2101DX04 | S |  | 0 | 400 | 0 | 400 | # EU | F5 | 15 | 16
BTK2101 | DX04 | DIO1 | 131 | 2 | 4 | 0 | 4 |  |  | BMXXEM010 | [10 empty] | 2.4\0.4:
BTK2101 | DX04 | DIO1 | 131 | 2 | 4 | 0 | 4 | [13 empty] | 2.4\0.4:
BTK2101 | DX04 | DIO1 | 131 | 2 | 4 | 0 | 4 | [13 empty] | 2.4\0.4:
BTK2101 | DX04 | DIO1 | 131 | 2 | 4 | 0 | 4 | [13 empty] | 2.4\0.4:
BTK2101 | DX04 | DIO1 | 131 | 2 | 4 | 0 | 5 |  |  | BMXXEM010 | [10 empty] | 2.4\0.5:
BTK2101 | DX04 | DIO1 | 131 | 2 | 4 | 0 | 5 | [13 empty] | 2.4\0.5:
BTK2101 | DX04 | DIO1 | 131 | 2 | 4 | 0 | 5 | [13 empty] | 2.4\0.5:
BTK2101 | DX04 | DIO1 | 131 | 2 | 4 | 0 | 5 | [13 empty] | 2.4\0.5:
BTK2101 | DX04 | DIO1 | 131 | #REF! | #REF! | 0 | 6 |  |  | BMXXEM010 | [10 empty] | #REF!
BTK2101 | DX04 | DIO1 | 131 | #REF! | #REF! | 0 | 6 | [13 empty] | #REF!
BTK2101 | DX04 | DIO1 | 131 | #REF! | #REF! | 0 | 6 | [13 empty] | #REF!
BTK2101 | DX04 | DIO1 | 131 | #REF! | #REF! | 0 | 6 | [13 empty] | #REF!
BTK2101 | DX04 | DIO1 | 131 | #REF! | #REF! | 0 | 7 |  |  | BMXXEM010 | [10 empty] | #REF!
BTK2101 | DX04 | DIO1 | 131 | #REF! | #REF! | 0 | 7 | [13 empty] | #REF!
BTK2101 | DX04 | DIO1 | 131 | #REF! | #REF! | 0 | 7 | [13 empty] | #REF!
BTK2101 | DX04 | DIO1 | 131 | #REF! | #REF! | 0 | 7 | [13 empty] | #REF!
BTK2101 | DX04 | DIO1 | 131 | #REF! | #REF! | 0 | 8 |  |  | BMXXEM010 | [10 empty] | #REF!
BTK2101 | DX04 | DIO1 | 131 | #REF! | #REF! | 0 | 8 | [13 empty] | #REF!
BTK2101 | DX04 | DIO1 | 131 | #REF! | #REF! | 0 | 8 | [13 empty] | #REF!
BTK2101 | DX04 | DIO1 | 131 | #REF! | #REF! | 0 | 8 | [13 empty] | #REF!
BTK2101 | DX04 | DIO1 | 131 | #REF! | #REF! | 0 | 9 |  |  | BMXXEM010 | [10 empty] | #REF!
BTK2101 | DX04 | DIO1 | 131 | #REF! | #REF! | 0 | 9 | [13 empty] | #REF!
BTK2101 | DX04 | DIO1 | 131 | #REF! | #REF! | 0 | 9 | [13 empty] | #REF!
BTK2101 | DX04 | DIO1 | 131 | #REF! | #REF! | 0 | 9 | [13 empty] | #REF!
BTK2101 | DX04 | DIO1 | 131 | #REF! | #REF! | 0 | 10 |  |  | BMXXEM010 | [10 empty] | #REF!
BTK2101 | DX04 | DIO1 | 131 | #REF! | #REF! | 0 | 10 | [13 empty] | #REF!
BTK2101 | DX04 | DIO1 | 131 | #REF! | #REF! | 0 | 10 | [13 empty] | #REF!
BTK2101 | DX04 | DIO1 | 131 | #REF! | #REF! | 0 | 10 | [13 empty] | #REF!
BTK2101 | DX04 | DIO1 | 131 | #REF! | #REF! | 0 | 11 |  |  | BMXXEM010 | [10 empty] | #REF!
BTK2101 | DX04 | DIO1 | 131 | #REF! | #REF! | 0 | 11 | [13 empty] | #REF!
BTK2101 | DX04 | DIO1 | 131 | #REF! | #REF! | 0 | 11 | [13 empty] | #REF!
BTK2101 | DX04 | DIO1 | 131 | #REF! | #REF! | 0 | 11 | [13 empty] | #REF!
[32 empty] | F7 | 1 | 2 | 3 | 4
[32 empty] | F7 | 5 | 6 | 7 | 8
[32 empty] | F7 | 9 | 10 | 11 | 12
[32 empty] | F7 | 13 | 14 | 15 | 16
[32 empty] | F7 | 17 | 18 | 19 | 20
[32 empty] | F7 | 21 | 22 | 23 | 24
[32 empty] | F7 | 25 | 26 | 27 | 28
[32 empty] | F7 | 29 | 30 | 31 | 32
[32 empty] | F7 | 33 | 34 | 35 | 36
[32 empty] | F7 | 37 | 38 | 39 | 40
[32 empty] | F7 | 41 | 42 | 43 | 44
[32 empty] | F7 | 45 | 46 | 47 | 48