## Sub IO Assignment
Item | Box | Node | PLC | Bus | Drop | Rack | Slot | Ch | Terminal | Node Type | IO Type | CPP | Rev | Instrument Tag | Device | Instrument List Description | Desc2 | State | Location | Drive | Datatype | Address | Drawing | Rev | Notes | FAT | SAT | Raw_Zero | Raw_Full | Eng_Zero | Eng_Full | Format | TS | T1 | T2 | T3 | T4 |  |  |  | Alm_AREA | Alm_PRIV | Alm_HELP | Alm_CATEGORY | Alm_CUSTOM1 | Alm_CUSTOM2 | Alm_CUSTOM3 | Alm_CUSTOM4 | Alm_CUSTOM5 | Alm_CUSTOM6 | Alm_CUSTOM7 | Alm_CUSTOM8
BSR130DX01
BMC1322
BSR132 | DX01 | DIO0 | 132 | 0 | 0 | 0 |  | Chassis |  | BMEXBP1200
BSR132 | DX01 | DIO0 | 132 | 0 | 0 | 0 |  | Power |  | BMXCPS4022
BSR132 | DX01 | DIO0 | 132 | 0 | 0 | 0 | 0 | CPU |  | BMEP586040 | DX01ES01 | [5 empty] | BPL132
BSR132 | DX01 | DIO0 | 132 | 0 | 0 | 0 | 0A | MEM |  | BMXRMS004GPF
BSR132 | DX01 | DIO0 | 132 | 0 | 0 | 0 | 2 | Spare - X |  | BMXXEM010
BSR132 | DX01 | DIO0 | 132 | 0 | 0 | 0 | 3 | Comms |  | BMENOC0301 | C | [5 empty] | PLC Comms
BSR132 | DX01 | DIO0 | 132 | 0 | 0 | 0 | 4 | Comms |  | BMENOC0301 | N/C CAT6 | [5 empty] | HMI Comms
BSR132 | DX01 | DIO0 | 132 | 0 | 0 | 0 | 5 | Comms |  | BMENOC0301 | DX01ES01 | [5 empty] | I/O
BSR132 | DX01 | DIO0 | 132 | 0 | 0 | 0 | 6 | Spare - E&X |  | BMXXEM010
BSR132 | DX01 | DIO0 | 132 | 0 | 0 | 0 | 7 | Spare - E&X |  | BMXXEM010
BSR132 | DX01 | DIO0 | 132 | 0 | 0 | 0 | 8 | Spare - X |  | BMXXEM010
BSR132 | DX01 | DIO0 | 132 | 0 | 0 | 0 | 9 | Spare - E&X |  | BMXXEM010
BSR132 | DX01 | DIO0 | 132 | 0 | 0 | 0 | 10 | Spare - X |  | BMXXEM010
BSR132 | DX01 | DIO0 | 132 | 0 | 0 | 0 | 11 | Media Conv |  | BMXXEM010
BMC1322
EIO node 1
BSR132 | DX01 | DIO1 | 132 | 2 | 1 | 0 | 0 | Chassis |  | BMEXBP1200
BSR132 | DX01 | DIO1 | 132 | 2 | 1 | 0 | 0 | Power |  | BMXCPS4022 |  |  | total |  | spare |  | % spare
BSR132 | DX01 | DIO1 | 132 | 2 | 1 | 0 | 0 | Comms |  | BMECRA31210 | DX01ES01 |  | 304 |  | 67 |  | 22.04% |  |  |  |  | 2.1\0.0:Comms
BSR132 | DX01 | DIO1 | 132 | 2 | 1 | 0 | 1 | 0 | BMXFCW303 | BMXDDI3202K | DI |  | 3 | BSR132BC02 | VDC02 |  | Battery Charger 110VDC Tripping Supply | Healthy | K112 | BSR132BC02 |  | 2.1\0.1:0 | BR4-2150-E-00063 | A | BSR132BC02-C2 | [7 empty] | F1 | 1 | 2
BSR132 | DX01 | DIO1 | 132 | 2 | 1 | 0 | 1 | 1 |  |  | DI |  | 3 | BSR132BC02 | CB02 |  | BMC1322INC01 110VDC INC01 Tripping Supply Circuit Breaker | Closed | Q114 | BSR132BC02 |  | 2.1\0.1:1 | BR4-2150-E-00063 | A | BSR132BC02-C2 | [7 empty] | F1 | 3 | 4
BSR132 | DX01 | DIO1 | 132 | 2 | 1 | 0 | 1 | 2 |  |  | DI |  | 3 | BSR132BC02 | CB03 |  | BMC1322INC02 110VDC INC02 Tripping Supply Circuit Breaker | Closed | Q117 | BSR132BC02 |  | 2.1\0.1:2 | BR4-2150-E-00063 | A | BSR132BC02-C2 | [7 empty] | F1 | 5 | 6
BSR132 | DX01 | DIO1 | 132 | 2 | 1 | 0 | 1 | 3 |  |  | DI |  | 3 | BSR132BC02 | CB04 |  | BMC1322INC03 110VDC INC03 Tripping Supply Circuit Breaker | Closed | Q120 | BSR132BC02 |  | 2.1\0.1:3 | BR4-2150-E-00063 | A | BSR132BC02-C2 | [7 empty] | F1 | 7 | 8
BSR132 | DX01 | DIO1 | 132 | 2 | 1 | 0 | 1 | 4 |  |  | DI |  | 3 | BSR132BC02 | CB05 |  | BMC1321INC01 110VDC INC01 Tripping Supply Circuit Breaker | Closed | Q123 | BSR132BC02 |  | 2.1\0.1:4 | BR4-2150-E-00063 | A | BSR132BC02-C2 | [7 empty] | F1 | 9 | 10
BSR132 | DX01 | DIO1 | 132 | 2 | 1 | 0 | 1 | 5 |  |  | DI |  | 3 | BSR132BC02 | CB06 |  | BMC1321FDR01 110VDC FDR01 Tripping Supply Circuit Breaker | Closed | Q126 | BSR132BC02 |  | 2.1\0.1:5 | BR4-2150-E-00063 | A | BSR132BC02-C2 | [7 empty] | F1 | 11 | 12
BSR132 | DX01 | DIO1 | 132 | 2 | 1 | 0 | 1 | 6 |  |  | DI |  | 3 | BSR132BC02 | CB07 |  | BMC1321FDR02 110VDC FDR02 Tripping Supply Circuit Breaker | Closed | Q129 | BSR132BC02 |  | 2.1\0.1:6 | BR4-2150-E-00063 | A | BSR132BC02-C2 | [7 empty] | F1 | 13 | 14
BSR132 | DX01 | DIO1 | 132 | 2 | 1 | 0 | 1 | 7 |  |  | DI |  | 3 | BSR132BC02 | CB08 |  | BMC1321FDR03 110VDC FDR03 Tripping Supply Circuit Breaker | Closed | Q132 | BSR132BC02 |  | 2.1\0.1:7 | BR4-2150-E-00063 | A | BSR132BC02-C2 | [7 empty] | F1 | 15 | 16
BSR132 | DX01 | DIO1 | 132 | 2 | 1 | 0 | 1 | 8 |  |  | DI |  | 3 | BSR132BC02 | CB09 |  | BSR132RSP01 110VDC Supply Circuit Breaker | Closed | Q135 | BSR132BC02 |  | 2.1\0.1:8 | BR4-2150-E-00063 | A | BSR132BC02-C2 | [7 empty] | F1 | 17 | 18
BSR132 | DX01 | DIO1 | 132 | 2 | 1 | 0 | 1 | 9 |  |  | DI |  | 3 | BSR132BC02 | CB10 |  | BSR132RSP03 110VDC Supply Circuit Breaker | Closed | Q138 | BSR132BC02 |  | 2.1\0.1:9 | BR4-2150-E-00063 | A | BSR132BC02-C2 | [7 empty] | F1 | 19 | 20
BSR132 | DX01 | DIO1 | 132 | 2 | 1 | 0 | 1 | 10 |  |  | DI |  | 3 | BSR132BC02 | CB11 |  | Spare | Closed |  | BSR132BC02 |  | 2.1\0.1:10 | BR4-2150-E-00063 | A | BSR132BC02-C2 | [7 empty] | F1 | 21 | 22
BSR132 | DX01 | DIO1 | 132 | 2 | 1 | 0 | 1 | 11 |  |  | DI |  | 3 | BSR132BC02 | CB12 |  | Spare | Closed |  | BSR132BC02 |  | 2.1\0.1:11 | BR4-2150-E-00063 | A | BSR132BC02-C2 | [7 empty] | F1 | 23 | 24
BSR132 | DX01 | DIO1 | 132 | 2 | 1 | 0 | 1 | 12 |  |  | DI | [10 empty] | 2.1\0.1:12 | [10 empty] | F1 | 25 | 26
BSR132 | DX01 | DIO1 | 132 | 2 | 1 | 0 | 1 | 13 |  |  | DI | [10 empty] | 2.1\0.1:13 | [10 empty] | F1 | 27 | 28
BSR132 | DX01 | DIO1 | 132 | 2 | 1 | 0 | 1 | 14 |  |  | DI | [10 empty] | 2.1\0.1:14 | [10 empty] | F1 | 29 | 30
BSR132 | DX01 | DIO1 | 132 | 2 | 1 | 0 | 1 | 15 |  |  | DI | [10 empty] | 2.1\0.1:15 | [10 empty] | F1 | 31 | 32
BSR132 | DX01 | DIO1 | 132 | 2 | 1 | 0 | 1 | 16 |  |  | DI | [10 empty] | 2.1\0.1:16 | [10 empty] | F1 | 33 | 34
BSR132 | DX01 | DIO1 | 132 | 2 | 1 | 0 | 1 | 17 |  |  | DI | [10 empty] | 2.1\0.1:17 | [10 empty] | F1 | 35 | 36
BSR132 | DX01 | DIO1 | 132 | 2 | 1 | 0 | 1 | 18 |  |  | DI | [10 empty] | 2.1\0.1:18 | [10 empty] | F1 | 37 | 38
BSR132 | DX01 | DIO1 | 132 | 2 | 1 | 0 | 1 | 19 |  |  | DI | [10 empty] | 2.1\0.1:19 | [10 empty] | F1 | 39 | 40
BSR132 | DX01 | DIO1 | 132 | 2 | 1 | 0 | 1 | 20 |  |  | DI |  | 1 | BSR132UP01SW01 | XS01 |  | Surge Filter | Healthy |  | BSR132UP01 |  | 2.1\0.1:20 | BR4-2150-E-00121 | A | BSR132UP01SD01-C1 | [7 empty] | F1 | 41 | 42
BSR132 | DX01 | DIO1 | 132 | 2 | 1 | 0 | 1 | 21 |  |  | DI |  | 3 | BSR132UP01SW01 | SW01 |  | UPS Bypassed / Test | Active |  | BSR132UP01 |  | 2.1\0.1:21 | BR4-2150-E-00121 | A | BSR132UP01SW01-C2, UPDATED TO 4 PR, SCHEMATIC TO BE CREATED | [7 empty] | F1 | 43 | 44
BSR132 | DX01 | DIO1 | 132 | 2 | 1 | 0 | 1 | 22 |  |  | DI | [10 empty] | 2.1\0.1:22 | BR4-2150-E-00121 | A | BSR132UP01SW01-C2, UPDATED TO 4 PR, SCHEMATIC TO BE CREATED | [7 empty] | F1 | 45 | 46
BSR132 | DX01 | DIO1 | 132 | 2 | 1 | 0 | 1 | 23 |  |  | DI |  | 1 | BSR132UP01SW01 | ZS01 |  | UPS in Normal Mode | Active |  | BSR132UP01 |  | 2.1\0.1:23 | BR4-2150-E-00121 | A | BSR132UP01SW01-C2, UPDATED TO 4 PR, SCHEMATIC TO BE CREATED | [7 empty] | F1 | 47 | 48
BSR132 | DX01 | DIO1 | 132 | 2 | 1 | 0 | 1 | 24 |  |  | DI | [10 empty] | 2.1\0.1:24 | BR4-2150-E-00121 | A | BSR132UP01SW01-C2, UPDATED TO 4 PR, SCHEMATIC TO BE CREATED | [7 empty] | F1 | 49 | 50
BSR132 | DX01 | DIO1 | 132 | 2 | 1 | 0 | 1 | 25 |  |  | DI | [10 empty] | 2.1\0.1:25 | [10 empty] | F1 | 51 | 52
BSR132 | DX01 | DIO1 | 132 | 2 | 1 | 0 | 1 | 26 |  |  | DI | [10 empty] | 2.1\0.1:26 | [10 empty] | F1 | 53 | 54
BSR132 | DX01 | DIO1 | 132 | 2 | 1 | 0 | 1 | 27 |  |  | DI | [10 empty] | 2.1\0.1:27 | [10 empty] | F1 | 55 | 56
BSR132 | DX01 | DIO1 | 132 | 2 | 1 | 0 | 1 | 28 |  |  | DI | [10 empty] | 2.1\0.1:28 | [10 empty] | F1 | 57 | 58
BSR132 | DX01 | DIO1 | 132 | 2 | 1 | 0 | 1 | 29 |  |  | DI | [10 empty] | 2.1\0.1:29 | [10 empty] | F1 | 59 | 60
BSR132 | DX01 | DIO1 | 132 | 2 | 1 | 0 | 1 | 30 |  |  | DI | [10 empty] | 2.1\0.1:30 | [10 empty] | F1 | 61 | 62
BSR132 | DX01 | DIO1 | 132 | 2 | 1 | 0 | 1 | 31 |  |  | DI | [10 empty] | 2.1\0.1:31 | [10 empty] | F1 | 63 | 64
BSR132 | DX01 | DIO1 | 132 | 2 | 1 | 0 | 2 | 0 | BMXFCW303 | BMXDDI3202K | DI | [10 empty] | 2.1\0.2:0 | [10 empty] | F2 | 1 | 2
BSR132 | DX01 | DIO1 | 132 | 2 | 1 | 0 | 2 | 1 |  |  | DI |  | 1 | BSR132UP01DB01 | R1 |  | BSR132DX01 Primary 240VAC UPS Circuit Breaker | Closed |  | BSR132UP01DB01 |  | 2.1\0.2:1 | BR4-2150-E-00119 | A | BSR132UP01DB01-C2 | [7 empty] | F2 | 3 | 4
BSR132 | DX01 | DIO1 | 132 | 2 | 1 | 0 | 2 | 2 |  |  | DI |  | 1 | BSR132UP01DB01 | W1 |  | BSR132DX01 Secondary 240VAC UPS Circuit Breaker | Closed |  | BSR132UP01DB01 |  | 2.1\0.2:2 | BR4-2150-E-00119 | A | BSR132UP01DB01-C2 | [7 empty] | F2 | 5 | 6
BSR132 | DX01 | DIO1 | 132 | 2 | 1 | 0 | 2 | 3 |  |  | DI |  | 3 | BSR132UP01DB01 | B1 |  | BSR132NEP01 240VAC Primary UPS Circuit Breaker | Closed |  | BSR132UP01DB01 |  | 2.1\0.2:3 | BR4-2150-E-00119 | A | BSR132UP01DB01-C2 | [7 empty] | F2 | 7 | 8
BSR132 | DX01 | DIO1 | 132 | 2 | 1 | 0 | 2 | 4 |  |  | DI |  | 3 | BSR132UP01DB01 | R2 |  | BSR132NEP01 240VAC Secondary UPS Circuit Breaker | Closed |  | BSR132UP01DB01 |  | 2.1\0.2:4 | BR4-2150-E-00119 | A | BSR132UP01DB01-C2 | [7 empty] | F2 | 9 | 10
BSR132 | DX01 | DIO1 | 132 | 2 | 1 | 0 | 2 | 5 |  |  | DI |  | 1 | BSR132UP01DB01 | W2 |  | Spare | Closed |  | BSR132UP01DB01 |  | 2.1\0.2:5 | BR4-2150-E-00119 | A | BSR132UP01DB01-C2 | [7 empty] | F2 | 11 | 12
BSR132 | DX01 | DIO1 | 132 | 2 | 1 | 0 | 2 | 6 |  |  | DI |  | 3 | BSR132UP01DB01 | B2 |  | BSR132PN01 HVAC Panel 240VAC UPS Circuit Breaker | Closed |  | BSR132UP01DB01 |  | 2.1\0.2:6 | BR4-2150-E-00119 | A | BSR132UP01DB01-C2 | [7 empty] | F2 | 13 | 14
BSR132 | DX01 | DIO1 | 132 | 2 | 1 | 0 | 2 | 7 |  |  | DI |  | 1 | BSR132UP01DB01 | R3 |  | BSR132RIS01 FIC 240VAC UPS Circuit Breaker | Closed |  | BSR132UP01DB01 |  | 2.1\0.2:7 | BR4-2150-E-00119 | A | BSR132UP01DB01-C2 | [7 empty] | F2 | 15 | 16
BSR132 | DX01 | DIO1 | 132 | 2 | 1 | 0 | 2 | 8 |  |  | DI |  | 1 | BSR132UP01DB01 | W3 |  | BSR132FIP01 Fire Panel 240VAC UPS Circuit Breaker | Closed |  | BSR132UP01DB01 |  | 2.1\0.2:8 | BR4-2150-E-00119 | A | BSR132UP01DB01-C2 | [7 empty] | F2 | 17 | 18
BSR132 | DX01 | DIO1 | 132 | 2 | 1 | 0 | 2 | 9 |  |  | DI |  | 1 | BSR132UP01DB01 | B3 |  | BSR132VES01 Vesda Fire Detection Panel Breaker | Closed |  | BSR132UP01DB01 |  | 2.1\0.2:9 | BR4-2150-E-00119 | A | BSR132UP01DB01-C2 | [7 empty] | F2 | 19 | 20
BSR132 | DX01 | DIO1 | 132 | 2 | 1 | 0 | 2 | 10 |  |  | DI |  | 3 | BSR132UP01DB01 | R4 |  | BSR132ACS01 Cardax 240VAC UPS Circuit Breaker | Closed |  | BSR132UP01DB01 |  | 2.1\0.2:10 | BR4-2150-E-00119 | A | BSR132UP01DB01-C2 | [7 empty] | F2 | 21 | 22
BSR132 | DX01 | DIO1 | 132 | 2 | 1 | 0 | 2 | 11 |  |  | DI |  | 1 | BSR132UP01DB01 | W4 |  | BBD131DX03 240VAC UPS Circuit Breaker | Closed |  | BSR132UP01DB01 |  | 2.1\0.2:11 | BR4-2150-E-00119 | A | BSR132UP01DB01-C2 | [7 empty] | F2 | 23 | 24
BSR132 | DX01 | DIO1 | 132 | 2 | 1 | 0 | 2 | 12 |  |  | DI |  | 1 | BSR132UP01DB01 | B4 |  | BBD131DX04 240VAC UPS Circuit Breaker | Closed |  | BSR132UP01DB01 |  | 2.1\0.2:12 | BR4-2150-E-00119 | A | BSR132UP01DB01-C2 | [7 empty] | F2 | 25 | 26
BSR132 | DX01 | DIO1 | 132 | 2 | 1 | 0 | 2 | 13 |  |  | DI |  | 1 | BSR132UP01DB01 | R5 |  | BSR132FSS01PN01 Supression Control Panel Breaker | Closed |  | BSR132UP01DB01 |  | 2.1\0.2:13 | BR4-2150-E-00119 | A | BSR132UP01DB01-C2 | [7 empty] | F2 | 27 | 28
BSR132 | DX01 | DIO1 | 132 | 2 | 1 | 0 | 2 | 14 |  |  | DI |  | 1 | BSR132UP01DB01 | W5 |  | BBD131CTV01 240VAC UPS Circuit Breaker | Closed |  | BSR132UP01DB01 |  | 2.1\0.2:14 | BR4-2150-E-00119 | A | BSR132UP01DB01-C2 | [7 empty] | F2 | 29 | 30
BSR132 | DX01 | DIO1 | 132 | 2 | 1 | 0 | 2 | 15 |  |  | DI |  | 1 | BSR132UP01DB01 | B5 |  | BCV131WN01 240VAC UPS Circuit Breaker | Closed |  | BSR132UP01DB01 |  | 2.1\0.2:15 | BR4-2150-E-00119 | A | BSR132UP01DB01-C2 | [7 empty] | F2 | 31 | 32
BSR132 | DX01 | DIO1 | 132 | 2 | 1 | 0 | 2 | 16 |  |  | DI |  | 1 | BSR132UP01DB01 | R6 |  | BBD131DX05 240VAC UPS Circuit Breaker | Closed |  | BSR132UP01DB01 |  | 2.1\0.2:16 | BR4-2150-E-00119 | A | BSR132UP01DB01-C2 | [7 empty] | F2 | 33 | 34
BSR132 | DX01 | DIO1 | 132 | 2 | 1 | 0 | 2 | 17 |  |  | DI |  | 3 | BSR132UP01DB01 | W6 |  | BCV131AX01/DX06 240VAC UPS Circuit Breaker | Closed |  | BSR132UP01DB01 |  | 2.1\0.2:17 | BR4-2150-E-00119 | A | BSR132UP01DB01-C2 | [7 empty] | F2 | 35 | 36
BSR132 | DX01 | DIO1 | 132 | 2 | 1 | 0 | 2 | 18 |  |  | DI |  | 3 | BSR132UP01DB01 | B6 |  | BCV131AX02/DX07 240VAC UPS Circuit Breaker | Closed |  | BSR132UP01DB01 |  | 2.1\0.2:18 | BR4-2150-E-00119 | A | BSR132UP01DB01-C2 | [7 empty] | F2 | 37 | 38
BSR132 | DX01 | DIO1 | 132 | 2 | 1 | 0 | 2 | 19 |  |  | DI |  | 3 | BSR132UP01DB01 | R7 |  | BCV131FIS01 240VAC UPS Circuit Breaker | Closed |  | BSR132UP01DB01 |  | 2.1\0.2:19 | BR4-2150-E-00119 | A | BSR132UP01DB01-C2 | [7 empty] | F2 | 39 | 40
BSR132 | DX01 | DIO1 | 132 | 2 | 1 | 0 | 2 | 20 |  |  | DI |  | 3 | BSR132UP01DB01 | W7 |  | BCV131FIS02 240VAC UPS Circuit Breaker | Closed |  | BSR132UP01DB01 |  | 2.1\0.2:20 | BR4-2150-E-00119 | A | BSR132UP01DB01-C2 | [7 empty] | F2 | 41 | 42
BSR132 | DX01 | DIO1 | 132 | 2 | 1 | 0 | 2 | 21 |  |  | DI |  | 1 | BSR132UP01DB01 | B7 |  | Spare | Closed |  | BSR132UP01DB01 |  | 2.1\0.2:21 | BR4-2150-E-00119 | A | BSR132UP01DB01-C2 | [7 empty] | F2 | 43 | 44
BSR132 | DX01 | DIO1 | 132 | 2 | 1 | 0 | 2 | 22 |  |  | DI |  | 1 | BSR132UP01DB01 | R8 |  | BCV131 DX08/AX03-AX17 240VAC UPS Circuit Breaker | Closed |  | BSR132UP01DB01 |  | 2.1\0.2:22 | BR4-2150-E-00119 | A | BSR132UP01DB01-C2 | [7 empty] | F2 | 45 | 46
BSR132 | DX01 | DIO1 | 132 | 2 | 1 | 0 | 2 | 23 |  |  | DI |  | 1 | BSR132UP01DB01 | W8 |  | BCV131 AX04-AX18 240VAC UPS Circuit Breaker | Closed |  | BSR132UP01DB01 |  | 2.1\0.2:23 | BR4-2150-E-00119 | A | BSR132UP01DB01-C2 | [7 empty] | F2 | 47 | 48
BSR132 | DX01 | DIO1 | 132 | 2 | 1 | 0 | 2 | 24 |  |  | DI |  | 1 | BSR132UP01DB01 | B8 |  | Spare | Closed |  | BSR132UP01DB01 |  | 2.1\0.2:24 | BR4-2150-E-00119 | A | BSR132UP01DB01-C2 | [7 empty] | F2 | 49 | 50
BSR132 | DX01 | DIO1 | 132 | 2 | 1 | 0 | 2 | 25 |  |  | DI |  | 1 | BSR132UP01DB01 | R9 |  | BCV131AVS01 240VAC UPS Circuit Breaker | Closed |  | BSR132UP01DB01 |  | 2.1\0.2:25 | BR4-2150-E-00119 | A | BSR132UP01DB01-C2 | [7 empty] | F2 | 51 | 52
BSR132 | DX01 | DIO1 | 132 | 2 | 1 | 0 | 2 | 26 |  |  | DI |  | 1 | BSR132UP01DB01 | W9 |  | BCV131BVS01 240VAC UPS Circuit Breaker | Closed |  | BSR132UP01DB01 |  | 2.1\0.2:26 | BR4-2150-E-00119 | A | BSR132UP01DB01-C2 | [7 empty] | F2 | 53 | 54
BSR132 | DX01 | DIO1 | 132 | 2 | 1 | 0 | 2 | 27 |  |  | DI |  | 1 | BSR132UP01DB01 | B9 |  | BCV131CVS01 240VAC UPS Circuit Breaker | Closed |  | BSR132UP01DB01 |  | 2.1\0.2:27 | BR4-2150-E-00119 | A | BSR132UP01DB01-C2 | [7 empty] | F2 | 55 | 56
BSR132 | DX01 | DIO1 | 132 | 2 | 1 | 0 | 2 | 28 |  |  | DI |  | 3 | BSR132UP01DB01 | R10 |  | Spare | Closed |  | BSR132UP01DB01 |  | 2.1\0.2:28 | BR4-2150-E-00119 | A | [8 empty] | F2 | 57 | 58
BSR132 | DX01 | DIO1 | 132 | 2 | 1 | 0 | 2 | 29 |  |  | DI |  | 3 | BSR132UP01DB01 | W10 |  | Spare | Closed |  | BSR132UP01DB01 |  | 2.1\0.2:29 | BR4-2150-E-00119 | A | [8 empty] | F2 | 59 | 60
BSR132 | DX01 | DIO1 | 132 | 2 | 1 | 0 | 2 | 30 |  |  | DI |  | 3 | BSR132UP01DB01 | B10 |  | Spare | Closed |  | BSR132UP01DB01 |  | 2.1\0.2:30 | BR4-2150-E-00119 | A | [8 empty] | F2 | 61 | 62
BSR132 | DX01 | DIO1 | 132 | 2 | 1 | 0 | 2 | 31 |  |  | DI | [10 empty] | 2.1\0.2:31 | [10 empty] | F2 | 63 | 64
BSR132 | DX01 | DIO1 | 132 | 2 | 1 | 0 | 3 | 0 | BMXFCW303 | BMXDDI3202K | DI |  | 1 |  | PB01 |  | Shutdown Pushbutton | Healthy |  | BSR132 |  | 2.1\0.3:0 | BR4-2150-E-00120 | A | NO CABLE, BSR132PB01-C1 CREATED 1 PAIR | [7 empty] | F3 | 1 | 2
BSR132 | DX01 | DIO1 | 132 | 2 | 1 | 0 | 3 | 1 |  |  | DI |  | 3 |  | XS01 |  | 24VDC Power Supply 1 | Healthy | U103A | BSR132DX01 |  | 2.1\0.3:1 | BR4-2150-E-00120 | A | INTERNAL WIRING | [7 empty] | F3 | 3 | 4
BSR132 | DX01 | DIO1 | 132 | 2 | 1 | 0 | 3 | 2 |  |  | DI |  | 3 |  | XS02 |  | 24VDC Power Supply 2 | Healthy | U103B | BSR132DX01 |  | 2.1\0.3:2 | BR4-2150-E-00120 | A | INTERNAL WIRING | [7 empty] | F3 | 5 | 6
BSR132 | DX01 | DIO1 | 132 | 2 | 1 | 0 | 3 | 3 |  |  | DI |  | 7 |  | CB01 |  | BSR132NEP01 Primary PDU Circuit Breaker | Healthy | Q130 | BSR132NEP01 |  | 2.1\0.3:3 | BR4-2150-E-00120 | A | BSR132NEP02-C6 4 PAIR | [7 empty] | F3 | 7 | 8
BSR132 | DX01 | DIO1 | 132 | 2 | 1 | 0 | 3 | 4 |  |  | DI |  | 7 |  | CB02 |  | BSR132NEP01 Secondary PDU Circuit Breaker | Healthy | Q180 | BSR132NEP01 |  | 2.1\0.3:4 | BR4-2150-E-00120 | A | BSR132NEP02-C6 4 PAIR | [7 empty] | F3 | 9 | 10
BSR132 | DX01 | DIO1 | 132 | 2 | 1 | 0 | 3 | 5 |  |  | DI |  | 1 |  | XS01 |  | Fire Panel | Healthy |  | BSR132FIP01 |  | 2.1\0.3:5 | BR4-2150-E-00120 | A | BSR132FIP01-C1 - Make 6 PAIR | [7 empty] | F3 | 11 | 12
BSR132 | DX01 | DIO1 | 132 | 2 | 1 | 0 | 3 | 6 |  |  | DI |  | 1 |  | IS01 |  | Fire Panel Isolator | Healthy |  | BSR132FIP01 |  | 2.1\0.3:6 | BR4-2150-E-00120 | A | BSR132FIP01-C1 - Make 6 PAIR | [7 empty] | F3 | 13 | 14
BSR132 | DX01 | DIO1 | 132 | 2 | 1 | 0 | 3 | 7 |  |  | DI |  | 1 |  | XS02 |  | Fire Panel Alarm | Healthy |  | BSR132FIP01 |  | 2.1\0.3:7 | BR4-2150-E-00120 | A | BSR132FIP01-C1 - Make 6 PAIR | [7 empty] | F3 | 15 | 16
BSR132 | DX01 | DIO1 | 132 | 2 | 1 | 0 | 3 | 8 |  |  | DI |  | 1 | BSR132PN01 | TS01 |  | Airlock Temperature | High |  | BSR132PN01 |  | 2.1\0.3:8 | BR4-2150-E-00120 | A | NO CABLE, BSR132PN01-C2 CREATED 10 PAIR | [7 empty] | F3 | 17 | 18
BSR132 | DX01 | DIO1 | 132 | 2 | 1 | 0 | 3 | 9 |  |  | DI |  | 7 | BSR132PN01 | TS02 |  | Fixed Plant Room Temperature | High |  | BSR132PN01 |  | 2.1\0.3:9 | BR4-2150-E-00120 | A | NO CABLE, BSR132PN01-C2 CREATED 10 PAIR | [7 empty] | F3 | 19 | 20
BSR132 | DX01 | DIO1 | 132 | 2 | 1 | 0 | 3 | 10 |  |  | DI |  | 1 | BSR132PN01 | PS01 |  | Switchroom Pressurisation Fan Filter | Alarm |  | BSR132PN01 |  | 2.1\0.3:10 | BR4-2150-E-00120 | A | NO CABLE, BSR132PN01-C2 CREATED 10 PAIR | [7 empty] | F3 | 21 | 22
BSR132 | DX01 | DIO1 | 132 | 2 | 1 | 0 | 3 | 11 |  |  | DI |  | 1 | BSR132PN01 | XS01 |  | Air Conditioner | Healthy |  | BSR132PN01 |  | 2.1\0.3:11 | BR4-2150-E-00120 | A | NO CABLE, BSR132PN01-C2 CREATED 10 PAIR | [7 empty] | F3 | 23 | 24
BSR132 | DX01 | DIO1 | 132 | 2 | 1 | 0 | 3 | 12 |  |  | DI |  | 1 | BSR132PN01 | XS02 |  | Air Conditioner Filter | Blocked |  | BSR132PN01 |  | 2.1\0.3:12 | BR4-2150-E-00120 | A | NO CABLE, BSR132PN01-C2 CREATED 10 PAIR | [7 empty] | F3 | 25 | 26
BSR132 | DX01 | DIO1 | 132 | 2 | 1 | 0 | 3 | 13 |  |  | DI |  | 1 | BSR132PN01 | XS03 |  | Air Conditioner 1 - HV VSD Room | Fault |  | BSR132PN01 |  | 2.1\0.3:13 | BR4-2150-E-00120 | A | NO CABLE, BSR132PN01-C2 CREATED 10 PAIR | [7 empty] | F3 | 27 | 28
BSR132 | DX01 | DIO1 | 132 | 2 | 1 | 0 | 3 | 14 |  |  | DI |  | 1 | BSR132PN01 | XS04 |  | Air Conditioner 2 - HV VSD Room | Fault |  | BSR132PN01 |  | 2.1\0.3:14 | BR4-2150-E-00120 | A | NO CABLE, BSR132PN01-C2 CREATED 10 PAIR | [7 empty] | F3 | 29 | 30
BSR132 | DX01 | DIO1 | 132 | 2 | 1 | 0 | 3 | 15 |  |  | DI |  | 1 | BSR132PN01 | XS05 |  | Air Conditioner 3 - HV VSD Room | Fault |  | BSR132PN01 |  | 2.1\0.3:15 | BR4-2150-E-00120 | A | NO CABLE, BSR132PN01-C2 CREATED 10 PAIR | [7 empty] | F3 | 31 | 32
BSR132 | DX01 | DIO1 | 132 | 2 | 1 | 0 | 3 | 16 |  |  | DI |  | 1 | BSR132PN01 | XS06 |  | Air Conditioner 7 - Airlock | Fault |  | BSR132PN01 |  | 2.1\0.3:16 | BR4-2150-E-00120 | A | NO CABLE, BSR132PN01-C2 CREATED 10 PAIR | [7 empty] | F3 | 33 | 34
BSR132 | DX01 | DIO1 | 132 | 2 | 1 | 0 | 3 | 17 |  |  | DI |  | 3 | BSR132PN01 | XS07 |  | Air Conditioner 8 - Airlock | Fault |  | BSR132PN01 |  | 2.1\0.3:17 | BR4-2150-E-00120 | A | NO CABLE, BSR132PN01-C2 CREATED 10 PAIR | [7 empty] | F3 | 35 | 36
BSR132 | DX01 | DIO1 | 132 | 2 | 1 | 0 | 3 | 18 |  |  | DI |  | 4 |  | XS01 |  | BSR132DB01 Surge Protection | Healthy | SD106 | BSR132DB01 |  | 2.1\0.3:18 | BR4-2150-E-00120 | A | BSR132DB01-C1 | [7 empty] | F3 | 37 | 38
BSR132 | DX01 | DIO1 | 132 | 2 | 1 | 0 | 3 | 19 |  |  | DI |  | 4 |  | XS01 |  | BSR132UP01DB01 Surge Protection | Healthy | SD106 | BSR132UP01DB01 |  | 2.1\0.3:19 | BR4-2150-E-00120 | A | NO CABLE? ONLY A 30 PAIR? | [7 empty] | F3 | 39 | 40
BSR132 | DX01 | DIO1 | 132 | 2 | 1 | 0 | 3 | 20 |  |  | DI |  | 4 |  | XS03 |  | Substation Gas | Discharged |  | BSR132FIP01 |  | 2.1\0.3:20 | BR4-2150-E-00120 | A | BSR132FIP01-C1 - Make 6 PAIR | [7 empty] | F3 | 41 | 42
BSR132 | DX01 | DIO1 | 132 | 2 | 1 | 0 | 3 | 21 |  |  | DI |  | 7 | BSR132PN01 | XS09 |  | Air Conditioner 9 - Fixed Plant Room | Fault |  | BSR132PN01 |  | 2.1\0.3:21 | based on Robs list of HVAC panels email 20260410 | [9 empty] | F3 | 43 | 44
BSR132 | DX01 | DIO1 | 132 | 2 | 1 | 0 | 3 | 22 |  |  | DI |  | 7 | BSR132PN01 | XS10 |  | Air Conditioner 10 - Fixed Plant Room | Fault |  | BSR132PN01 |  | 2.1\0.3:22 | BR4-2150-E-00120 | [9 empty] | F3 | 45 | 46
BSR132 | DX01 | DIO1 | 132 | 2 | 1 | 0 | 3 | 23 |  |  | DI |  | 7 | BSR132PN01 | XS11 |  | Air Conditioner 11 - Fixed Plant Room | Fault |  | BSR132PN01 |  | 2.1\0.3:23 | BR4-2150-E-00120 | [9 empty] | F3 | 47 | 48
BSR132 | DX01 | DIO1 | 132 | 2 | 1 | 0 | 3 | 24 |  |  | DI |  | 7 | BSR132PN01 | XS12 |  | Air Conditioner 12 - Fixed Plant Room | Fault |  | BSR132PN01 |  | 2.1\0.3:24 | BR4-2150-E-00120 | [9 empty] | F3 | 49 | 50
BSR132 | DX01 | DIO1 | 132 | 2 | 1 | 0 | 3 | 25 |  |  | DI |  | 7 | BSR132PN01 | XS13 |  | Air Conditioner 13 - Fixed Plant Room | Fault |  | BSR132PN01 |  | 2.1\0.3:25 | BR4-2150-E-00120 | [9 empty] | F3 | 51 | 52
BSR132 | DX01 | DIO1 | 132 | 2 | 1 | 0 | 3 | 26 |  |  | DI |  | 7 | BSR132PN01 | XS14 |  | Air Conditioner 14 - Fixed Plant Room | Fault |  | BSR132PN01 |  | 2.1\0.3:26 | BR4-2150-E-00120 | [9 empty] | F3 | 53 | 54
BSR132 | DX01 | DIO1 | 132 | 2 | 1 | 0 | 3 | 27 |  |  | DI |  | 7 | BSR132PN01 | TS03 |  | HV VSD Room Temperature Alarm | High |  | BSR132PN01 |  | 2.1\0.3:27 | BR4-2150-E-00120 | [9 empty] | F3 | 55 | 56
BSR132 | DX01 | DIO1 | 132 | 2 | 1 | 0 | 3 | 28 |  |  | DI |  | 8 | [8 empty] | 2.1\0.3:28 | [10 empty] | F3 | 57 | 58
BSR132 | DX01 | DIO1 | 132 | 2 | 1 | 0 | 3 | 29 |  |  | DI |  | 8 | [8 empty] | 2.1\0.3:29 | [10 empty] | F3 | 59 | 60
BSR132 | DX01 | DIO1 | 132 | 2 | 1 | 0 | 3 | 30 |  |  | DI | [10 empty] | 2.1\0.3:30 | [10 empty] | F3 | 61 | 62
BSR132 | DX01 | DIO1 | 132 | 2 | 1 | 0 | 3 | 31 |  |  | DI | [10 empty] | 2.1\0.3:31 | [10 empty] | F3 | 63 | 64
BSR132 | DX01 | DIO1 | 132 | 2 | 1 | 0 | 4 | 0 | BMXFCW303 | BMXDDI3202K | DI |  | 3 | BMC1322INC01 | VDC01 |  | BMC1322INC01 24VDC Control Supply | Healthy | Q267 | BMC1322INC01 |  | 2.1\0.4:0 | BR4-2150-E-00084 | A | BMC1322INC01-C1 12 PAIR, ONLY NEED 9 PAIR, MAKE 10 PAIR | [7 empty] | F4 | 1 | 2
BSR132 | DX01 | DIO1 | 132 | 2 | 1 | 0 | 4 | 1 |  |  | DI |  | 3 |  | CB02 |  | BMC1322INC01 Arc Flash Supply | Healthy | Q204 | BMC1322INC01 |  | 2.1\0.4:1 | BR4-2150-E-00084 | A | BMC1322INC01-C1 12 PAIR, ONLY NEED 9 PAIR, MAKE 10 PAIR | [7 empty] | F4 | 3 | 4
BSR132 | DX01 | DIO1 | 132 | 2 | 1 | 0 | 4 | 2 |  |  | DI |  | 3 |  | TRP02 |  | BMC1322INC01 Arc Flash | Trip | F113 | BMC1322INC01 |  | 2.1\0.4:2 | BR4-2150-E-00084 | A | BMC1322INC01-C1 12 PAIR, ONLY NEED 9 PAIR, MAKE 10 PAIR | [7 empty] | F4 | 5 | 6
BSR132 | DX01 | DIO1 | 132 | 2 | 1 | 0 | 4 | 3 |  |  | DI |  | 3 |  | XS02 |  | BMC1322INC01 Arc Flash Relay Self Supervision | Healthy | F113 | BMC1322INC01 |  | 2.1\0.4:3 | BR4-2150-E-00084 | A | BMC1322INC01-C1 12 PAIR, ONLY NEED 9 PAIR, MAKE 10 PAIR | [7 empty] | F4 | 7 | 8
BSR132 | DX01 | DIO1 | 132 | 2 | 1 | 0 | 4 | 4 |  |  | DI |  | 3 |  | CB03 |  | BMC1322INC01 Spring Charge Supply | Healthy | Q212 | BMC1322INC01 |  | 2.1\0.4:4 | BR4-2150-E-00084 | A | BMC1322INC01-C1 12 PAIR, ONLY NEED 9 PAIR, MAKE 10 PAIR | [7 empty] | F4 | 9 | 10
BSR132 | DX01 | DIO1 | 132 | 2 | 1 | 0 | 4 | 5 |  |  | DI |  | 3 |  | CB04 |  | BMC1322INC01 Trip Supply | Healthy | Q220 | BMC1322INC01 |  | 2.1\0.4:5 | BR4-2150-E-00084 | A | BMC1322INC01-C1 12 PAIR, ONLY NEED 9 PAIR, MAKE 10 PAIR | [7 empty] | F4 | 11 | 12
BSR132 | DX01 | DIO1 | 132 | 2 | 1 | 0 | 4 | 6 |  |  | DI |  | 3 |  | CB05 |  | BMC1322INC01 24VDC Cubicle Bus Supply | Healthy | Q256 | BMC1322INC01 |  | 2.1\0.4:6 | BR4-2150-E-00084 | A | BMC1322INC01-C1 12 PAIR, ONLY NEED 9 PAIR, MAKE 10 PAIR | [7 empty] | F4 | 13 | 14
BSR132 | DX01 | DIO1 | 132 | 2 | 1 | 0 | 4 | 7 |  |  | DI |  | 3 |  | XS03 |  | BMC1322INC01 Surge Protection | Healthy |  | BMC1322INC01 |  | 2.1\0.4:7 | BR4-2150-E-00084 | A | BMC1322INC01-C1 12 PAIR, ONLY NEED 9 PAIR, MAKE 10 PAIR | [7 empty] | F4 | 15 | 16
BSR132 | DX01 | DIO1 | 132 | 2 | 1 | 0 | 4 | 8 |  |  | DI |  | 3 |  | CB06 |  | BMC1322INC01 110/24VDC Power Supply | Healthy | Q215 | BMC1322INC01 |  | 2.1\0.4:8 | BR4-2150-E-00084 | A | BMC1322INC01-C1 12 PAIR, ONLY NEED 9 PAIR, MAKE 10 PAIR | [7 empty] | F4 | 17 | 18
BSR132 | DX01 | DIO1 | 132 | 2 | 1 | 0 | 4 | 9 |  |  | DI |  | 3 |  | TRP03 |  | BMC1322INC01 Upstream Intertrip | Active | K294 | BMC1322INC01 |  | 2.1\0.4:9 | BR4-2150-E-00084 | A | BMC1322INC01-C1 12 PAIR, ONLY NEED 9 PAIR, MAKE 10 PAIR | [7 empty] | F4 | 19 | 20
BSR132 | DX01 | DIO1 | 132 | 2 | 1 | 0 | 4 | 10 |  |  | DI |  | 3 | BMC1322INC02 | VDC01 |  | BMC1322 Essential Bus 24VDC Control Supply | Healthy | Q267 | BMC1322INC02 |  | 2.1\0.4:10 | BR4-2150-E-00086 | A | BMC1322INC02-C1 8 PAIR, ONLY NEED 5 PAIR MAKE 8 PAIR | [7 empty] | F4 | 21 | 22
BSR132 | DX01 | DIO1 | 132 | 2 | 1 | 0 | 4 | 11 |  |  | DI |  | 3 |  | CB03 |  | BMC1322 Essential Bus Spring Charge Supply | Healthy | Q212 | BMC1322INC02 |  | 2.1\0.4:11 | BR4-2150-E-00086 | A | BMC1322INC02-C1 8 PAIR, ONLY NEED 5 PAIR MAKE 8 PAIR | [7 empty] | F4 | 23 | 24
BSR132 | DX01 | DIO1 | 132 | 2 | 1 | 0 | 4 | 12 |  |  | DI |  | 3 |  | CB04 |  | BMC1322 Essential Bus Trip Supply | Healthy | Q220 | BMC1322INC02 |  | 2.1\0.4:12 | BR4-2150-E-00086 | A | BMC1322INC02-C1 8 PAIR, ONLY NEED 5 PAIR MAKE 8 PAIR | [7 empty] | F4 | 25 | 26
BSR132 | DX01 | DIO1 | 132 | 2 | 1 | 0 | 4 | 13 |  |  | DI |  | 3 |  | CB05 |  | BMC1322 Essential Bus 24VDC Cubicle Bus Supply | Healthy | Q256 | BMC1322INC02 |  | 2.1\0.4:13 | BR4-2150-E-00086 | A | BMC1322INC02-C1 8 PAIR, ONLY NEED 5 PAIR MAKE 8 PAIR | [7 empty] | F4 | 27 | 28
BSR132 | DX01 | DIO1 | 132 | 2 | 1 | 0 | 4 | 14 |  |  | DI |  | 3 |  | XS03 |  | BMC1322 Essential Bus Surge Protection | Healthy |  | BMC1322INC02 |  | 2.1\0.4:14 | BR4-2150-E-00086 | A | BMC1322INC02-C1 8 PAIR, ONLY NEED 5 PAIR MAKE 8 PAIR | [7 empty] | F4 | 29 | 30
BSR132 | DX01 | DIO1 | 132 | 2 | 1 | 0 | 4 | 15 |  |  | DI |  | 3 |  | CB06 |  | BMC1322 Essential Bus 110/24VDC Power Supply | Healthy | Q215 | BMC1322INC02 |  | 2.1\0.4:15 | BR4-2150-E-00086 | A | BMC1322INC02-C1 8 PAIR, ONLY NEED 5 PAIR MAKE 8 PAIR | [7 empty] | F4 | 31 | 32
BSR132 | DX01 | DIO1 | 132 | 2 | 1 | 0 | 4 | 16 |  |  | DI |  | 3 | BMC1322INC03 | VDC01 |  | BMC1322INC03 24VDC Control Supply | Healthy | Q267 | BMC1322INC03 |  | 2.1\0.4:16 | BR4-2150-E-00088 | A | BMC1322INC03-C1 10 PAIR, ONLY NEED 6 PAIR MAKE 8 PAIR | [7 empty] | F4 | 33 | 34
BSR132 | DX01 | DIO1 | 132 | 2 | 1 | 0 | 4 | 17 |  |  | DI |  | 3 |  | TRP02 |  | BMC1322INC03 Arc Flash | Trip | F110 | BMC1322INC03 |  | 2.1\0.4:17 | BR4-2150-E-00088 | A | BMC1322INC03-C1 10 PAIR, ONLY NEED 6 PAIR MAKE 8 PAIR | [7 empty] | F4 | 35 | 36
BSR132 | DX01 | DIO1 | 132 | 2 | 1 | 0 | 4 | 18 |  |  | DI |  | 3 |  | CB03 |  | BMC1322INC03 Spring Charge Supply | Healthy | Q212 | BMC1322INC03 |  | 2.1\0.4:18 | BR4-2150-E-00088 | A | BMC1322INC03-C1 10 PAIR, ONLY NEED 6 PAIR MAKE 8 PAIR | [7 empty] | F4 | 37 | 38
BSR132 | DX01 | DIO1 | 132 | 2 | 1 | 0 | 4 | 19 |  |  | DI |  | 3 |  | CB04 |  | BMC1322INC03 Trip Supply | Healthy | Q220 | BMC1322INC03 |  | 2.1\0.4:19 | BR4-2150-E-00088 | A | BMC1322INC03-C1 10 PAIR, ONLY NEED 6 PAIR MAKE 8 PAIR | [7 empty] | F4 | 39 | 40
BSR132 | DX01 | DIO1 | 132 | 2 | 1 | 0 | 4 | 20 |  |  | DI |  | 3 |  | CB05 |  | BMC1322INC03 24VDC Cubicle Bus Supply | Healthy | Q256 | BMC1322INC03 |  | 2.1\0.4:20 | BR4-2150-E-00088 | A | BMC1322INC03-C1 10 PAIR, ONLY NEED 6 PAIR MAKE 8 PAIR | [7 empty] | F4 | 41 | 42
BSR132 | DX01 | DIO1 | 132 | 2 | 1 | 0 | 4 | 21 |  |  | DI |  | 3 |  | CB06 |  | BMC1322INC03 Arc Flash Expansion Module 24VDC Supply | Healthy | Q258 | BMC1322INC03 |  | 2.1\0.4:21 | BR4-2150-E-00088 | A | BMC1322INC03-C1 10 PAIR, ONLY NEED 6 PAIR MAKE 8 PAIR | [7 empty] | F4 | 43 | 44
BSR132 | DX01 | DIO1 | 132 | 2 | 1 | 0 | 4 | 22 |  |  | DI |  | 3 |  | CB07 |  | BMC1322INC03 110/24VDC Power Supply | Healthy | Q215 | BMC1322INC03 |  | 2.1\0.4:22 | BR4-2150-E-00088 | A | BMC1322INC03-C1 10 PAIR, ONLY NEED 6 PAIR MAKE 8 PAIR | [7 empty] | F4 | 45 | 46
BSR132 | DX01 | DIO1 | 132 | 2 | 1 | 0 | 4 | 23 |  |  | DI | [21 empty] | F4 | 47 | 48
BSR132 | DX01 | DIO1 | 132 | 2 | 1 | 0 | 4 | 24 |  |  | DI | [21 empty] | F4 | 49 | 50
BSR132 | DX01 | DIO1 | 132 | 2 | 1 | 0 | 4 | 25 |  |  | DI | [21 empty] | F4 | 51 | 52
BSR132 | DX01 | DIO1 | 132 | 2 | 1 | 0 | 4 | 26 |  |  | DI |  |  | all via comms | [18 empty] | F4 | 53 | 54
BSR132 | DX01 | DIO1 | 132 | 2 | 1 | 0 | 4 | 27 |  |  | DI | [21 empty] | F4 | 55 | 56
BSR132 | DX01 | DIO1 | 132 | 2 | 1 | 0 | 4 | 28 |  |  | DI | [21 empty] | F4 | 57 | 58
BSR132 | DX01 | DIO1 | 132 | 2 | 1 | 0 | 4 | 29 |  |  | DI | [21 empty] | F4 | 59 | 60
BSR132 | DX01 | DIO1 | 132 | 2 | 1 | 0 | 4 | 30 |  |  | DI | [21 empty] | F4 | 61 | 62
BSR132 | DX01 | DIO1 | 132 | 2 | 1 | 0 | 4 | 31 |  |  | DI | [21 empty] | F4 | 63 | 64
BSR132 | DX01 | DIO1 | 132 | 2 | 1 | 0 | 5 | 0 | BMXFCW303 | BMXDDI3202K | DI |  | 3 | BSR132BC01 | VDC01 |  | 24VDC Control Supply | Healthy | Q155 | BSR132BC01 |  | 2.1\0.5:0 | BR4-2150-E-00064 | A | BSR132BC01-C1 2 PAIR | [7 empty] | F5 | 1 | 2
BSR132 | DX01 | DIO1 | 132 | 2 | 1 | 0 | 5 | 1 |  |  | DI |  | 3 | BSR132BC01 | CB01 |  | Main Circuit Breaker | Closed | Q103 | BSR132BC01 |  | 2.1\0.5:1 | BR4-2150-E-00064 | A | BSR132BC01-C1 2 PAIR | [7 empty] | F5 | 3 | 4
BSR132 | DX01 | DIO1 | 132 | 2 | 1 | 0 | 5 | 2 |  |  | DI |  | 3 | BSR132BC01 | TRP01 |  | Main Circuit Breaker | Tripped | Q103 | BSR132BC01 |  | 2.1\0.5:2 | BR4-2150-E-00064 | A | BSR132BC01-C1 2 PAIR | [7 empty] | F5 | 5 | 6
BSR132 | DX01 | DIO1 | 132 | 2 | 1 | 0 | 5 | 3 |  |  | DI |  | 3 | BSR132BC02 | VDC01 |  | 24VDC Control Supply | Healthy | Q155 | BSR132BC02 |  | 2.1\0.5:3 | BR4-2150-E-00065 | A | BSR132BC02-C1 2 PAIR | [7 empty] | F5 | 7 | 8
BSR132 | DX01 | DIO1 | 132 | 2 | 1 | 0 | 5 | 4 |  |  | DI |  | 3 | BSR132BC02 | CB01 |  | Main Circuit Breaker | Closed | Q103 | BSR132BC02 |  | 2.1\0.5:4 | BR4-2150-E-00065 | A | BSR132BC02-C1 2 PAIR | [7 empty] | F5 | 9 | 10
BSR132 | DX01 | DIO1 | 132 | 2 | 1 | 0 | 5 | 5 |  |  | DI |  | 3 | BSR132BC02 | TRP01 |  | Main Circuit Breaker | Tripped | Q103 | BSR132BC02 |  | 2.1\0.5:5 | BR4-2150-E-00065 | A | BSR132BC02-C1 2 PAIR | [7 empty] | F5 | 11 | 12
BSR132 | DX01 | DIO1 | 132 | 2 | 1 | 0 | 5 | 6 |  |  | DI |  | 3 | BSR132UP01SW01 | VDC01 |  | 24VDC Control Supply | Healthy | Q155 | BSR132UP01 |  | 2.1\0.5:6 | BR4-2150-E-00071 | A | BSR132UP01SW01-C1 2 PAIR | [7 empty] | F5 | 13 | 14
BSR132 | DX01 | DIO1 | 132 | 2 | 1 | 0 | 5 | 7 |  |  | DI |  | 3 | BSR132UP01SW01 | CB01 |  | Main Circuit Breaker | Closed | Q103 | BSR132UP01 |  | 2.1\0.5:7 | BR4-2150-E-00071 | A | BSR132UP01SW01-C1 2 PAIR | [7 empty] | F5 | 15 | 16
BSR132 | DX01 | DIO1 | 132 | 2 | 1 | 0 | 5 | 8 |  |  | DI |  | 3 | BSR132UP01SW01 | TRP01 |  | Main Circuit Breaker | Tripped | Q103 | BSR132UP01 |  | 2.1\0.5:8 | BR4-2150-E-00071 | A | BSR132UP01SW01-C1 2 PAIR | [7 empty] | F5 | 17 | 18
BSR132 | DX01 | DIO1 | 132 | 2 | 1 | 0 | 5 | 9 |  |  | DI |  | 3 | BSR132AC01 | VDC01 |  | 24VDC Control Supply | Healthy | Q155 | BSR132AC01 |  | 2.1\0.5:9 | BR4-2150-E-00066 | A | BSR132AC01-C1 2 PAIR | [7 empty] | F5 | 19 | 20
BSR132 | DX01 | DIO1 | 132 | 2 | 1 | 0 | 5 | 10 |  |  | DI |  | 3 | BSR132AC01 | CB01 |  | Main Circuit Breaker | Closed | Q103 | BSR132AC01 |  | 2.1\0.5:10 | BR4-2150-E-00066 | A | BSR132AC01-C1 2 PAIR | [7 empty] | F5 | 21 | 22
BSR132 | DX01 | DIO1 | 132 | 2 | 1 | 0 | 5 | 11 |  |  | DI |  | 3 | BSR132AC01 | TRP01 |  | Main Circuit Breaker | Tripped | Q103 | BSR132AC01 |  | 2.1\0.5:11 | BR4-2150-E-00066 | A | BSR132AC01-C1 2 PAIR | [7 empty] | F5 | 23 | 24
BSR132 | DX01 | DIO1 | 132 | 2 | 1 | 0 | 5 | 12 |  |  | DI |  | 3 | BSR132AC02 | VDC01 |  | 24VDC Control Supply | Healthy | Q155 | BSR132AC02 |  | 2.1\0.5:12 | BR4-2150-E-00067 | A | BSR132AC02-C1 2 PAIR | [7 empty] | F5 | 25 | 26
BSR132 | DX01 | DIO1 | 132 | 2 | 1 | 0 | 5 | 13 |  |  | DI |  | 3 | BSR132AC02 | CB01 |  | Main Circuit Breaker | Closed | Q103 | BSR132AC02 |  | 2.1\0.5:13 | BR4-2150-E-00067 | A | BSR132AC02-C1 2 PAIR | [7 empty] | F5 | 27 | 28
BSR132 | DX01 | DIO1 | 132 | 2 | 1 | 0 | 5 | 14 |  |  | DI |  | 3 | BSR132AC02 | TRP01 |  | Main Circuit Breaker | Tripped | Q103 | BSR132AC02 |  | 2.1\0.5:14 | BR4-2150-E-00067 | A | BSR132AC02-C1 2 PAIR | [7 empty] | F5 | 29 | 30
BSR132 | DX01 | DIO1 | 132 | 2 | 1 | 0 | 5 | 15 |  |  | DI |  | 3 | BSR132AC03 | VDC01 |  | 24VDC Control Supply | Healthy | Q155 | BSR132AC03 |  | 2.1\0.5:15 | BR4-2150-E-00068 | A | BSR132AC03-C1 2 PAIR | [7 empty] | F5 | 31 | 32
BSR132 | DX01 | DIO1 | 132 | 2 | 1 | 0 | 5 | 16 |  |  | DI |  | 3 | BSR132AC03 | CB01 |  | Main Circuit Breaker | Closed | Q103 | BSR132AC03 |  | 2.1\0.5:16 | BR4-2150-E-00068 | A | BSR132AC03-C1 2 PAIR | [7 empty] | F5 | 33 | 34
BSR132 | DX01 | DIO1 | 132 | 2 | 1 | 0 | 5 | 17 |  |  | DI |  | 3 | BSR132AC03 | TRP01 |  | Main Circuit Breaker | Tripped | Q103 | BSR132AC03 |  | 2.1\0.5:17 | BR4-2150-E-00068 | A | BSR132AC03-C1 2 PAIR | [7 empty] | F5 | 35 | 36
BSR132 | DX01 | DIO1 | 132 | 2 | 1 | 0 | 5 | 18 |  |  | DI |  | 7 |  | VDC01 |  | 24VDC Control Supply | Healthy | Q155 | Spare1 |  | 2.1\0.5:18 | BR4-2150-E-00069 | A | BSR132AC04-C1 2 PAIR | [7 empty] | F5 | 37 | 38
BSR132 | DX01 | DIO1 | 132 | 2 | 1 | 0 | 5 | 19 |  |  | DI |  | 7 |  | CB01 |  | Main Circuit Breaker | Closed | Q103 | Spare1 |  | 2.1\0.5:19 | BR4-2150-E-00069 | A | BSR132AC04-C1 2 PAIR | [7 empty] | F5 | 39 | 40
BSR132 | DX01 | DIO1 | 132 | 2 | 1 | 0 | 5 | 20 |  |  | DI |  | 7 |  | TRP01 |  | Main Circuit Breaker | Tripped | Q103 | Spare1 |  | 2.1\0.5:20 | BR4-2150-E-00069 | A | BSR132AC04-C1 2 PAIR | [7 empty] | F5 | 41 | 42
BSR132 | DX01 | DIO1 | 132 | 2 | 1 | 0 | 5 | 21 |  |  | DI |  | 7 |  | VDC01 |  | 24VDC Control Supply | Healthy | Q155 | Spare2 |  | 2.1\0.5:21 | BR4-2150-E-00070 | A | BSR132AC05-C1 2 PAIR | [7 empty] | F5 | 43 | 44
BSR132 | DX01 | DIO1 | 132 | 2 | 1 | 0 | 5 | 22 |  |  | DI |  | 7 |  | CB01 |  | Main Circuit Breaker | Closed | Q103 | Spare2 |  | 2.1\0.5:22 | BR4-2150-E-00070 | A | BSR132AC05-C1 2 PAIR | [7 empty] | F5 | 45 | 46
BSR132 | DX01 | DIO1 | 132 | 2 | 1 | 0 | 5 | 23 |  |  | DI |  | 7 |  | TRP01 |  | Main Circuit Breaker | Tripped | Q103 | Spare2 |  | 2.1\0.5:23 | BR4-2150-E-00070 | A | BSR132AC05-C1 2 PAIR | [7 empty] | F5 | 47 | 48
BSR132 | DX01 | DIO1 | 132 | 2 | 1 | 0 | 5 | 24 |  |  | DI |  | 3 | BCV131WN01PN01 | VDC01 |  | 24VDC Control Supply | Healthy | Q155 | BCV131WN01PN01 |  | 2.1\0.5:24 | BR4-2150-E-00089 | A | BCV131WN01PN01-C1 2 PAIR | [7 empty] | F5 | 49 | 50
BSR132 | DX01 | DIO1 | 132 | 2 | 1 | 0 | 5 | 25 |  |  | DI |  | 3 | BCV131WN01PN01 | CB01 |  | Main Circuit Breaker | Closed | Q103 | BCV131WN01PN01 |  | 2.1\0.5:25 | BR4-2150-E-00089 | A | BCV131WN01PN01-C1 2 PAIR | [7 empty] | F5 | 51 | 52
BSR132 | DX01 | DIO1 | 132 | 2 | 1 | 0 | 5 | 26 |  |  | DI |  | 3 | BCV131WN01PN01 | TRP01 |  | Main Circuit Breaker | Tripped | Q103 | BCV131WN01PN01 |  | 2.1\0.5:26 | BR4-2150-E-00089 | A | BCV131WN01PN01-C1 2 PAIR | [7 empty] | F5 | 53 | 54
BSR132 | DX01 | DIO1 | 132 | 2 | 1 | 0 | 5 | 27 |  |  | DI |  | 3 | BAF131HT01 | VDC01 |  | 24VDC Control Supply | Healthy | Q155 | BAF131HT01 |  | 2.1\0.5:27 | BR4-2150-E-00105 | A | BAF131HP01HT01-C1 2 PAIR | [7 empty] | F5 | 55 | 56
BSR132 | DX01 | DIO1 | 132 | 2 | 1 | 0 | 5 | 28 |  |  | DI |  | 3 | BAF131HT01 | CB01 |  | Main Circuit Breaker | Closed | Q103 | BAF131HT01 |  | 2.1\0.5:28 | BR4-2150-E-00105 | A | BAF131HP01HT01-C1 2 PAIR | [7 empty] | F5 | 57 | 58
BSR132 | DX01 | DIO1 | 132 | 2 | 1 | 0 | 5 | 29 |  |  | DI |  | 3 | BAF131HT01 | TRP01 |  | Main Circuit Breaker | Tripped | Q103 | BAF131HT01 |  | 2.1\0.5:29 | BR4-2150-E-00105 | A | BAF131HP01HT01-C1 2 PAIR | [7 empty] | F5 | 59 | 60
BSR132 | DX01 | DIO1 | 132 | 2 | 1 | 0 | 5 | 30 |  |  | DI |  | 3 | BAF131HT01 | CAX01 |  | Auxilary Contactor | Closed | K148 | BAF131HT01 |  | 2.1\0.5:30 | BR4-2150-E-00105 | A | BAF131HP01HT01-C1 2 PAIR | [7 empty] | F5 | 61 | 62
BSR132 | DX01 | DIO1 | 132 | 2 | 1 | 0 | 5 | 31 |  |  | DI | [10 empty] | 2.1\0.5:31 | [10 empty] | F5 | 63 | 64
BSR132 | DX01 | DIO1 | 132 | 2 | 1 | 0 | 6 | 0 | BMXFCW303 | BMXDDI3202K | DI |  | 3 | BSR132DB01 | VDC01 |  | 24VDC Control Supply | Healthy | Q155 | BSR132DB01 |  | 2.1\0.6:0 | BR4-2150-E-00072 | A | BSR132DB01-C1 2 PAIR | [7 empty] | F6 | 1 | 2
BSR132 | DX01 | DIO1 | 132 | 2 | 1 | 0 | 6 | 1 |  |  | DI |  | 3 | BSR132DB01 | CB01 |  | Main Circuit Breaker | Closed | Q103 | BSR132DB01 |  | 2.1\0.6:1 | BR4-2150-E-00072 | A | BSR132DB01-C1 2 PAIR | [7 empty] | F6 | 3 | 4
BSR132 | DX01 | DIO1 | 132 | 2 | 1 | 0 | 6 | 2 |  |  | DI |  | 3 | BSR132DB01 | TRP01 |  | Main Circuit Breaker | Tripped | Q103 | BSR132DB01 |  | 2.1\0.6:2 | BR4-2150-E-00072 | A | BSR132DB01-C1 2 PAIR | [7 empty] | F6 | 5 | 6
BSR132 | DX01 | DIO1 | 132 | 2 | 1 | 0 | 6 | 3 |  |  | DI |  | 3 | BSR132DB02 | VDC01 |  | 24VDC Control Supply | Healthy | Q155 | BSR132DB02 |  | 2.1\0.6:3 | BR4-2150-E-00079 | A | BSR132DB02-C1 2 PAIR | [7 empty] | F6 | 7 | 8
BSR132 | DX01 | DIO1 | 132 | 2 | 1 | 0 | 6 | 4 |  |  | DI |  | 3 | BSR132DB02 | CB01 |  | Main Circuit Breaker | Closed | Q103 | BSR132DB02 |  | 2.1\0.6:4 | BR4-2150-E-00079 | A | BSR132DB02-C1 2 PAIR | [7 empty] | F6 | 9 | 10
BSR132 | DX01 | DIO1 | 132 | 2 | 1 | 0 | 6 | 5 |  |  | DI |  | 3 | BSR132DB02 | TRP01 |  | Main Circuit Breaker | Tripped | Q103 | BSR132DB02 |  | 2.1\0.6:5 | BR4-2150-E-00079 | A | BSR132DB02-C1 2 PAIR | [7 empty] | F6 | 11 | 12
BSR132 | DX01 | DIO1 | 132 | 2 | 1 | 0 | 6 | 6 |  |  | DI |  | 3 | BSR132DB03 | VDC01 |  | 24VDC Control Supply | Healthy | Q155 | BSR132DB03 |  | 2.1\0.6:6 | BR4-2150-E-00080 | A | BSR132DB03-C1 2 PAIR | [7 empty] | F6 | 13 | 14
BSR132 | DX01 | DIO1 | 132 | 2 | 1 | 0 | 6 | 7 |  |  | DI |  | 3 | BSR132DB03 | CB01 |  | Main Circuit Breaker | Closed | Q103 | BSR132DB03 |  | 2.1\0.6:7 | BR4-2150-E-00080 | A | BSR132DB03-C1 2 PAIR | [7 empty] | F6 | 15 | 16
BSR132 | DX01 | DIO1 | 132 | 2 | 1 | 0 | 6 | 8 |  |  | DI |  | 3 | BSR132DB03 | TRP01 |  | Main Circuit Breaker | Tripped | Q103 | BSR132DB03 |  | 2.1\0.6:8 | BR4-2150-E-00080 | A | BSR132DB03-C1 2 PAIR | [7 empty] | F6 | 17 | 18
BSR132 | DX01 | DIO1 | 132 | 2 | 1 | 0 | 6 | 9 |  |  | DI |  | 3 | BPQE2106PN01 | VDC01 |  | 24VDC Control Supply | Healthy | Q155 | BPQE2106PN01 |  | 2.1\0.6:9 | BR4-2150-E-00081 | A | BPQE2106PN01-C1 2 PAIR | [7 empty] | F6 | 19 | 20
BSR132 | DX01 | DIO1 | 132 | 2 | 1 | 0 | 6 | 10 |  |  | DI |  | 3 | BPQE2106PN01 | CB01 |  | Main Circuit Breaker | Closed | Q103 | BPQE2106PN01 |  | 2.1\0.6:10 | BR4-2150-E-00081 | A | BPQE2106PN01-C1 2 PAIR | [7 empty] | F6 | 21 | 22
BSR132 | DX01 | DIO1 | 132 | 2 | 1 | 0 | 6 | 11 |  |  | DI |  | 3 | BPQE2106PN01 | TRP01 |  | Main Circuit Breaker | Tripped | Q103 | BPQE2106PN01 |  | 2.1\0.6:11 | BR4-2150-E-00081 | A | BPQE2106PN01-C1 2 PAIR | [7 empty] | F6 | 23 | 24
BSR132 | DX01 | DIO1 | 132 | 2 | 1 | 0 | 6 | 12 |  |  | DI |  | 3 | BPQE2106DB01 | VDC01 |  | 24VDC Control Supply | Healthy | Q155 | BPQE2106DB01 |  | 2.1\0.6:12 | BR4-2150-E-00082 | A | BPQE2106DB01-C1 2 PAIR | [7 empty] | F6 | 25 | 26
BSR132 | DX01 | DIO1 | 132 | 2 | 1 | 0 | 6 | 13 |  |  | DI |  | 3 | BPQE2106DB01 | CB01 |  | Main Circuit Breaker | Closed | Q103 | BPQE2106DB01 |  | 2.1\0.6:13 | BR4-2150-E-00082 | A | BPQE2106DB01-C1 2 PAIR | [7 empty] | F6 | 27 | 28
BSR132 | DX01 | DIO1 | 132 | 2 | 1 | 0 | 6 | 14 |  |  | DI |  | 3 | BPQE2106DB01 | TRP01 |  | Main Circuit Breaker | Tripped | Q103 | BPQE2106DB01 |  | 2.1\0.6:14 | BR4-2150-E-00082 | A | BPQE2106DB01-C1 2 PAIR | [7 empty] | F6 | 29 | 30
BSR132 | DX01 | DIO1 | 132 | 2 | 1 | 0 | 6 | 15 |  |  | DI | [10 empty] | 2.1\0.6:15 | [10 empty] | F6 | 31 | 32
BSR132 | DX01 | DIO1 | 132 | 2 | 1 | 0 | 6 | 16 |  |  | DI | [10 empty] | 2.1\0.6:16 | [10 empty] | F6 | 33 | 34
BSR132 | DX01 | DIO1 | 132 | 2 | 1 | 0 | 6 | 17 |  |  | DI |  | 5 | BCV131AVS01 | VDC01 |  | 24VDC Control Supply | Healthy | Q284 | BCV131AVS01PN01 |  | 2.1\0.6:17 | BR4-2150-E-00124 | 0 | [8 empty] | F6 | 35 | 36
BSR132 | DX01 | DIO1 | 132 | 2 | 1 | 0 | 6 | 18 |  |  | DI |  | 5 | BCV131AVS01 | VAC01 |  | 240VAC Control Supply | Healthy | F5 | BCV131AVS01PN01 |  | 2.1\0.6:18 | BR4-2150-E-00047 | A | BCV131AVS01-C4 2 PAIR | [7 empty] | F6 | 37 | 38
BSR132 | DX01 | DIO1 | 132 | 2 | 1 | 0 | 6 | 19 |  |  | DI |  | 5 | BCV131AVS01 | VAC02 |  | 240VAC Supply Three Posn Switch Motor Isolator | Closed | -IS1 | BCV131AVS01PN01 |  | 2.1\0.6:19 | BR4-2150-E-00047 | A | BCV131AVS01-C4 2 PAIR | [7 empty] | F6 | 39 | 40
BSR132 | DX01 | DIO1 | 132 | 2 | 1 | 0 | 6 | 20 |  |  | DI |  | 3 | [19 empty] | F6 | 41 | 42
BSR132 | DX01 | DIO1 | 132 | 2 | 1 | 0 | 6 | 21 |  |  | DI | [10 empty] | 2.1\0.6:21 | [10 empty] | F6 | 43 | 44
BSR132 | DX01 | DIO1 | 132 | 2 | 1 | 0 | 6 | 22 |  |  | DI |  | 5 | BCV131BVS01 | VDC01 |  | 24VDC Control Supply | Healthy | Q287 | BCV131BVS01PN01 |  | 2.1\0.6:22 | BR4-2150-E-00124 | 0 | [8 empty] | F6 | 45 | 46
BSR132 | DX01 | DIO1 | 132 | 2 | 1 | 0 | 6 | 23 |  |  | DI |  | 5 | BCV131BVS01 | VAC01 |  | 240VAC Control Supply | Healthy | F5 | BCV131BVS01PN01 |  | 2.1\0.6:23 | BR4-2150-E-00050 | A | BCV131BVS01-C4 2 PAIR | [7 empty] | F6 | 47 | 48
BSR132 | DX01 | DIO1 | 132 | 2 | 1 | 0 | 6 | 24 |  |  | DI |  | 5 | BCV131BVS01 | VAC02 |  | 240VAC Supply Three Posn Switch Motor Isolator | Closed | -IS1 | BCV131BVS01PN01 |  | 2.1\0.6:24 | BR4-2150-E-00050 | A | BCV131BVS01-C4 2 PAIR | [7 empty] | F6 | 49 | 50
BSR132 | DX01 | DIO1 | 132 | 2 | 1 | 0 | 6 | 25 |  |  | DI |  | 3 | [19 empty] | F6 | 51 | 52
BSR132 | DX01 | DIO1 | 132 | 2 | 1 | 0 | 6 | 26 |  |  | DI | [10 empty] | 2.1\0.6:26 | [10 empty] | F6 | 53 | 54
BSR132 | DX01 | DIO1 | 132 | 2 | 1 | 0 | 6 | 27 |  |  | DI |  | 5 | BCV131CVS01 | VDC01 |  | 24VDC Control Supply | Healthy | Q290 | BCV131CVS01PN01 |  | 2.1\0.6:27 | BR4-2150-E-00124 | 0 | [8 empty] | F6 | 55 | 56
BSR132 | DX01 | DIO1 | 132 | 2 | 1 | 0 | 6 | 28 |  |  | DI |  | 5 | BCV131CVS01 | VAC01 |  | 240VAC Control Supply | Healthy | F5 | BCV131CVS01PN01 |  | 2.1\0.6:28 | BR4-2150-E-00053 | A | BCV131CVS01-C4 2 PAIR | [7 empty] | F6 | 57 | 58
BSR132 | DX01 | DIO1 | 132 | 2 | 1 | 0 | 6 | 29 |  |  | DI |  | 5 | BCV131CVS01 | VAC02 |  | 240VAC Supply Three Posn Switch Motor Isolator | Closed | -IS1 | BCV131CVS01PN01 |  | 2.1\0.6:29 | BR4-2150-E-00053 | A | BCV131CVS01-C4 2 PAIR | [7 empty] | F6 | 59 | 60
BSR132 | DX01 | DIO1 | 132 | 2 | 1 | 0 | 6 | 30 |  |  | DI |  | 3 | [19 empty] | F6 | 61 | 62
BSR132 | DX01 | DIO1 | 132 | 2 | 1 | 0 | 6 | 31 |  |  | DI | [10 empty] | 2.1\0.6:31 | [10 empty] | F6 | 63 | 64
BSR132 | DX01 | DIO1 | 132 | 2 | 1 | 0 | 7 | 0 | BMXFCW303 | BMXDDI3202K | DI |  | 3 |  | VDC01 |  | DX01 24VDC Control Supply Healthy | Healthy | Q110 | BSR132DX01 |  | 2.1\0.7:0 | BR4-2150-E-00123 | 0 | [8 empty] | F7 | 1 | 2
BSR132 | DX01 | DIO1 | 132 | 2 | 1 | 0 | 7 | 1 |  |  | DI |  | 3 |  | VDC02 |  | DX01 24VDC DIO1 Output Module Control Supply | Healthy | Q181 | BSR132DX01 |  | 2.1\0.7:1 | BR4-2150-E-00123 | 0 | [8 empty] | F7 | 3 | 4
BSR132 | DX01 | DIO1 | 132 | 2 | 1 | 0 | 7 | 2 |  |  | DI |  | 3 | BSR132UP01 | VDC03 |  | BSR132UP01 24VDC Control Supply | Healthy | Q254 | BSR132DX01 |  | 2.1\0.7:2 | BR4-2150-E-00124 | 0 | [8 empty] | F7 | 5 | 6
BSR132 | DX01 | DIO1 | 132 | 2 | 1 | 0 | 7 | 3 |  |  | DI |  | 3 | BSR132BC01 | VDC04 |  | BSR132BC01 24VDC Control Supply | Healthy | Q257 | BSR132DX01 |  | 2.1\0.7:3 | BR4-2150-E-00124 | 0 | [8 empty] | F7 | 7 | 8
BSR132 | DX01 | DIO1 | 132 | 2 | 1 | 0 | 7 | 4 |  |  | DI |  | 3 | BSR132BC02 | VDC05 |  | BSR132BC02 24VDC Control Supply | Healthy | Q260 | BSR132DX01 |  | 2.1\0.7:4 | BR4-2150-E-00124 | 0 | [8 empty] | F7 | 9 | 10
BSR132 | DX01 | DIO1 | 132 | 2 | 1 | 0 | 7 | 5 |  |  | DI |  | 3 | BSR132UP01DB01 | VDC06 |  | BSR132UP01DB01 24VDC Control Supply | Healthy | Q263 | BSR132DX01 |  | 2.1\0.7:5 | BR4-2150-E-00124 | 0 | [8 empty] | F7 | 11 | 12
BSR132 | DX01 | DIO1 | 132 | 2 | 1 | 0 | 7 | 6 |  |  | DI |  | 3 |  | VDC07 |  | Misc Substation Alarms 24VDC Control Supply | Healthy | Q266 | BSR132DX01 |  | 2.1\0.7:6 | BR4-2150-E-00124 | 0 | [8 empty] | F7 | 13 | 14
BSR132 | DX01 | DIO1 | 132 | 2 | 1 | 0 | 7 | 7 |  |  | DI |  | 3 |  | VDC08 |  | Safety PLC Circuit 1 | Healthy | Q269 | BSR132DX01 |  | 2.1\0.7:7 | BR4-2150-E-00124 | 0 | [8 empty] | F7 | 15 | 16
BSR132 | DX01 | DIO1 | 132 | 2 | 1 | 0 | 7 | 8 |  |  | DI |  | 3 |  | VDC09 |  | Safety PLC Circuit 2 | Healthy | Q272 | BSR132DX01 |  | 2.1\0.7:8 | BR4-2150-E-00124 | 0 | [8 empty] | F7 | 17 | 18
BSR132 | DX01 | DIO1 | 132 | 2 | 1 | 0 | 7 | 9 |  |  | DI |  | 3 |  | VDC10 |  | BPP2104VS01 24VDC Control Supply | Healthy | Q275 | BSR132DX01 |  | 2.1\0.7:9 | BR4-2150-E-00124 | 0 | [8 empty] | F7 | 19 | 20
BSR132 | DX01 | DIO1 | 132 | 2 | 1 | 0 | 7 | 10 |  |  | DI |  | 3 |  | VDC11 |  | BPP2105VS01 24VDC Control Supply | Healthy | Q278 | BSR132DX01 |  | 2.1\0.7:10 | BR4-2150-E-00124 | 0 | [8 empty] | F7 | 21 | 22
BSR132 | DX01 | DIO1 | 132 | 2 | 1 | 0 | 7 | 11 |  |  | DI |  | 3 |  | VDC12 |  | Spare | Healthy | Q281 | BSR132DX01 |  | 2.1\0.7:11 | BR4-2150-E-00124 | 0 | [8 empty] | F7 | 23 | 24
BSR132 | DX01 | DIO1 | 132 | 2 | 1 | 0 | 7 | 12 |  |  | DI | [10 empty] | 2.1\0.7:12 | [10 empty] | F7 | 25 | 26
BSR132 | DX01 | DIO1 | 132 | 2 | 1 | 0 | 7 | 13 |  |  | DI | [10 empty] | 2.1\0.7:13 | [10 empty] | F7 | 27 | 28
BSR132 | DX01 | DIO1 | 132 | 2 | 1 | 0 | 7 | 14 |  |  | DI |  | 3 | BCV131PP02 | VDC01 |  | 24VDC Control Supply | Healthy | Q155 | BCV131PP02 |  | 2.1\0.7:14 | BR4-2150-E-00073 | A | [8 empty] | F7 | 29 | 30
BSR132 | DX01 | DIO1 | 132 | 2 | 1 | 0 | 7 | 15 |  |  | DI |  | 3 | BCV131PP03 | VDC01 |  | 24VDC Control Supply | Healthy | Q155 | BCV131PP03 |  | 2.1\0.7:15 | BR4-2150-E-00075 | A | [8 empty] | F7 | 31 | 32
BSR132 | DX01 | DIO1 | 132 | 2 | 1 | 0 | 7 | 16 |  |  | DI |  | 3 | BBD131PP01 | VDC01 |  | 24VDC Control Supply | Healthy | Q155 | BBD131PP01 |  | 2.1\0.7:16 | BR4-2150-E-00077 | A | [8 empty] | F7 | 33 | 34
BSR132 | DX01 | DIO1 | 132 | 2 | 1 | 0 | 7 | 17 |  |  | DI |  | 3 | BAF131PP01 | VDC01 |  | 24VDC Control Supply | Healthy | Q155 | BAF131PP01 |  | 2.1\0.7:17 | BR4-2150-E-00099 | A | [8 empty] | F7 | 35 | 36
BSR132 | DX01 | DIO1 | 132 | 2 | 1 | 0 | 7 | 18 |  |  | DI |  | 3 | BAF131PP02 | VDC01 |  | 24VDC Control Supply | Healthy | Q155 | BAF131PP02 |  | 2.1\0.7:18 | BR4-2150-E-00103 | A | [8 empty] | F7 | 37 | 38
BSR132 | DX01 | DIO1 | 132 | 2 | 1 | 0 | 7 | 19 |  |  | DI |  | 3 | BAF131FN01 | VDC01 |  | 24VDC Control Supply | Healthy | Q155 | BAF131FN01 |  | 2.1\0.7:19 | BR4-2150-E-00104 | A | [8 empty] | F7 | 39 | 40
BSR132 | DX01 | DIO1 | 132 | 2 | 1 | 0 | 7 | 20 |  |  | DI |  | 3 | BDU131FN01 | VDC01 |  | 24VDC Control Supply | Healthy | Q155 | BDU131FN01 |  | 2.1\0.7:20 | BR4-2150-E-00106 | A | [8 empty] | F7 | 41 | 42
BSR132 | DX01 | DIO1 | 132 | 2 | 1 | 0 | 7 | 21 |  |  | DI |  | 3 | BCV131AFN01 | VDC01 |  | 24VDC Control Supply | Healthy | Q155 | BCV131AFN01 |  | 2.1\0.7:21 | BR4-2150-E-00096 | A | [8 empty] | F7 | 43 | 44
BSR132 | DX01 | DIO1 | 132 | 2 | 1 | 0 | 7 | 22 |  |  | DI |  | 3 | BCV131AFN02 | VDC01 |  | 24VDC Control Supply | Healthy | Q155 | BCV131AFN02 |  | 2.1\0.7:22 | BR4-2150-E-00090 | A | [8 empty] | F7 | 45 | 46
BSR132 | DX01 | DIO1 | 132 | 2 | 1 | 0 | 7 | 23 |  |  | DI |  | 3 | BCV131AFN03 | VDC01 |  | 24VDC Control Supply | Healthy | Q155 | BCV131AFN03 |  | 2.1\0.7:23 | BR4-2150-E-00091 | A | [8 empty] | F7 | 47 | 48
BSR132 | DX01 | DIO1 | 132 | 2 | 1 | 0 | 7 | 24 |  |  | DI |  | 3 | BCV131BFN01 | VDC01 |  | 24VDC Control Supply | Healthy | Q155 | BCV131BFN01 |  | 2.1\0.7:24 | BR4-2150-E-00097 | A | [8 empty] | F7 | 49 | 50
BSR132 | DX01 | DIO1 | 132 | 2 | 1 | 0 | 7 | 25 |  |  | DI |  | 3 | BCV131BFN02 | VDC01 |  | 24VDC Control Supply | Healthy | Q155 | BCV131BFN02 |  | 2.1\0.7:25 | BR4-2150-E-00092 | A | [8 empty] | F7 | 51 | 52
BSR132 | DX01 | DIO1 | 132 | 2 | 1 | 0 | 7 | 26 |  |  | DI |  | 3 | BCV131BFN03 | VDC01 |  | 24VDC Control Supply | Healthy | Q155 | BCV131BFN03 |  | 2.1\0.7:26 | BR4-2150-E-00093 | A | [8 empty] | F7 | 53 | 54
BSR132 | DX01 | DIO1 | 132 | 2 | 1 | 0 | 7 | 27 |  |  | DI |  | 3 | BCV131CFN01 | VDC01 |  | 24VDC Control Supply | Healthy | Q155 | BCV131CFN01 |  | 2.1\0.7:27 | BR4-2150-E-00098 | A | [8 empty] | F7 | 55 | 56
BSR132 | DX01 | DIO1 | 132 | 2 | 1 | 0 | 7 | 28 |  |  | DI |  | 3 | BCV131CFN02 | VDC01 |  | 24VDC Control Supply | Healthy | Q155 | BCV131CFN02 |  | 2.1\0.7:28 | BR4-2150-E-00094 | A | [8 empty] | F7 | 57 | 58
BSR132 | DX01 | DIO1 | 132 | 2 | 1 | 0 | 7 | 29 |  |  | DI |  | 3 | BCV131CFN03 | VDC01 |  | 24VDC Control Supply | Healthy | Q155 | BCV131CFN03 |  | 2.1\0.7:29 | BR4-2150-E-00095 | A | [8 empty] | F7 | 59 | 60
BSR132 | DX01 | DIO1 | 132 | 2 | 1 | 0 | 7 | 30 |  |  | DI |  | 3 | BAF131PP04 | VDC01 |  | 24VDC Control Supply | Healthy | Q155 | BAF131PP04 |  | 2.1\0.7:30 | BR4-2150-E-00061 | A | [8 empty] | F7 | 61 | 62
BSR132 | DX01 | DIO1 | 132 | 2 | 1 | 0 | 7 | 31 |  |  | DI | [10 empty] | 2.1\0.7:31 | [10 empty] | F7 | 63 | 64
BSR132 | DX01 | DIO1 | 132 | 2 | 1 | 0 | 8 | 0 | BMXFCW303 | BMXDDI3202K | DI |  | 3 | BDU131CP01 | VDC01 |  | 24VDC Control Supply | Healthy | Q155 | BDU131CP01 |  | 2.1\0.8:0 | BR4-2150-E-00107 | A | BDU131CP01PN01-C1 2 PAIR | [7 empty] | F8 | 1 | 2
BSR132 | DX01 | DIO1 | 132 | 2 | 1 | 0 | 8 | 1 |  |  | DI |  | 3 | BDU131CP01 | CB01 |  | Main Circuit Breaker | Closed | Q103 | BDU131CP01 |  | 2.1\0.8:1 | BR4-2150-E-00107 | A | BDU131CP01PN01-C1 2 PAIR | [7 empty] | F8 | 3 | 4
BSR132 | DX01 | DIO1 | 132 | 2 | 1 | 0 | 8 | 2 |  |  | DI |  | 3 | BDU131CP01 | TRP01 |  | Main Circuit Breaker | Tripped | Q103 | BDU131CP01 |  | 2.1\0.8:2 | BR4-2150-E-00107 | A | BDU131CP01PN01-C1 2 PAIR | [7 empty] | F8 | 5 | 6
BSR132 | DX01 | DIO1 | 132 | 2 | 1 | 0 | 8 | 3 |  |  | DI |  | 3 | BPP2104 | VDC01 |  | 24VDC Control Supply | Healthy | Q155 | BPP2104 |  | 2.1\0.8:3 | BR4-2150-E-00108 | A | BPP2104EM01-C1 4 PAIR - CHANGED TO 2 PAIR | [7 empty] | F8 | 7 | 8
BSR132 | DX01 | DIO1 | 132 | 2 | 1 | 0 | 8 | 4 |  |  | DI |  | 3 | BPP2104 | LOS01 |  | Safety Interlock Relay | Healthy | K161 | BPP2104 |  | 2.1\0.8:4 | BR4-2150-E-00108 | A | BPP2104EM01-C1 4 PAIR - CHANGED TO 2 PAIR | [7 empty] | F8 | 9 | 10
BSR132 | DX01 | DIO1 | 132 | 2 | 1 | 0 | 8 | 5 |  |  | DI |  | 3 | BPP2104 | CB01 |  | Main Circuit Breaker | Closed | Q103 | BPP2104 |  | 2.1\0.8:5 | BR4-2150-E-00108 | A | BPP2104EM01-C1 4 PAIR - CHANGED TO 2 PAIR | [7 empty] | F8 | 11 | 12
BSR132 | DX01 | DIO1 | 132 | 2 | 1 | 0 | 8 | 6 |  |  | DI |  | 3 | BPP2104 | TRP01 |  | Main Circuit Breaker | Tripped | Q103 | BPP2104 |  | 2.1\0.8:6 | BR4-2150-E-00108 | A | BPP2104EM01-C1 4 PAIR - CHANGED TO 2 PAIR | [7 empty] | F8 | 13 | 14
BSR132 | DX01 | DIO1 | 132 | 2 | 1 | 0 | 8 | 7 |  |  | DI |  | 3 | BPP2105 | VDC01 |  | 24VDC Control Supply | Healthy | Q155 | BPP2105 |  | 2.1\0.8:7 | BR4-2150-E-00109 | A | BPP2105EM01-C1 4 PAIR - CHANGED TO 2 PAIR | [7 empty] | F8 | 15 | 16
BSR132 | DX01 | DIO1 | 132 | 2 | 1 | 0 | 8 | 8 |  |  | DI |  | 3 | BPP2105 | LOS01 |  | Safety Interlock Relay | Healthy | K161 | BPP2105 |  | 2.1\0.8:8 | BR4-2150-E-00109 | A | BPP2105EM01-C1 4 PAIR - CHANGED TO 2 PAIR | [7 empty] | F8 | 17 | 18
BSR132 | DX01 | DIO1 | 132 | 2 | 1 | 0 | 8 | 9 |  |  | DI |  | 3 | BPP2105 | CB01 |  | Main Circuit Breaker | Tripped | Q103 | BPP2105 |  | 2.1\0.8:9 | BR4-2150-E-00109 | A | BPP2105EM01-C1 4 PAIR - CHANGED TO 2 PAIR | [7 empty] | F8 | 19 | 20
BSR132 | DX01 | DIO1 | 132 | 2 | 1 | 0 | 8 | 10 |  |  | DI |  | 3 | BPP2105 | TRP01 |  | Main Circuit Breaker | Healthy | Q103 | BPP2105 |  | 2.1\0.8:10 | BR4-2150-E-00109 | A | BPP2105EM01-C1 4 PAIR - CHANGED TO 2 PAIR | [7 empty] | F8 | 21 | 22
BSR132 | DX01 | DIO1 | 132 | 2 | 1 | 0 | 8 | 11 |  |  | DI |  | 3 | BCV131AVS01 | VDC01 |  | 24VDC Control Supply | Healthy | Q155 | BCV131AVS01 |  | 2.1\0.8:11 | BR4-2150-E-00100 | A | BCV131AVS01-C1 2 PAIR | [7 empty] | F8 | 23 | 24
BSR132 | DX01 | DIO1 | 132 | 2 | 1 | 0 | 8 | 12 |  |  | DI |  | 3 | BCV131AVS01 | CB01 |  | Main Circuit Breaker | Closed | Q103 | BCV131AVS01 |  | 2.1\0.8:12 | BR4-2150-E-00100 | A | BCV131AVS01-C1 2 PAIR | [7 empty] | F8 | 25 | 26
BSR132 | DX01 | DIO1 | 132 | 2 | 1 | 0 | 8 | 13 |  |  | DI |  | 3 | BCV131AVS01 | TRP01 |  | Main Circuit Breaker | Tripped | Q103 | BCV131AVS01 |  | 2.1\0.8:13 | BR4-2150-E-00100 | A | BCV131AVS01-C1 2 PAIR | [7 empty] | F8 | 27 | 28
BSR132 | DX01 | DIO1 | 132 | 2 | 1 | 0 | 8 | 14 |  |  | DI |  | 3 | BCV131BVS01 | VDC01 |  | 24VDC Control Supply | Healthy | Q155 | BCV131BVS01 |  | 2.1\0.8:14 | BR4-2150-E-00101 | A | BCV131BVS01-C1 2 PAIR | [7 empty] | F8 | 29 | 30
BSR132 | DX01 | DIO1 | 132 | 2 | 1 | 0 | 8 | 15 |  |  | DI |  | 3 | BCV131BVS01 | CB01 |  | Main Circuit Breaker | Closed | Q103 | BCV131BVS01 |  | 2.1\0.8:15 | BR4-2150-E-00101 | A | BCV131BVS01-C1 2 PAIR | [7 empty] | F8 | 31 | 32
BSR132 | DX01 | DIO1 | 132 | 2 | 1 | 0 | 8 | 16 |  |  | DI |  | 3 | BCV131BVS01 | TRP01 |  | Main Circuit Breaker | Tripped | Q103 | BCV131BVS01 |  | 2.1\0.8:16 | BR4-2150-E-00101 | A | BCV131BVS01-C1 2 PAIR | [7 empty] | F8 | 33 | 34
BSR132 | DX01 | DIO1 | 132 | 2 | 1 | 0 | 8 | 17 |  |  | DI |  | 3 | BCV131CVS01 | VDC01 |  | 24VDC Control Supply | Healthy | Q155 | BCV131CVS01 |  | 2.1\0.8:17 | BR4-2150-E-00102 | A | BCV131CVS01-C1 2 PAIR | [7 empty] | F8 | 35 | 36
BSR132 | DX01 | DIO1 | 132 | 2 | 1 | 0 | 8 | 18 |  |  | DI |  | 3 | BCV131CVS01 | CB01 |  | Main Circuit Breaker | Closed | Q103 | BCV131CVS01 |  | 2.1\0.8:18 | BR4-2150-E-00102 | A | BCV131CVS01-C1 2 PAIR | [7 empty] | F8 | 37 | 38
BSR132 | DX01 | DIO1 | 132 | 2 | 1 | 0 | 8 | 19 |  |  | DI |  | 3 | BCV131CVS01 | TRP01 |  | Main Circuit Breaker | Tripped | Q103 | BCV131CVS01 |  | 2.1\0.8:19 | BR4-2150-E-00102 | A | BCV131CVS01-C1 2 PAIR | [7 empty] | F8 | 39 | 40
BSR132 | DX01 | DIO1 | 132 | 2 | 1 | 0 | 8 | 20 |  |  | DI |  | 4 | BSR132DB04 | VDC01 |  | 24VDC Control Supply | Healthy | Q155 | BSR132DB04 |  | 2.1\0.8:20 | BR4-2150-E-00122 | A | [8 empty] | F8 | 41 | 42
BSR132 | DX01 | DIO1 | 132 | 2 | 1 | 0 | 8 | 21 |  |  | DI |  | 4 | BSR132DB04 | CB01 |  | Main Circuit Breaker | Closed | Q103 | BSR132DB04 |  | 2.1\0.8:21 | BR4-2150-E-00122 | A | [8 empty] | F8 | 43 | 44
BSR132 | DX01 | DIO1 | 132 | 2 | 1 | 0 | 8 | 22 |  |  | DI |  | 4 | BSR132DB04 | TRP01 |  | Main Circuit Breaker | Tripped | Q103 | BSR132DB04 |  | 2.1\0.8:22 | BR4-2150-E-00122 | A | [8 empty] | F8 | 45 | 46
BSR132 | DX01 | DIO1 | 132 | 2 | 1 | 0 | 8 | 23 |  |  | DI |  | 6 | BCV131WN01WE01 | XS01 |  | Load Cell 1 | High |  | BCV131WN01 |  | 2.1\0.8:23 | BR4-2150-E-00693 | 1 | [8 empty] | F8 | 47 | 48
BSR132 | DX01 | DIO1 | 132 | 2 | 1 | 0 | 8 | 24 |  |  | DI |  | 6 | BCV131WN01WE01 | XS02 |  | Load Cell 1 | Low |  | BCV131WN01 |  | 2.1\0.8:24 | BR4-2150-E-00693 | 1 | [8 empty] | F8 | 49 | 50
BSR132 | DX01 | DIO1 | 132 | 2 | 1 | 0 | 8 | 25 |  |  | DI |  | 6 | BCV131WN01WE02 | XS01 |  | Load Cell 2 | High |  | BCV131WN01 |  | 2.1\0.8:25 | BR4-2150-E-00693 | 1 | [8 empty] | F8 | 51 | 52
BSR132 | DX01 | DIO1 | 132 | 2 | 1 | 0 | 8 | 26 |  |  | DI |  | 6 | BCV131WN01WE02 | XS02 |  | Load Cell 2 | Low |  | BCV131WN01 |  | 2.1\0.8:26 | BR4-2150-E-00693 | 1 | [8 empty] | F8 | 53 | 54
BSR132 | DX01 | DIO1 | 132 | 2 | 1 | 0 | 8 | 27 |  |  | DI |  | 6 | BCV131WN01 | XS01 |  | Load Cell Overload | Trip |  | BCV131WN01 |  | 2.1\0.8:27 | BR4-2150-E-00693 | 1 | [8 empty] | F8 | 55 | 56
BSR132 | DX01 | DIO1 | 132 | 2 | 1 | 0 | 8 | 28 |  |  | DI | [10 empty] | 2.1\0.8:28 | [10 empty] | F8 | 57 | 58
BSR132 | DX01 | DIO1 | 132 | 2 | 1 | 0 | 8 | 29 |  |  | DI |  | 4 | BCV131APP02 | VDC01 |  | 24VDC Control Supply | Healthy | Q155 | BCV131APP02 |  | 2.1\0.8:29 | BR4-2150-E-00058 | A | [8 empty] | F8 | 59 | 60
BSR132 | DX01 | DIO1 | 132 | 2 | 1 | 0 | 8 | 30 |  |  | DI |  | 4 | BCV131BPP02 | VDC01 |  | 24VDC Control Supply | Healthy | Q155 | BCV131BPP02 |  | 2.1\0.8:30 | BR4-2150-E-00059 | A | [8 empty] | F8 | 61 | 62
BSR132 | DX01 | DIO1 | 132 | 2 | 1 | 0 | 8 | 31 |  |  | DI |  | 4 | BCV131CPP02 | VDC01 |  | 24VDC Control Supply | Healthy | Q155 | BCV131CPP02 |  | 2.1\0.8:31 | BR4-2150-E-00060 | A | [8 empty] | F8 | 63 | 64
BSR132 | DX01 | DIO1 | 132 | 2 | 1 | 0 | 9 | 0 | BMXFCW303 | BMXDDI3202K | DI | [10 empty] | 2.1\0.9:0 | [10 empty] | F9 | 1 | 2
BSR132 | DX01 | DIO1 | 132 | 2 | 1 | 0 | 9 | 1 |  |  | DI | [10 empty] | 2.1\0.9:1 | [10 empty] | F9 | 3 | 4
BSR132 | DX01 | DIO1 | 132 | 2 | 1 | 0 | 9 | 2 |  |  | DI |  | 3 | BAF131 | SY01 |  | Safety Interlock Relay (K355-1) | Healthy | K355-1 | BAF131 |  | 2.1\0.9:2 | BR4-2150-E-00204 | 0 | [8 empty] | F9 | 5 | 6
BSR132 | DX01 | DIO1 | 132 | 2 | 1 | 0 | 9 | 3 |  |  | DI |  | 3 | BAF131AFN02 | SY01 |  | Safety Interlock Relay (K405-1) | Healthy | K405-1 | BCV131AFN02 |  | 2.1\0.9:3 | BR4-2150-E-00205 | 0 | [8 empty] | F9 | 7 | 8
BSR132 | DX01 | DIO1 | 132 | 2 | 1 | 0 | 9 | 4 |  |  | DI |  | 3 | BAF131BFN02 | SY01 |  | Safety Interlock Relay (K420-1) | Healthy | K420-1 | BCV131BFN02 |  | 2.1\0.9:4 | BR4-2150-E-00205 | 0 | [8 empty] | F9 | 9 | 10
BSR132 | DX01 | DIO1 | 132 | 2 | 1 | 0 | 9 | 5 |  |  | DI |  | 3 | BAF131CFN02 | SY01 |  | Safety Interlock Relay (K435-1) | Healthy | K435-1 | BCV131CFN02 |  | 2.1\0.9:5 | BR4-2150-E-00205 | 0 | [8 empty] | F9 | 11 | 12
BSR132 | DX01 | DIO1 | 132 | 2 | 1 | 0 | 9 | 6 |  |  | DI |  | 4 |  | SY01 |  | Safety Interlock Relay (K455-1) | Healthy | K455-1 | BCV131AGB01 |  | 2.1\0.9:6 | BR4-2150-E-00205 | 1 | [8 empty] | F9 | 13 | 14
BSR132 | DX01 | DIO1 | 132 | 2 | 1 | 0 | 9 | 7 |  |  | DI |  | 4 |  | SY01 |  | Safety Interlock Relay (K470-1) | Healthy | K470-1 | BCV131BGB01 |  | 2.1\0.9:7 | BR4-2150-E-00205 | 1 | [8 empty] | F9 | 15 | 16
BSR132 | DX01 | DIO1 | 132 | 2 | 1 | 0 | 9 | 8 |  |  | DI |  | 4 |  | SY01 |  | Safety Interlock Relay (K485-1) | Healthy | K485-1 | BCV131CGB01 |  | 2.1\0.9:8 | BR4-2150-E-00205 | 1 | [8 empty] | F9 | 17 | 18
BSR132 | DX01 | DIO1 | 132 | 2 | 1 | 0 | 9 | 9 |  |  | DI | [10 empty] | 2.1\0.9:9 | [10 empty] | F9 | 19 | 20
BSR132 | DX01 | DIO1 | 132 | 2 | 1 | 0 | 9 | 10 |  |  | DI |  | 3 | BCV131 | SLC01SY01 |  | Safety SLC01 Circuit | Healthy | K132 | BCV131 |  | 2.1\0.9:10 | BR4-2150-E-00202 | 0 | [8 empty] | F9 | 21 | 22
BSR132 | DX01 | DIO1 | 132 | 2 | 1 | 0 | 9 | 11 |  |  | DI |  | 3 | BCV131 | SY01 |  | Safety Interlock Relay | Healthy | K155-1 | BCV131 |  | 2.1\0.9:11 | BR4-2150-E-00202 | 0 | [8 empty] | F9 | 23 | 24
BSR132 | DX01 | DIO1 | 132 | 2 | 1 | 0 | 9 | 12 |  |  | DI | [10 empty] | 2.1\0.9:12 | [10 empty] | F9 | 25 | 26
BSR132 | DX01 | DIO1 | 132 | 2 | 1 | 0 | 9 | 13 |  |  | DI |  | 3 | BCV131 | SLC02SY01 |  | Safety SLC02 Circuit | Healthy | K232 | BCV131 |  | 2.1\0.9:13 | BR4-2150-E-00203 | 0 | [8 empty] | F9 | 27 | 28
BSR132 | DX01 | DIO1 | 132 | 2 | 1 | 0 | 9 | 14 |  |  | DI |  | 3 | BBN131LS0x | SY01 |  | Safety Interlock Relay | Healthy | K255-1 | BBN131LS0x |  | 2.1\0.9:14 | BR4-2150-E-00203 | 0 | [8 empty] | F9 | 29 | 30
BSR132 | DX01 | DIO1 | 132 | 2 | 1 | 0 | 9 | 15 |  |  | DI | [10 empty] | 2.1\0.9:15 | [10 empty] | F9 | 31 | 32
BSR132 | DX01 | DIO1 | 132 | 2 | 1 | 0 | 9 | 16 |  |  | DI |  | 6 |  | SW01A |  | 240VAC Supply Three Posn Switch Mode | Local | SS | BCV131AVS01PN01 |  | 2.1\0.9:16 | BR4-2150-E-00047 | A | missing | [7 empty] | F9 | 33 | 34
BSR132 | DX01 | DIO1 | 132 | 2 | 1 | 0 | 9 | 17 |  |  | DI |  | 6 |  | SW01B |  | 240VAC Supply Three Posn Switch Mode | Remote | SS | BCV131AVS01PN01 |  | 2.1\0.9:17 | BR4-2150-E-00047 | A | [8 empty] | F9 | 35 | 36
BSR132 | DX01 | DIO1 | 132 | 2 | 1 | 0 | 9 | 18 |  |  | DI |  | 6 |  | SY01 |  | Safety Circuit Relay | Healthy | K91 | BCV131AVS01PN01 |  | 2.1\0.9:18 | BR4-2150-E-00047 | A | [8 empty] | F9 | 37 | 38
BSR132 | DX01 | DIO1 | 132 | 2 | 1 | 0 | 9 | 19 |  |  | DI |  | 6 | [8 empty] | 2.1\0.9:19 | BR4-2150-E-00047 | A | [8 empty] | F9 | 39 | 40
BSR132 | DX01 | DIO1 | 132 | 2 | 1 | 0 | 9 | 20 |  |  | DI |  | 6 |  | SW01A |  | 240VAC Supply Three Posn Switch Mode | Local | SS | BCV131BVS01PN01 |  | 2.1\0.9:20 | BR4-2150-E-00050 | [9 empty] | F9 | 41 | 42
BSR132 | DX01 | DIO1 | 132 | 2 | 1 | 0 | 9 | 21 |  |  | DI |  | 6 |  | SW01B |  | 240VAC Supply Three Posn Switch Mode | Remote | SS | BCV131BVS01PN01 |  | 2.1\0.9:21 | BR4-2150-E-00050 | [9 empty] | F9 | 43 | 44
BSR132 | DX01 | DIO1 | 132 | 2 | 1 | 0 | 9 | 22 |  |  | DI |  | 6 |  | SY01 |  | Safety Circuit Relay | Healthy | K91 | BCV131BVS01PN01 |  | 2.1\0.9:22 | BR4-2150-E-00050 | [9 empty] | F9 | 45 | 46
BSR132 | DX01 | DIO1 | 132 | 2 | 1 | 0 | 9 | 23 |  |  | DI |  | 6 | [8 empty] | 2.1\0.9:23 | BR4-2150-E-00050 | [9 empty] | F9 | 47 | 48
BSR132 | DX01 | DIO1 | 132 | 2 | 1 | 0 | 9 | 24 |  |  | DI |  | 6 |  | SW01A |  | 240VAC Supply Three Posn Switch Mode | Local | SS | BCV131CVS01PN01 |  | 2.1\0.9:24 | BR4-2150-E-00053 | [9 empty] | F9 | 49 | 50
BSR132 | DX01 | DIO1 | 132 | 2 | 1 | 0 | 9 | 25 |  |  | DI |  | 6 |  | SW01B |  | 240VAC Supply Three Posn Switch Mode | Remote | SS | BCV131CVS01PN01 |  | 2.1\0.9:25 | BR4-2150-E-00053 | [9 empty] | F9 | 51 | 52
BSR132 | DX01 | DIO1 | 132 | 2 | 1 | 0 | 9 | 26 |  |  | DI |  | 6 |  | SY01 |  | Safety Circuit Relay | Healthy | K91 | BCV131CVS01PN01 |  | 2.1\0.9:26 | BR4-2150-E-00053 | [9 empty] | F9 | 53 | 54
BSR132 | DX01 | DIO1 | 132 | 2 | 1 | 0 | 9 | 27 |  |  | DI |  | 6 | [8 empty] | 2.1\0.9:27 | BR4-2150-E-00053 | [9 empty] | F9 | 55 | 56
BSR132 | DX01 | DIO1 | 132 | 2 | 1 | 0 | 9 | 28 |  |  | DI | [10 empty] | 2.1\0.9:28 | [10 empty] | F9 | 57 | 58
BSR132 | DX01 | DIO1 | 132 | 2 | 1 | 0 | 9 | 29 |  |  | DI | [10 empty] | 2.1\0.9:29 | [10 empty] | F9 | 59 | 60
BSR132 | DX01 | DIO1 | 132 | 2 | 1 | 0 | 9 | 30 |  |  | DI | [10 empty] | 2.1\0.9:30 | [10 empty] | F9 | 61 | 62
BSR132 | DX01 | DIO1 | 132 | 2 | 1 | 0 | 9 | 31 |  |  | DI | [10 empty] | 2.1\0.9:31 | [10 empty] | F9 | 63 | 64
BSR132 | DX01 | DIO1 | 132 | 2 | 1 | 0 | 10 | 0 | BMXFTB2010 | BMXDDO1602 | DO |  | 4 | BCV131AVS01 | RST01 |  | VVVF STO Reset | Activated |  | BCV131AVS01 |  | 2.1\0.10:0 | BR4-2150-E-00047 | [9 empty] | F10 | 1 | 2
BSR132 | DX01 | DIO1 | 132 | 2 | 1 | 0 | 10 | 1 |  |  | DO |  | 4 | BAF131HT01 | SR01 |  | Start Relay | Closed |  | BAF131HT01 |  | 2.1\0.10:1 | BR4-2150-E-00105 | A | [8 empty] | F10 | 3 | 4
BSR132 | DX01 | DIO1 | 132 | 2 | 1 | 0 | 10 | 2 |  |  | DO |  | 4 | BCV131BVS01 | RST01 |  | VVVF STO Reset | Activated |  | BCV131BVS01 |  | 2.1\0.10:2 | BR4-2150-E-00050 | [9 empty] | F10 | 5 | 6
BSR132 | DX01 | DIO1 | 132 | 2 | 1 | 0 | 10 | 3 |  |  | DO |  | 4 | BCV131CVS01 | RST01 |  | VVVF STO Reset | Activated |  | BCV131CVS01 |  | 2.1\0.10:3 | BR4-2150-E-00053 | [9 empty] | F10 | 7 | 8
BSR132 | DX01 | DIO1 | 132 | 2 | 1 | 0 | 10 | 4 |  |  | DO | [10 empty] | 2.1\0.10:4 | [10 empty] | F10 | 9 | 10
BSR132 | DX01 | DIO1 | 132 | 2 | 1 | 0 | 10 | 5 |  |  | DO | [10 empty] | 2.1\0.10:5 | [10 empty] | F10 | 11 | 12
BSR132 | DX01 | DIO1 | 132 | 2 | 1 | 0 | 10 | 6 |  |  | DO | [10 empty] | 2.1\0.10:6 | [10 empty] | F10 | 13 | 14
BSR132 | DX01 | DIO1 | 132 | 2 | 1 | 0 | 10 | 7 |  |  | DO | [10 empty] | 2.1\0.10:7 | [10 empty] | F10 | 15 | 16
BSR132 | DX01 | DIO1 | 132 | 2 | 1 | 0 | 10 | 8 |  |  | DO | [10 empty] | 2.1\0.10:8 | [10 empty] | F10 | 17 | 18
BSR132 | DX01 | DIO1 | 132 | 2 | 1 | 0 | 10 | 9 |  |  | DO | [10 empty] | 2.1\0.10:9 | [10 empty] | F10 | 19 | 20
BSR132 | DX01 | DIO1 | 132 | 2 | 1 | 0 | 10 | 10 |  |  | DO | [10 empty] | 2.1\0.10:10 | [10 empty] | F10 | 21 | 22
BSR132 | DX01 | DIO1 | 132 | 2 | 1 | 0 | 10 | 11 |  |  | DO | [10 empty] | 2.1\0.10:11 | [10 empty] | F10 | 23 | 24
BSR132 | DX01 | DIO1 | 132 | 2 | 1 | 0 | 10 | 12 |  |  | DO | [10 empty] | 2.1\0.10:12 | [10 empty] | F10 | 25 | 26
BSR132 | DX01 | DIO1 | 132 | 2 | 1 | 0 | 10 | 13 |  |  | DO |  |  | BSR132CAP0x | SR01 |  | Capacitor Bank Start Relay |  |  |  |  | 2.1\0.10:13 |  |  | Drives interposing relay to bring in 3rd cap bank during conveyor starting | [7 empty] | F10 | 27 | 28
BSR132 | DX01 | DIO1 | 132 | 2 | 1 | 0 | 10 | 14 |  |  | DO |  | 6 | [8 empty] | 2.1\0.10:14 | [10 empty] | F10 | 29 | 30
BSR132 | DX01 | DIO1 | 132 | 2 | 1 | 0 | 10 | 15 |  |  | DO |  | 6 | BSR132DB01 | SR01 |  | Lighting Control Relay | Closed |  | BSR132DB01 |  | 2.1\0.10:15 | BR4-2150-E-00114 | [9 empty] | F10 | 31 | 32
BSR132 | DX01 | DIO1 | 132 | 2 | 1 | 0 | 11 | 0 |  | BMXXEM010 | [11 empty] | 2.1\0.11:0
BSR132 | DX01 | DIO1 | 132 | 2 | 1 | 0 | 11 | 1 | [13 empty] | 2.1\0.11:1
BSR132 | DX01 | DIO1 | 132 | 2 | 1 | 0 | 11 | 2 | [13 empty] | 2.1\0.11:2
BSR132 | DX01 | DIO1 | 132 | 2 | 1 | 0 | 11 | 3 | [13 empty] | 2.1\0.11:3
[33 empty] | #REF! | 81 | 82 | 83 | 84
|  | TeSysT |  |  |  | PR | 1 | 1 | C / I1 | TeSysT | DI |  | 3 |  | CB01 |  | Drive Circuit Breaker | Closed | Q103 | BCV131PP02 |  |  | BR4-2150-E-00073 | A
[6 empty] | PR | 1 | 2 | C / I2 | DX01ES01 | DI |  | 4 |  | TRP02 |  | Drive Circuit Breaker | Tripped | Q103 | BCV131PP02 |  |  | BR4-2150-E-00073 | A
[6 empty] | PR | 1 | 3 | C / I3 |  | DI |  | 3 |  | CAX01 |  | Drive Contactor | Closed | K148 | BCV131PP02 |  |  | BR4-2150-E-00073 | A
[6 empty] | PR | 1 | 4 | C / I4 |  | DI |  | 3 |  | SY01 |  | Safety Interlock Relay | Healthy | K165 | BCV131PP02 |  |  | BR4-2150-E-00073 | A
[6 empty] | PR | 1 | 5 | C / I5 |  | DI | [8 empty] | BCV131PP02 |  |  | BR4-2150-E-00073 | A
[6 empty] | PR | 1 | 6 | C / I6 |  | DI |  | 3 |  | SW01 |  | Remote Mode | Selected |  | BCV131PP02 |  |  | BR4-2150-E-00073 | A
[6 empty] | PR | 1 | 1 | 13 / 14 |  | DO |  | 3 |  | SR01 |  | Start Relay | Closed | K159 | BCV131PP02 |  |  | BR4-2150-E-00073 | A
[6 empty] | PR | 1 | 2 | 23 / 24 |  | DO |  | 6 |  | SHT01 |  | Shunt Trip | Activated | K161 | BCV131PP02 |  |  | BR4-2150-E-00073 | A
[6 empty] | PR | 1 | 3 | 33 / 34 |  | DO | [8 empty] | BCV131PP02 |  |  | BR4-2150-E-00073 | A
[6 empty] | PR | 1 | 4 | 95 / 96 |  | DO |  | 4 |  | TRP01 |  | Drive Circuit Breaker | Trip | Q103 | BCV131PP02 |  |  | BR4-2150-E-00073 | A
|  | TeSysT |  |  |  | PR | 1 | 1 | C / I1 | TeSysT | DI |  | 3 |  | CB01 |  | Drive Circuit Breaker | Closed | Q103 | BCV131PP03 |  |  | BR4-2150-E-00075 | A
[6 empty] | PR | 1 | 2 | C / I2 | DX01ES01 | DI |  | 4 |  | TRP02 |  | Drive Circuit Breaker | Tripped | Q103 | BCV131PP03 |  |  | BR4-2150-E-00075 | A
[6 empty] | PR | 1 | 3 | C / I3 |  | DI |  | 3 |  | CAX01 |  | Drive Contactor | Closed | K148 | BCV131PP03 |  |  | BR4-2150-E-00075 | A
[6 empty] | PR | 1 | 4 | C / I4 |  | DI |  | 3 |  | SY01 |  | Safety Interlock Relay | Healthy | K165 | BCV131PP03 |  |  | BR4-2150-E-00075 | A
[6 empty] | PR | 1 | 5 | C / I5 |  | DI | [8 empty] | BCV131PP03 |  |  | BR4-2150-E-00075 | A
[6 empty] | PR | 1 | 6 | C / I6 |  | DI |  | 3 |  | SW01 |  | Remote Mode | Selected |  | BCV131PP03 |  |  | BR4-2150-E-00075 | A
[6 empty] | PR | 1 | 1 | 13 / 14 |  | DO |  | 3 |  | SR01 |  | Start Relay | Closed | K159 | BCV131PP03 |  |  | BR4-2150-E-00075 | A
[6 empty] | PR | 1 | 2 | 23 / 24 |  | DO |  | 6 |  | SHT01 |  | Shunt Trip | Activated | K161 | BCV131PP03 |  |  | BR4-2150-E-00075 | A
[6 empty] | PR | 1 | 3 | 33 / 34 |  | DO | [8 empty] | BCV131PP03 |  |  | BR4-2150-E-00075 | A
[6 empty] | PR | 1 | 4 | 95 / 96 |  | DO |  | 4 |  | TRP01 |  | Drive Circuit Breaker | Trip | Q103 | BCV131PP03 |  |  | BR4-2150-E-00075 | A
|  | TeSysT |  |  |  | PR | 1 | 1 | C / I1 | TeSysT | DI |  | 3 |  | CB01 |  | Drive Circuit Breaker | Closed | Q103 | BBD131PP01 |  |  | BR4-2150-E-00077 | A
[6 empty] | PR | 1 | 2 | C / I2 | DX01ES01 | DI |  | 4 |  | TRP02 |  | Drive Circuit Breaker | Tripped | Q103 | BBD131PP01 |  |  | BR4-2150-E-00077 | A
[6 empty] | PR | 1 | 3 | C / I3 |  | DI |  | 3 |  | CAX01 |  | Drive Contactor | Closed | K148 | BBD131PP01 |  |  | BR4-2150-E-00077 | A
[6 empty] | PR | 1 | 4 | C / I4 |  | DI |  | 3 |  | SY01 |  | Safety Interlock Relay | Healthy | K165 | BBD131PP01 |  |  | BR4-2150-E-00077 | A
[6 empty] | PR | 1 | 5 | C / I5 |  | DI | [8 empty] | BBD131PP01 |  |  | BR4-2150-E-00077 | A
[6 empty] | PR | 1 | 6 | C / I6 |  | DI |  | 3 |  | SW01 |  | Remote Mode | Selected |  | BBD131PP01 |  |  | BR4-2150-E-00077 | A
[6 empty] | PR | 1 | 1 | 13 / 14 |  | DO |  | 3 |  | SR01 |  | Start Relay | Closed | K159 | BBD131PP01 |  |  | BR4-2150-E-00077 | A
[6 empty] | PR | 1 | 2 | 23 / 24 |  | DO |  | 6 |  | SHT01 |  | Shunt Trip | Activated | K161 | BBD131PP01 |  |  | BR4-2150-E-00077 | A
[6 empty] | PR | 1 | 3 | 33 / 34 |  | DO | [8 empty] | BBD131PP01 |  |  | BR4-2150-E-00077 | A
[6 empty] | PR | 1 | 4 | 95 / 96 |  | DO |  | 4 |  | TRP01 |  | Drive Circuit Breaker | Trip | Q103 | BBD131PP01 |  |  | BR4-2150-E-00077 | A
|  | TeSysT |  |  |  | PR | 1 | 1 | C / I1 | TeSysT | DI |  | 3 |  | CB01 |  | Drive Circuit Breaker | Closed | Q103 | BAF131PP01 |  |  | BR4-2150-E-00099 | 0
[6 empty] | PR | 1 | 2 | C / I2 | DX01ES01 | DI |  | 6 |  | TRP02 |  | Drive Circuit Breaker | Tripped | Q103 | BAF131PP01 |  |  | BR4-2150-E-00099 | 0
[6 empty] | PR | 1 | 3 | C / I3 |  | DI |  | 3 |  | CAX01 |  | Drive Contactor | Closed | K148 | BAF131PP01 |  |  | BR4-2150-E-00099 | 0
[6 empty] | PR | 1 | 4 | C / I4 |  | DI |  | 3 |  | SY01 |  | Safety Interlock Relay | Healthy | K165 | BAF131PP01 |  |  | BR4-2150-E-00099 | 0
[6 empty] | PR | 1 | 5 | C / I5 |  | DI |  |  |  | TRP02 |  | Drive Circuit Breaker | Tripped | Q103 | BAF131PP01 |  |  | BR4-2150-E-00099 | 0
[6 empty] | PR | 1 | 6 | C / I6 |  | DI |  | 3 |  | SW01 |  | Remote Mode | Selected |  | BAF131PP01 |  |  | BR4-2150-E-00099 | 0
[6 empty] | PR | 1 | 7 | C / I7 |  | DI
[6 empty] | PR | 1 | 8 | C / I8 |  | DI |  | 6 |  | VAC01 |  | 240 VAC Supply Relay | Healthy | K146 | 0 |  |  | 0 | 0
[6 empty] | PR | 1 | 9 | C / I9 |  | DI
[6 empty] | PR | 1 | 10 | C / I10 |  | DI
[6 empty] | PR | 1 | 1 | 13 / 14 |  | DO |  | 3 |  | SR01 |  | Start Relay | Closed | K159 | BAF131PP01 |  |  | BR4-2150-E-00099 | 0
[6 empty] | PR | 1 | 2 | 23 / 24 |  | DO |  | 6 |  | SHT01 |  | Shunt Trip | Activated | K161 | BAF131PP01 |  |  | BR4-2150-E-00099 | 0
[6 empty] | PR | 1 | 3 | 33 / 34 |  | DO | [8 empty] | BAF131PP01 |  |  | BR4-2150-E-00099 | 0
[6 empty] | PR | 1 | 4 | 95 / 96 |  | DO |  | 4 |  | TRP01 |  | Drive Circuit Breaker | Trip | Q103 | BAF131PP01 |  |  | BR4-2150-E-00099 | 0
|  | TeSysT |  |  |  | PR | 1 | 1 | C / I1 | TeSysT | DI |  | 3 |  | CB01 |  | Drive Circuit Breaker | Closed | Q103 | BAF131PP02 |  |  | BR4-2150-E-00103 | A
[6 empty] | PR | 1 | 2 | C / I2 | DX01ES01 | DI |  | 4 |  | TRP02 |  | Drive Circuit Breaker | Tripped | Q103 | BAF131PP02 |  |  | BR4-2150-E-00103 | A
[6 empty] | PR | 1 | 3 | C / I3 |  | DI |  | 3 |  | CAX01 |  | Drive Contactor | Closed | K148 | BAF131PP02 |  |  | BR4-2150-E-00103 | A
[6 empty] | PR | 1 | 4 | C / I4 |  | DI |  | 3 |  | SY01 |  | Safety Interlock Relay | Healthy | K165 | BAF131PP02 |  |  | BR4-2150-E-00103 | A
[6 empty] | PR | 1 | 5 | C / I5 |  | DI | [8 empty] | BAF131PP02 |  |  | BR4-2150-E-00103 | A
[6 empty] | PR | 1 | 6 | C / I6 |  | DI |  | 3 |  | SW01 |  | Remote Mode | Selected |  | BAF131PP02 |  |  | BR4-2150-E-00103 | A
[6 empty] | PR | 1 | 1 | 13 / 14 |  | DO |  | 3 |  | SR01 |  | Start Relay | Closed | K159 | BAF131PP02 |  |  | BR4-2150-E-00103 | A
[6 empty] | PR | 1 | 2 | 23 / 24 |  | DO |  | 6 |  | SHT01 |  | Shunt Trip | Activated | K161 | BAF131PP02 |  |  | BR4-2150-E-00103 | A
[6 empty] | PR | 1 | 3 | 33 / 34 |  | DO | [8 empty] | BAF131PP02 |  |  | BR4-2150-E-00103 | A
[6 empty] | PR | 1 | 4 | 95 / 96 |  | DO |  | 4 |  | TRP01 |  | Drive Circuit Breaker | Trip | Q103 | BAF131PP02 |  |  | BR4-2150-E-00103 | A
|  | TeSysT |  |  |  | PR | 1 | 1 | C / I1 | TeSysT | DI |  | 3 |  | CB01 |  | Drive Circuit Breaker | Closed | Q103 | BAF131PP04 |  |  | BR4-2150-E-00061 | A
[6 empty] | PR | 1 | 2 | C / I2 | DX01ES01 | DI |  | 4 |  | TRP02 |  | Drive Circuit Breaker | Tripped | Q103 | BAF131PP04 |  |  | BR4-2150-E-00061 | A
[6 empty] | PR | 1 | 3 | C / I3 |  | DI |  | 3 |  | CAX01 |  | Drive Contactor | Closed | K148 | BAF131PP04 |  |  | BR4-2150-E-00061 | A
[6 empty] | PR | 1 | 4 | C / I4 |  | DI |  | 3 |  | SY01 |  | Safety Interlock Relay | Healthy | K165 | BAF131PP04 |  |  | BR4-2150-E-00061 | A
[6 empty] | PR | 1 | 5 | C / I5 |  | DI | [8 empty] | BAF131PP04 |  |  | BR4-2150-E-00061 | A
[6 empty] | PR | 1 | 6 | C / I6 |  | DI |  | 3 |  | SW01 |  | Remote Mode | Selected |  | BAF131PP04 |  |  | BR4-2150-E-00061 | A
[6 empty] | PR | 1 | 1 | 13 / 14 |  | DO |  | 3 |  | SR01 |  | Start Relay | Closed | K159 | BAF131PP04 |  |  | BR4-2150-E-00061 | A
[6 empty] | PR | 1 | 2 | 23 / 24 |  | DO |  | 6 |  | SHT01 |  | Shunt Trip | Activated | K161 | BAF131PP04 |  |  | BR4-2150-E-00061 | A
[6 empty] | PR | 1 | 3 | 33 / 34 |  | DO | [8 empty] | BAF131PP04 |  |  | BR4-2150-E-00061 | A
[6 empty] | PR | 1 | 4 | 95 / 96 |  | DO |  | 4 |  | TRP01 |  | Drive Circuit Breaker | Trip | Q103 | BAF131PP04 |  |  | BR4-2150-E-00061 | A
|  | TeSysT |  |  |  | PR | 1 | 1 | C / I1 | TeSysT | DI |  | 3 |  | CB01 |  | Drive Circuit Breaker | Closed | Q103 | BAF131FN01 |  |  | BR4-2150-E-00104 | A
[6 empty] | PR | 1 | 2 | C / I2 | DX01ES01 | DI |  | 4 |  | TRP02 |  | Drive Circuit Breaker | Tripped | Q103 | BAF131FN01 |  |  | BR4-2150-E-00104 | A
[6 empty] | PR | 1 | 3 | C / I3 |  | DI |  | 3 |  | CAX01 |  | Drive Contactor | Closed | K148 | BAF131FN01 |  |  | BR4-2150-E-00104 | A
[6 empty] | PR | 1 | 4 | C / I4 |  | DI |  | 3 |  | SY01 |  | Safety Interlock Relay | Healthy | K165 | BAF131FN01 |  |  | BR4-2150-E-00104 | A
[6 empty] | PR | 1 | 5 | C / I5 |  | DI | [8 empty] | BAF131FN01 |  |  | BR4-2150-E-00104 | A
[6 empty] | PR | 1 | 6 | C / I6 |  | DI |  | 3 |  | SW01 |  | Remote Mode | Selected |  | BAF131FN01 |  |  | BR4-2150-E-00104 | A
[6 empty] | PR | 1 | 1 | 13 / 14 |  | DO |  | 3 |  | SR01 |  | Start Relay | Closed | K159 | BAF131FN01 |  |  | BR4-2150-E-00104 | A
[6 empty] | PR | 1 | 2 | 23 / 24 |  | DO |  | 6 |  | SHT01 |  | Shunt Trip | Activated | K161 | BAF131FN01 |  |  | BR4-2150-E-00104 | A
[6 empty] | PR | 1 | 3 | 33 / 34 |  | DO | [8 empty] | BAF131FN01 |  |  | BR4-2150-E-00104 | A
[6 empty] | PR | 1 | 4 | 95 / 96 |  | DO |  | 4 |  | TRP01 |  | Drive Circuit Breaker | Trip | Q103 | BAF131FN01 |  |  | BR4-2150-E-00104 | A
|  | TeSysT |  |  |  | PR | 1 | 1 | C / I1 | TeSysT | DI |  | 3 |  | CB01 |  | Drive Circuit Breaker | Closed | Q103 | BDU131FN01 |  |  | BR4-2150-E-00106 | A
[6 empty] | PR | 1 | 2 | C / I2 | DX01ES01 | DI |  | 4 |  | TRP02 |  | Drive Circuit Breaker | Tripped | Q103 | BDU131FN01 |  |  | BR4-2150-E-00106 | A
[6 empty] | PR | 1 | 3 | C / I3 |  | DI |  | 3 |  | CAX01 |  | Drive Contactor | Closed | K148 | BDU131FN01 |  |  | BR4-2150-E-00106 | A
[6 empty] | PR | 1 | 4 | C / I4 |  | DI |  | 3 |  | SY01 |  | Safety Interlock Relay | Healthy | K165 | BDU131FN01 |  |  | BR4-2150-E-00106 | A
[6 empty] | PR | 1 | 5 | C / I5 |  | DI | [8 empty] | BDU131FN01 |  |  | BR4-2150-E-00106 | A
[6 empty] | PR | 1 | 6 | C / I6 |  | DI |  | 3 |  | SW01 |  | Remote Mode | Selected |  | BDU131FN01 |  |  | BR4-2150-E-00106 | A
[6 empty] | PR | 1 | 1 | 13 / 14 |  | DO |  | 3 |  | SR01 |  | Start Relay | Closed | K159 | BDU131FN01 |  |  | BR4-2150-E-00106 | A
[6 empty] | PR | 1 | 2 | 23 / 24 |  | DO |  | 6 |  | SHT01 |  | Shunt Trip | Activated | K161 | BDU131FN01 |  |  | BR4-2150-E-00106 | A
[6 empty] | PR | 1 | 3 | 33 / 34 |  | DO | [8 empty] | BDU131FN01 |  |  | BR4-2150-E-00106 | A
[6 empty] | PR | 1 | 4 | 95 / 96 |  | DO |  | 4 |  | TRP01 |  | Drive Circuit Breaker | Trip | Q103 | BDU131FN01 |  |  | BR4-2150-E-00106 | A
|  | TeSysT |  |  |  | PR | 1 | 1 | C / I1 | TeSysT | DI |  | 3 |  | CB01 |  | Drive Circuit Breaker | Closed | Q103 | BCV131AFN01 |  |  | BR4-2150-E-00096 | A
[6 empty] | PR | 1 | 2 | C / I2 | DX01ES01 | DI |  | 4 |  | TRP02 |  | Drive Circuit Breaker | Tripped | Q103 | BCV131AFN01 |  |  | BR4-2150-E-00096 | A
[6 empty] | PR | 1 | 3 | C / I3 |  | DI |  | 3 |  | CAX01 |  | Drive Contactor | Closed | K148 | BCV131AFN01 |  |  | BR4-2150-E-00096 | A
[6 empty] | PR | 1 | 4 | C / I4 |  | DI |  | 3 |  | SY01 |  | Safety Interlock Relay | Healthy | K165 | BCV131AFN01 |  |  | BR4-2150-E-00096 | A
[6 empty] | PR | 1 | 5 | C / I5 |  | DI | [8 empty] | BCV131AFN01 |  |  | BR4-2150-E-00096 | A
[6 empty] | PR | 1 | 6 | C / I6 |  | DI |  | 3 |  | SW01 |  | Remote Mode | Selected |  | BCV131AFN01 |  |  | BR4-2150-E-00096 | A
[6 empty] | PR | 1 | 1 | 13 / 14 |  | DO |  | 3 |  | SR01 |  | Start Relay | Closed | K159 | BCV131AFN01 |  |  | BR4-2150-E-00096 | A
[6 empty] | PR | 1 | 2 | 23 / 24 |  | DO |  | 6 |  | SHT01 |  | Shunt Trip | Activated | K161 | BCV131AFN01 |  |  | BR4-2150-E-00096 | A
[6 empty] | PR | 1 | 3 | 33 / 34 |  | DO | [8 empty] | BCV131AFN01 |  |  | BR4-2150-E-00096 | A
[6 empty] | PR | 1 | 4 | 95 / 96 |  | DO |  | 4 |  | TRP01 |  | Drive Circuit Breaker | Trip | Q103 | BCV131AFN01 |  |  | BR4-2150-E-00096 | A
|  | TeSysT |  |  |  | PR | 1 | 1 | C / I1 | TeSysT | DI |  | 3 |  | CB01 |  | Drive Circuit Breaker | Closed | Q103 | BCV131AFN02 |  |  | BR4-2150-E-00090 | A
[6 empty] | PR | 1 | 2 | C / I2 | DX01ES01 | DI |  | 4 |  | TRP02 |  | Drive Circuit Breaker | Tripped | Q103 | BCV131AFN02 |  |  | BR4-2150-E-00090 | A
[6 empty] | PR | 1 | 3 | C / I3 |  | DI |  | 3 |  | CAX01 |  | Drive Contactor | Closed | K148 | BCV131AFN02 |  |  | BR4-2150-E-00090 | A
[6 empty] | PR | 1 | 4 | C / I4 |  | DI |  | 3 |  | SY01 |  | Safety Interlock Relay | Healthy | K165 | BCV131AFN02 |  |  | BR4-2150-E-00090 | A
[6 empty] | PR | 1 | 5 | C / I5 |  | DI | [8 empty] | BCV131AFN02 |  |  | BR4-2150-E-00090 | A
[6 empty] | PR | 1 | 6 | C / I6 |  | DI |  | 3 |  | SW01 |  | Remote Mode | Selected |  | BCV131AFN02 |  |  | BR4-2150-E-00090 | A
[6 empty] | PR | 1 | 1 | 13 / 14 |  | DO |  | 3 |  | SR01 |  | Start Relay | Closed | K159 | BCV131AFN02 |  |  | BR4-2150-E-00090 | A
[6 empty] | PR | 1 | 2 | 23 / 24 |  | DO |  | 6 |  | SHT01 |  | Shunt Trip | Activated | K161 | BCV131AFN02 |  |  | BR4-2150-E-00090 | A
[6 empty] | PR | 1 | 3 | 33 / 34 |  | DO | [8 empty] | BCV131AFN02 |  |  | BR4-2150-E-00090 | A
[6 empty] | PR | 1 | 4 | 95 / 96 |  | DO |  | 4 |  | TRP01 |  | Drive Circuit Breaker | Trip | Q103 | BCV131AFN02 |  |  | BR4-2150-E-00090 | A
|  | TeSysT |  |  |  | PR | 1 | 1 | C / I1 | TeSysT | DI |  | 3 |  | CB01 |  | Drive Circuit Breaker | Closed | Q103 | BCV131AFN03 |  |  | BR4-2150-E-00091 | A
[6 empty] | PR | 1 | 2 | C / I2 | DX01ES01 | DI |  | 4 |  | TRP02 |  | Drive Circuit Breaker | Tripped | Q103 | BCV131AFN03 |  |  | BR4-2150-E-00091 | A
[6 empty] | PR | 1 | 3 | C / I3 |  | DI |  | 3 |  | CAX01 |  | Drive Contactor | Closed | K148 | BCV131AFN03 |  |  | BR4-2150-E-00091 | A
[6 empty] | PR | 1 | 4 | C / I4 |  | DI |  | 3 |  | SY01 |  | Safety Interlock Relay | Healthy | K165 | BCV131AFN03 |  |  | BR4-2150-E-00091 | A
[6 empty] | PR | 1 | 5 | C / I5 |  | DI | [8 empty] | BCV131AFN03 |  |  | BR4-2150-E-00091 | A
[6 empty] | PR | 1 | 6 | C / I6 |  | DI |  | 3 |  | SW01 |  | Remote Mode | Selected |  | BCV131AFN03 |  |  | BR4-2150-E-00091 | A
[6 empty] | PR | 1 | 1 | 13 / 14 |  | DO |  | 3 |  | SR01 |  | Start Relay | Closed | K159 | BCV131AFN03 |  |  | BR4-2150-E-00091 | A
[6 empty] | PR | 1 | 2 | 23 / 24 |  | DO |  | 6 |  | SHT01 |  | Shunt Trip | Activated | K161 | BCV131AFN03 |  |  | BR4-2150-E-00091 | A
[6 empty] | PR | 1 | 3 | 33 / 34 |  | DO | [8 empty] | BCV131AFN03 |  |  | BR4-2150-E-00091 | A
[6 empty] | PR | 1 | 4 | 95 / 96 |  | DO |  | 4 |  | TRP01 |  | Drive Circuit Breaker | Trip | Q103 | BCV131AFN03 |  |  | BR4-2150-E-00091 | A
|  | TeSysT |  |  |  | PR | 1 | 1 | C / I1 | TeSysT | DI |  | 3 |  | CB01 |  | Drive Circuit Breaker | Closed | Q103 | BCV131APP02 |  |  | BR4-2150-E-00058 | A
[6 empty] | PR | 1 | 2 | C / I2 | DX01ES01 | DI |  | 4 |  | TRP02 |  | Drive Circuit Breaker | Tripped | Q103 | BCV131APP02 |  |  | BR4-2150-E-00058 | A
[6 empty] | PR | 1 | 3 | C / I3 |  | DI |  | 3 |  | CAX01 |  | Drive Contactor | Closed | K148 | BCV131APP02 |  |  | BR4-2150-E-00058 | A
[6 empty] | PR | 1 | 4 | C / I4 |  | DI |  | 3 |  | SY01 |  | Safety Interlock Relay | Healthy | K165 | BCV131APP02 |  |  | BR4-2150-E-00058 | A
[6 empty] | PR | 1 | 5 | C / I5 |  | DI | [8 empty] | BCV131APP02 |  |  | BR4-2150-E-00058 | A
[6 empty] | PR | 1 | 6 | C / I6 |  | DI |  | 3 |  | SW01 |  | Remote Mode | Selected |  | BCV131APP02 |  |  | BR4-2150-E-00058 | A
[6 empty] | PR | 1 | 1 | 13 / 14 |  | DO |  | 3 |  | SR01 |  | Start Relay | Closed | K159 | BCV131APP02 |  |  | BR4-2150-E-00058 | A
[6 empty] | PR | 1 | 2 | 23 / 24 |  | DO |  | 6 |  | SHT01 |  | Shunt Trip | Activated | K161 | BCV131APP02 |  |  | BR4-2150-E-00058 | A
[6 empty] | PR | 1 | 3 | 33 / 34 |  | DO | [8 empty] | BCV131APP02 |  |  | BR4-2150-E-00058 | A
[6 empty] | PR | 1 | 4 | 95 / 96 |  | DO |  | 4 |  | TRP01 |  | Drive Circuit Breaker | Trip | Q103 | BCV131APP02 |  |  | BR4-2150-E-00058 | A
|  | TeSysT |  |  |  | PR | 1 | 1 | C / I1 | TeSysT | DI |  | 3 |  | CB01 |  | Drive Circuit Breaker | Closed | Q103 | BCV131BFN01 |  |  | BR4-2150-E-00097 | A
[6 empty] | PR | 1 | 2 | C / I2 | DX01ES01 | DI |  | 4 |  | TRP02 |  | Drive Circuit Breaker | Tripped | Q103 | BCV131BFN01 |  |  | BR4-2150-E-00097 | A
[6 empty] | PR | 1 | 3 | C / I3 |  | DI |  | 3 |  | CAX01 |  | Drive Contactor | Closed | K148 | BCV131BFN01 |  |  | BR4-2150-E-00097 | A
[6 empty] | PR | 1 | 4 | C / I4 |  | DI |  | 3 |  | SY01 |  | Safety Interlock Relay | Healthy | K165 | BCV131BFN01 |  |  | BR4-2150-E-00097 | A
[6 empty] | PR | 1 | 5 | C / I5 |  | DI | [8 empty] | BCV131BFN01 |  |  | BR4-2150-E-00097 | A
[6 empty] | PR | 1 | 6 | C / I6 |  | DI |  | 3 |  | SW01 |  | Remote Mode | Selected |  | BCV131BFN01 |  |  | BR4-2150-E-00097 | A
[6 empty] | PR | 1 | 1 | 13 / 14 |  | DO |  | 3 |  | SR01 |  | Start Relay | Closed | K159 | BCV131BFN01 |  |  | BR4-2150-E-00097 | A
[6 empty] | PR | 1 | 2 | 23 / 24 |  | DO |  | 6 |  | SHT01 |  | Shunt Trip | Activated | K161 | BCV131BFN01 |  |  | BR4-2150-E-00097 | A
[6 empty] | PR | 1 | 3 | 33 / 34 |  | DO | [8 empty] | BCV131BFN01 |  |  | BR4-2150-E-00097 | A
[6 empty] | PR | 1 | 4 | 95 / 96 |  | DO |  | 4 |  | TRP01 |  | Drive Circuit Breaker | Trip | Q103 | BCV131BFN01 |  |  | BR4-2150-E-00097 | A
|  | TeSysT |  |  |  | PR | 1 | 1 | C / I1 | TeSysT | DI |  | 3 |  | CB01 |  | Drive Circuit Breaker | Closed | Q103 | BCV131BFN02 |  |  | BR4-2150-E-00092 | A
[6 empty] | PR | 1 | 2 | C / I2 | DX01ES01 | DI |  | 6 |  | TRP02 |  | Drive Circuit Breaker | Tripped | Q103 | BCV131BFN02 |  |  | BR4-2150-E-00092 | A
[6 empty] | PR | 1 | 3 | C / I3 |  | DI |  | 3 |  | CAX01 |  | Drive Contactor | Closed | K148 | BCV131BFN02 |  |  | BR4-2150-E-00092 | A
[6 empty] | PR | 1 | 4 | C / I4 |  | DI |  | 3 |  | SY01 |  | Safety Interlock Relay | Healthy | K165 | BCV131BFN02 |  |  | BR4-2150-E-00092 | A
[6 empty] | PR | 1 | 5 | C / I5 |  | DI
[6 empty] | PR | 1 | 6 | C / I6 |  | DI |  | 3 |  | SW01 |  | Remote Mode | Selected |  | BCV131BFN02 |  |  | BR4-2150-E-00092 | A
[6 empty] | PR | 1 | 1 | 13 / 14 |  | DO |  | 3 |  | SR01 |  | Start Relay | Closed | K159 | BCV131BFN02 |  |  | BR4-2150-E-00092 | A
[6 empty] | PR | 1 | 2 | 23 / 24 |  | DO |  | 6 |  | SHT01 |  | Shunt Trip | Activated | K161 | BCV131BFN02 |  |  | BR4-2150-E-00092 | 0
[6 empty] | PR | 1 | 3 | 33 / 34 |  | DO
[6 empty] | PR | 1 | 4 | 95 / 96 |  | DO |  | 6 |  | TRP01 |  | Drive Circuit Breaker | Trip | Q103 | BCV131BFN02 |  |  | BR4-2150-E-00092 | 0
|  | TeSysT |  |  |  | PR | 1 | 1 | C / I1 | TeSysT | DI |  | 3 |  | CB01 |  | Drive Circuit Breaker | Closed | Q103 | BCV131BFN03 |  |  | BR4-2150-E-00093 | A
[6 empty] | PR | 1 | 2 | C / I2 | DX01ES01 | DI |  | 6 |  | TRP02 |  | Drive Circuit Breaker | Tripped | Q103 | BCV131BFN03 |  |  | BR4-2150-E-00093 | A
[6 empty] | PR | 1 | 3 | C / I3 |  | DI |  | 3 |  | CAX01 |  | Drive Contactor | Closed | K148 | BCV131BFN03 |  |  | BR4-2150-E-00093 | A
[6 empty] | PR | 1 | 4 | C / I4 |  | DI |  | 3 |  | SY01 |  | Safety Interlock Relay | Healthy | K165 | BCV131BFN03 |  |  | BR4-2150-E-00093 | A
[6 empty] | PR | 1 | 5 | C / I5 |  | DI
[6 empty] | PR | 1 | 6 | C / I6 |  | DI |  | 3 |  | SW01 |  | Remote Mode | Selected |  | BCV131BFN03 |  |  | BR4-2150-E-00093 | A
[6 empty] | PR | 1 | 1 | 13 / 14 |  | DO |  | 3 |  | SR01 |  | Start Relay | Closed | K159 | BCV131BFN03 |  |  | BR4-2150-E-00093 | A
[6 empty] | PR | 1 | 2 | 23 / 24 |  | DO |  | 6 |  | SHT01 |  | Shunt Trip | Activated | K161 | BCV131BFN03 |  |  | BR4-2150-E-00093 | 0
[6 empty] | PR | 1 | 3 | 33 / 34 |  | DO
[6 empty] | PR | 1 | 4 | 95 / 96 |  | DO |  | 6 |  | TRP01 |  | Drive Circuit Breaker | Trip | Q103 | BCV131BFN03 |  |  | BR4-2150-E-00093 | 0
|  | TeSysT |  |  |  | PR | 1 | 1 | C / I1 | TeSysT | DI |  | 3 |  | CB01 |  | Drive Circuit Breaker | Closed | Q103 | BCV131BPP02 |  |  | BR4-2150-E-00059 | A
[6 empty] | PR | 1 | 2 | C / I2 | DX01ES01 | DI |  | 3 |  | TRP02 |  | Drive Circuit Breaker | Tripped | Q103 | BCV131BPP02 |  |  | BR4-2150-E-00059 | A
[6 empty] | PR | 1 | 3 | C / I3 |  | DI |  | 3 |  | CAX01 |  | Drive Contactor | Closed | K148 | BCV131BPP02 |  |  | BR4-2150-E-00059 | A
[6 empty] | PR | 1 | 4 | C / I4 |  | DI |  | 3 |  | SY01 |  | Safety Interlock Relay | Healthy | K165 | BCV131BPP02 |  |  | BR4-2150-E-00059 | A
[6 empty] | PR | 1 | 5 | C / I5 |  | DI
[6 empty] | PR | 1 | 6 | C / I6 |  | DI |  | 3 |  | SW01 |  | Remote Mode | Selected |  | BCV131BPP02 |  |  | BR4-2150-E-00059 | A
[6 empty] | PR | 1 | 1 | 13 / 14 |  | DO |  | 3 |  | SR01 |  | Start Relay | Closed | K159 | BCV131BPP02 |  |  | BR4-2150-E-00059 | A
[6 empty] | PR | 1 | 2 | 23 / 24 |  | DO |  | 6 |  | SHT01 |  | Shunt Trip | Activated | K161 | BCV131BPP02 |  |  | BR4-2150-E-00059 | 0
[6 empty] | PR | 1 | 3 | 33 / 34 |  | DO
[6 empty] | PR | 1 | 4 | 95 / 96 |  | DO |  | 6 |  | TRP01 |  | Drive Circuit Breaker | Trip | Q103 | BCV131BPP02 |  |  | BR4-2150-E-00059 | 0
|  | TeSysT |  |  |  | PR | 1 | 1 | C / I1 | TeSysT | DI |  | 3 |  | CB01 |  | Drive Circuit Breaker | Closed | Q103 | BCV131CFN01 |  |  | BR4-2150-E-00098 | A
[6 empty] | PR | 1 | 2 | C / I2 | DX01ES01 | DI |  | 6 |  | TRP02 |  | Drive Circuit Breaker | Tripped | Q103 | BCV131CFN01 |  |  | BR4-2150-E-00098 | A
[6 empty] | PR | 1 | 3 | C / I3 |  | DI |  | 3 |  | CAX01 |  | Drive Contactor | Closed | K148 | BCV131CFN01 |  |  | BR4-2150-E-00098 | A
[6 empty] | PR | 1 | 4 | C / I4 |  | DI |  | 3 |  | SY01 |  | Safety Interlock Relay | Healthy | K165 | BCV131CFN01 |  |  | BR4-2150-E-00098 | A
[6 empty] | PR | 1 | 5 | C / I5 |  | DI
[6 empty] | PR | 1 | 6 | C / I6 |  | DI |  | 3 |  | SW01 |  | Remote Mode | Selected |  | BCV131CFN01 |  |  | BR4-2150-E-00098 | A
[6 empty] | PR | 1 | 1 | 13 / 14 |  | DO |  | 3 |  | SR01 |  | Start Relay | Closed | K159 | BCV131CFN01 |  |  | BR4-2150-E-00098 | A
[6 empty] | PR | 1 | 2 | 23 / 24 |  | DO |  | 6 |  | SHT01 |  | Shunt Trip | Activated | K161 | BCV131CFN01 |  |  | BR4-2150-E-00098 | 0
[6 empty] | PR | 1 | 3 | 33 / 34 |  | DO
[6 empty] | PR | 1 | 4 | 95 / 96 |  | DO |  | 6 |  | TRP01 |  | Drive Circuit Breaker | Trip | Q103 | BCV131CFN01 |  |  | BR4-2150-E-00098 | 0
|  | TeSysT |  |  |  | PR | 1 | 1 | C / I1 | TeSysT | DI |  | 3 |  | CB01 |  | Drive Circuit Breaker | Closed | Q103 | BCV131CFN02 |  |  | BR4-2150-E-00094 | A
[6 empty] | PR | 1 | 2 | C / I2 | DX01ES01 | DI |  | 4 |  | TRP02 |  | Drive Circuit Breaker | Tripped | Q103 | BCV131CFN02 |  |  | BR4-2150-E-00094 | A
[6 empty] | PR | 1 | 3 | C / I3 |  | DI |  | 3 |  | CAX01 |  | Drive Contactor | Closed | K148 | BCV131CFN02 |  |  | BR4-2150-E-00094 | A
[6 empty] | PR | 1 | 4 | C / I4 |  | DI |  | 3 |  | SY01 |  | Safety Interlock Relay | Healthy | K165 | BCV131CFN02 |  |  | BR4-2150-E-00094 | A
[6 empty] | PR | 1 | 5 | C / I5 |  | DI | [8 empty] | BCV131CFN02 |  |  | BR4-2150-E-00094 | A
[6 empty] | PR | 1 | 6 | C / I6 |  | DI |  | 3 |  | SW01 |  | Remote Mode | Selected |  | BCV131CFN02 |  |  | BR4-2150-E-00094 | A
[6 empty] | PR | 1 | 1 | 13 / 14 |  | DO |  | 3 |  | SR01 |  | Start Relay | Closed | K159 | BCV131CFN02 |  |  | BR4-2150-E-00094 | A
[6 empty] | PR | 1 | 2 | 23 / 24 |  | DO |  | 6 |  | SHT01 |  | Shunt Trip | Activated | K161 | BCV131CFN02 |  |  | BR4-2150-E-00094 | A
[6 empty] | PR | 1 | 3 | 33 / 34 |  | DO | [8 empty] | BCV131CFN02 |  |  | BR4-2150-E-00094 | A
[6 empty] | PR | 1 | 4 | 95 / 96 |  | DO |  | 4 |  | TRP01 |  | Drive Circuit Breaker | Trip | Q103 | BCV131CFN02 |  |  | BR4-2150-E-00094 | A
|  | TeSysT |  |  |  | PR | 1 | 1 | C / I1 | TeSysT | DI |  | 3 |  | CB01 |  | Drive Circuit Breaker | Closed | Q103 | BCV131CFN03 |  |  | BR4-2150-E-00095 | A
[6 empty] | PR | 1 | 2 | C / I2 | DX01ES01 | DI |  | 4 |  | TRP02 |  | Drive Circuit Breaker | Tripped | Q103 | BCV131CFN03 |  |  | BR4-2150-E-00095 | A
[6 empty] | PR | 1 | 3 | C / I3 |  | DI |  | 3 |  | CAX01 |  | Drive Contactor | Closed | K148 | BCV131CFN03 |  |  | BR4-2150-E-00095 | A
[6 empty] | PR | 1 | 4 | C / I4 |  | DI |  | 3 |  | SY01 |  | Safety Interlock Relay | Healthy | K165 | BCV131CFN03 |  |  | BR4-2150-E-00095 | A
[6 empty] | PR | 1 | 5 | C / I5 |  | DI | [8 empty] | BCV131CFN03 |  |  | BR4-2150-E-00095 | A
[6 empty] | PR | 1 | 6 | C / I6 |  | DI |  | 3 |  | SW01 |  | Remote Mode | Selected |  | BCV131CFN03 |  |  | BR4-2150-E-00095 | A
[6 empty] | PR | 1 | 1 | 13 / 14 |  | DO |  | 3 |  | SR01 |  | Start Relay | Closed | K159 | BCV131CFN03 |  |  | BR4-2150-E-00095 | A
[6 empty] | PR | 1 | 2 | 23 / 24 |  | DO |  | 6 |  | SHT01 |  | Shunt Trip | Activated | K161 | BCV131CFN03 |  |  | BR4-2150-E-00095 | A
[6 empty] | PR | 1 | 3 | 33 / 34 |  | DO | [8 empty] | BCV131CFN03 |  |  | BR4-2150-E-00095 | A
[6 empty] | PR | 1 | 4 | 95 / 96 |  | DO |  | 4 |  | TRP01 |  | Drive Circuit Breaker | Trip | Q103 | BCV131CFN03 |  |  | BR4-2150-E-00095 | A
|  | TeSysT |  |  |  | PR | 1 | 1 | C / I1 | TeSysT | DI |  | 3 |  | CB01 |  | Drive Circuit Breaker | Closed | Q103 | BCV131CPP02 |  |  | BR4-2150-E-00060 | A
[6 empty] | PR | 1 | 2 | C / I2 | DX01ES01 | DI |  | 4 |  | TRP02 |  | Drive Circuit Breaker | Tripped | Q103 | BCV131CPP02 |  |  | BR4-2150-E-00060 | A
[6 empty] | PR | 1 | 3 | C / I3 |  | DI |  | 3 |  | CAX01 |  | Drive Contactor | Closed | K148 | BCV131CPP02 |  |  | BR4-2150-E-00060 | A
[6 empty] | PR | 1 | 4 | C / I4 |  | DI |  | 3 |  | SY01 |  | Safety Interlock Relay | Healthy | K165 | BCV131CPP02 |  |  | BR4-2150-E-00060 | A
[6 empty] | PR | 1 | 5 | C / I5 |  | DI | [8 empty] | BCV131CPP02 |  |  | BR4-2150-E-00060 | A
[6 empty] | PR | 1 | 6 | C / I6 |  | DI |  | 3 |  | SW01 |  | Remote Mode | Selected |  | BCV131CPP02 |  |  | BR4-2150-E-00060 | A
[6 empty] | PR | 1 | 1 | 13 / 14 |  | DO |  | 3 |  | SR01 |  | Start Relay | Closed | K159 | BCV131CPP02 |  |  | BR4-2150-E-00060 | A
[6 empty] | PR | 1 | 2 | 23 / 24 |  | DO |  | 6 |  | SHT01 |  | Shunt Trip | Activated | K161 | BCV131CPP02 |  |  | BR4-2150-E-00060 | A
[6 empty] | PR | 1 | 3 | 33 / 34 |  | DO | [8 empty] | BCV131CPP02 |  |  | BR4-2150-E-00060 | A
[6 empty] | PR | 1 | 4 | 95 / 96 |  | DO |  | 4 |  | TRP01 |  | Drive Circuit Breaker | Trip | Q103 | BCV131CPP02 |  |  | BR4-2150-E-00060 | A
BSR130 remote drop
|  | TeSysT |  |  |  | PR | 1 | 1 | C / I1 | TeSysT | DI |  | 3 |  | CB01 |  | Drive Circuit Breaker | Closed | Q103 | BCV131PP04 |  |  | BR4-2110-E-00218 | A | PART OF BSR130 REMOTE SWITCH
[6 empty] | PR | 1 | 2 | C / I2 | DX01ES01 | DI |  | 4 |  | TRP02 |  | Drive Circuit Breaker | Tripped | Q103 | BCV131PP04 |  |  | BR4-2110-E-00218 | A
[6 empty] | PR | 1 | 3 | C / I3 |  | DI |  | 3 |  | CAX01 |  | Drive Contactor | Closed | K148 | BCV131PP04 |  |  | BR4-2110-E-00218 | A
[6 empty] | PR | 1 | 4 | C / I4 |  | DI |  | 3 |  | SY01 |  | Safety Interlock Relay | Healthy | K165 | BCV131PP04 |  |  | BR4-2110-E-00218 | A
[6 empty] | PR | 1 | 5 | C / I5 |  | DI | [8 empty] | BCV131PP04 |  |  | BR4-2110-E-00218 | A
[6 empty] | PR | 1 | 6 | C / I6 |  | DI |  | 3 |  | SW01 |  | Remote Mode | Selected |  | BCV131PP04 |  |  | BR4-2110-E-00218 | A
[6 empty] | PR | 1 | 1 | 13 / 14 |  | DO |  | 3 |  | SR01 |  | Start Relay | Closed | K159 | BCV131PP04 |  |  | BR4-2110-E-00218 | A
[6 empty] | PR | 1 | 2 | 23 / 24 |  | DO |  | 6 |  | SHT01 |  | Shunt Trip | Activated | K161 | BCV131PP04 |  |  | BR4-2110-E-00218 | A
[6 empty] | PR | 1 | 3 | 33 / 34 |  | DO | [8 empty] | BCV131PP04 |  |  | BR4-2110-E-00218 | A
[6 empty] | PR | 1 | 4 | 95 / 96 |  | DO |  | 4 |  | TRP01 |  | Drive Circuit Breaker | Trip | Q103 | BCV131PP04 |  |  | BR4-2110-E-00218 | A
|  | TeSysT |  |  |  | PR | 1 | 1 | C / I1 | TeSysT | DI |  | 3 |  | CB01 |  | Drive Circuit Breaker | Closed | Q103 | BCV131PP05 |  |  | BR4-2110-E-00219 | A | PART OF BSR130 REMOTE SWITCH
[6 empty] | PR | 1 | 2 | C / I2 | DX01ES01 | DI |  | 4 |  | TRP02 |  | Drive Circuit Breaker | Tripped | Q103 | BCV131PP05 |  |  | BR4-2110-E-00219 | A
[6 empty] | PR | 1 | 3 | C / I3 |  | DI |  | 3 |  | CAX01 |  | Drive Contactor | Closed | K148 | BCV131PP05 |  |  | BR4-2110-E-00219 | A
[6 empty] | PR | 1 | 4 | C / I4 |  | DI |  | 3 |  | SY01 |  | Safety Interlock Relay | Healthy | K165 | BCV131PP05 |  |  | BR4-2110-E-00219 | A
[6 empty] | PR | 1 | 5 | C / I5 |  | DI | [8 empty] | BCV131PP05 |  |  | BR4-2110-E-00219 | A
[6 empty] | PR | 1 | 6 | C / I6 |  | DI |  | 3 |  | SW01 |  | Remote Mode | Selected |  | BCV131PP05 |  |  | BR4-2110-E-00219 | A
[6 empty] | PR | 1 | 1 | 13 / 14 |  | DO |  | 3 |  | SR01 |  | Start Relay | Closed | K159 | BCV131PP05 |  |  | BR4-2110-E-00219 | A
[6 empty] | PR | 1 | 2 | 23 / 24 |  | DO |  | 6 |  | SHT01 |  | Shunt Trip | Activated | K161 | BCV131PP05 |  |  | BR4-2110-E-00219 | A
[6 empty] | PR | 1 | 3 | 33 / 34 |  | DO | [8 empty] | BCV131PP05 |  |  | BR4-2110-E-00219 | A
[6 empty] | PR | 1 | 4 | 95 / 96 |  | DO |  | 4 |  | TRP01 |  | Drive Circuit Breaker | Trip | Q103 | BCV131PP05 |  |  | BR4-2110-E-00219 | A
|  | ACS880 |  |  |  |  | 1 | 1 | XDI:1 | ACS880 | DI |  | 3 |  | ENB01 |  | Run |  |  | BPP2104 |  |  | BR4-2150-E-00108 | A
[7 empty] | 1 | 2 | XDI:2 |  | DI
[7 empty] | 1 | 3 | XDI:3 |  | DI |  | 3 |  | IS01 |  | Drive Isolator | Closed |  | BPP2104 |  |  | BR4-2150-E-00108 | A
[7 empty] | 1 | 6 | XDI:6 |  | DI
[7 empty] | 1 |  | STO |  | DI |  | 3 |  | VS01SY01 |  | STO Relay | Healthy |  | BPP2104 |  |  | BR4-2150-E-00108 | A
|  | ACS880 |  |  |  |  | 1 | 1 | XDI:1 | ACS880 | DI |  | 3 |  | ENB01 |  | Run |  |  | BPP2105 |  |  | BR4-2150-E-00109 | A
[7 empty] | 1 | 2 | XDI:2 |  | DI
[7 empty] | 1 | 3 | XDI:3 |  | DI |  | 3 |  | IS01 |  | Drive Isolator | Closed |  | BPP2105 |  |  | BR4-2150-E-00109 | A
[7 empty] | 1 | 6 | XDI:6 |  | DI
[7 empty] | 1 |  | STO |  | DI |  | 3 |  | VS01SY01 |  | STO Relay | Healthy |  | BPP2105 |  |  | BR4-2150-E-00109 | A
| BCV131A | VS1 |  |  |  |  | 1 |  |  | G180 NXGpro+
| BCV131A | VS1 |  |  |  |  | 1 | 0 | DI-0A | NEP01ES03 | DI |  | 3 |  | SW01 |  | Remote Inhibit |  |  | BCV131AVS01 |  |  | BR4-2150-E-00046 | A | BR4-2150-E-00519
| BCV131A | VS1 |  |  |  |  | 1 | 1 | DI-1A | NEP01ES04 | DI |  | 3 |  | SW02A |  | Remote Start |  |  | BCV131AVS01 |  |  | BR4-2150-E-00046 | A | BR4-2150-E-00519
| BCV131A | VS1 |  |  |  |  | 1 | 2 | DI-2A |  | DI |  | 3 |  | SW02B |  | Remote Stop |  |  | BCV131AVS01 |  |  | BR4-2150-E-00046 | A | BR4-2150-E-00519
| BCV131A | VS1 |  |  |  |  | 1 | 3 | DI-3A |  | DI |  | 3 |  | SW03 |  | Remot Fault Reset |  |  | BCV131AVS01 |  |  | BR4-2150-E-00046 | A | BR4-2150-E-00519
| BCV131A | VS1 |  |  |  |  | 1 | 4 | DI-0B |  | DI |  | 3 |  | SW04B |  | Sel SW-Off |  |  | BCV131AVS01 |  |  | BR4-2150-E-00046 | A | BR4-2150-E-00519
| BCV131A | VS1 |  |  |  |  | 1 | 5 | DI-1B |  | DI |  | 3 |  | SW04A |  | SEL SW-Remote |  |  | BCV131AVS01 |  |  | BR4-2150-E-00046 | A | BR4-2150-E-00519
| BCV131A | VS1 |  |  |  |  | 1 | 6 | DI-2B |  | DI |  | 3 |  |  |  | Spare |  |  | BCV131AVS01 |  |  | BR4-2150-E-00046 | A | BR4-2150-E-00519
| BCV131A | VS1 |  |  |  |  | 1 | 7 | DI-3B |  | DI |  | 3 |  | XS02 |  | Arc Flash Alarm |  |  | BCV131AVS01 |  |  | BR4-2150-E-00046 | A | BR4-2150-E-00519
| BCV131A | VS1 |  |  |  |  | 1 | 8 | DI-0C |  | DI |  | 3 |  | XS01 |  | Output Ground Switch | Closed |  | BCV131AVS01 |  |  | BR4-2150-E-00046 | A | BR4-2150-E-00519
| BCV131A | VS1 |  |  |  |  | 1 | 9 | DI-1C |  | DI |  | 3 |  | TRP05 |  | Arc Flash | Tripped |  | BCV131AVS01 |  |  | BR4-2150-E-00046 | A | BR4-2150-E-00519
| BCV131A | VS1 |  |  |  |  | 1 | 10 | DI-2C |  | DI |  | 3 |  | TRP07 |  | PCVMR Trip | Healthy |  | BCV131AVS01 |  |  | BR4-2150-E-00046 | A | BR4-2150-E-00519
| BCV131A | VS1 |  |  |  |  | 1 | 11 | DI-3C |  | DI |  | 6 |  | TS01 |  | Transformer Cabinet Thermal Over Temp Alarm | Healthy |  | BCV131AVS01 |  |  | BR4-2150-E-00046 | A | BR4-2150-E-00519
| BCV131A | VS1 |  |  |  |  | 1 | 12 | DI-0D |  | DI |  | 6 |  | TS02 |  | Transformer Cabinet Thermal Over Temp Trip | Healthy |  | BCV131AVS01 |  |  | BR4-2150-E-00046 | A | BR4-2150-E-00519
| BCV131A | VS1 |  |  |  |  | 1 | 13 | DI-1D |  | DI |  | 3 |  | TRP02 |  | Blower 1 | Healthy |  | BCV131AVS01 |  |  | BR4-2150-E-00046 | A | BR4-2150-E-00519
| BCV131A | VS1 |  |  |  |  | 1 | 14 | DI-2D |  | DI |  | 3 |  | TRP03 |  | Blower 2 | Healthy |  | BCV131AVS01 |  |  | BR4-2150-E-00046 | A | BR4-2150-E-00519
| BCV131A | VS1 |  |  |  |  | 1 | 15 | DI-3D |  | DI |  | 3 |  | TRP04 |  | Blower 3 | Healthy |  | BCV131AVS01 |  |  | BR4-2150-E-00046 | A | BR4-2150-E-00519
| BCV131A | VS1 |  |  |  |  | 1 | 16 | DI-0E |  | DI |  | 6 |  | TRP08 |  | Blower 4 | Healthy |  | BCV131AVS01 |  |  | BR4-2150-E-00046 | A | BR4-2150-E-00520
| BCV131A | VS1 |  |  |  |  | 1 | 17 | DI-1E |  | DI |  | 6 |  | TRP09 |  | Blower 5 | Healthy |  | BCV131AVS01 |  |  | BR4-2150-E-00046 | A | BR4-2150-E-00520
| BCV131A | VS1 |  |  |  |  | 1 | 18 | DI-2E |  | DI |  | 3 |  | XS03 |  | Output Disconnector | Closed |  | BCV131AVS01 |  |  | BR4-2150-E-00046 | A | BR4-2150-E-00520
| BCV131A | VS1 |  |  |  |  | 1 | 19 | DI-3E |  | DI |  | 3 |  | TRP06 |  | LFR Feedback | Healthy |  | BCV131AVS01 |  |  | BR4-2150-E-00046 | A | BR4-2150-E-00520
| BCV131A | VS1 |  |  |  |  | 1 | 0 | DO-0 |  | DO |  | 3 |  | XS04 |  | Speed Demand in Local at VFD |  |  | BCV131AVS01 |  |  | BR4-2150-E-00046 | A | BR4-2150-E-00517
| BCV131A | VS1 |  |  |  |  | 1 | 1 | DO-1 |  | DO |  | 3 |  | XS05 |  | Drive Ready to Run |  |  | BCV131AVS01 |  |  | BR4-2150-E-00046 | A | BR4-2150-E-00517
| BCV131A | VS1 |  |  |  |  | 1 | 2 | DO-2 |  | DO |  | 3 |  | XS06 |  | Drive Running |  |  | BCV131AVS01 |  |  | BR4-2150-E-00046 | A | BR4-2150-E-00517
| BCV131A | VS1 |  |  |  |  | 1 | 3 | DO-3 |  | DO |  | 3 |  | XS07 |  | Drive Alarm |  |  | BCV131AVS01 |  |  | BR4-2150-E-00046 | A | BR4-2150-E-00517
| BCV131A | VS1 |  |  |  |  | 1 | 4 | DO-4 |  | DO |  | 6 |  | XS08 |  | Drive Fault |  |  | BCV131AVS01 |  |  | BR4-2150-E-00046 | A | BR4-2150-E-00517
| BCV131A | VS1 |  |  |  |  | 1 | 5 | DO-5 |  | DO |  | 3 |  |  |  | Spare |  |  | BCV131AVS01 |  |  | BR4-2150-E-00046 | A | BR4-2150-E-00517
| BCV131A | VS1 |  |  |  |  | 1 | 6 | DO-6 |  | DO |  | 3 |  |  |  | Spare |  |  | BCV131AVS01 |  |  | BR4-2150-E-00046 | A | BR4-2150-E-00517
| BCV131A | VS1 |  |  |  |  | 1 | 7 | DO-7 |  | DO |  | 3 |  | XS09 |  | VSD Running Interlock |  |  | BCV131AVS01 |  |  | BR4-2150-E-00046 | A | BR4-2150-E-00517
| BCV131A | VS1 |  |  |  |  | 1 | 8 | DO-8 |  | DO |  | 3 |  | SR01 |  | Blower 1 Control |  |  | BCV131AVS01 |  |  | BR4-2150-E-00046 | A | BR4-2150-E-00518
| BCV131A | VS1 |  |  |  |  | 1 | 9 | DO-9 |  | DO |  | 3 |  | SR02 |  | Blower 2 Control |  |  | BCV131AVS01 |  |  | BR4-2150-E-00046 | A | BR4-2150-E-00518
| BCV131A | VS1 |  |  |  |  | 1 | 10 | DO-10 |  | DO |  | 3 |  | SR03 |  | Blower 3 Control |  |  | BCV131AVS01 |  |  | BR4-2150-E-00046 | A | BR4-2150-E-00518
| BCV131A | VS1 |  |  |  |  | 1 | 11 | DO-11 |  | DO |  | 6 |  | SR06 |  | Blower 4 Control |  |  | BCV131AVS01 |  |  | BR4-2150-E-00046 | A | BR4-2150-E-00518
| BCV131A | VS1 |  |  |  |  | 1 | 12 | DO-12 |  | DO |  | 6 |  | SR07 |  | Blower 5 Control |  |  | BCV131AVS01 |  |  | BR4-2150-E-00046 | A | BR4-2150-E-00518
| BCV131A | VS1 |  |  |  |  | 1 | 13 | DO-13 |  | DO |  | 6 |  | XS10 |  | Spare |  |  | BCV131AVS01 |  |  | BR4-2150-E-00046 | A | BR4-2150-E-00518
| BCV131A | VS1 |  |  |  |  | 1 | 14 | DO-14 |  | DO |  | 3 |  | SR04 |  | Arc Flash Trip Reset |  |  | BCV131AVS01 |  |  | BR4-2150-E-00046 | A | BR4-2150-E-00518
| BCV131A | VS1 |  |  |  |  | 1 | 15 | DO-15 |  | DO |  | 3 |  | SR05 |  | Fault Lock |  |  | BCV131AVS01 |  |  | BR4-2150-E-00046 | A | BR4-2150-E-00518
| BCV131B | VS1 |  |  |  |  | 1 |  |  | G180 NXGpro+
| BCV131B | VS1 |  |  |  |  | 1 | 0 | DI-0A | NEP1ES3 | DI |  | 3 |  | SW01 |  | Remote Inhibit |  |  | BCV131BVS01 |  |  | BR4-2150-E-00049 | A | BR4-2150-E-00579
| BCV131B | VS1 |  |  |  |  | 1 | 1 | DI-1A | NEP1ES4 | DI |  | 3 |  | SW02A |  | Remote Start |  |  | BCV131BVS01 |  |  | BR4-2150-E-00049 | A | BR4-2150-E-00579
| BCV131B | VS1 |  |  |  |  | 1 | 2 | DI-2A |  | DI |  | 3 |  | SW02B |  | Remote Stop |  |  | BCV131BVS01 |  |  | BR4-2150-E-00049 | A | BR4-2150-E-00579
| BCV131B | VS1 |  |  |  |  | 1 | 3 | DI-3A |  | DI |  | 3 |  | SW03 |  | Remot Fault Reset |  |  | BCV131BVS01 |  |  | BR4-2150-E-00049 | A | BR4-2150-E-00579
| BCV131B | VS1 |  |  |  |  | 1 | 4 | DI-0B |  | DI |  | 3 |  | SW04B |  | Sel SW-Off |  |  | BCV131BVS01 |  |  | BR4-2150-E-00049 | A | BR4-2150-E-00579
| BCV131B | VS1 |  |  |  |  | 1 | 5 | DI-1B |  | DI |  | 3 |  | SW04A |  | SEL SW-Remote |  |  | BCV131BVS01 |  |  | BR4-2150-E-00049 | A | BR4-2150-E-00579
| BCV131B | VS1 |  |  |  |  | 1 | 6 | DI-2B |  | DI |  | 3 |  |  |  | Spare |  |  | BCV131BVS01 |  |  | BR4-2150-E-00049 | A | BR4-2150-E-00579
| BCV131B | VS1 |  |  |  |  | 1 | 7 | DI-3B |  | DI |  | 3 |  | XS02 |  | Arc Flash Alarm |  |  | BCV131BVS01 |  |  | BR4-2150-E-00049 | A | BR4-2150-E-00579
| BCV131B | VS1 |  |  |  |  | 1 | 8 | DI-0C |  | DI |  | 3 |  | XS01 |  | Output Ground Switch | Closed |  | BCV131BVS01 |  |  | BR4-2150-E-00049 | A | BR4-2150-E-00579
| BCV131B | VS1 |  |  |  |  | 1 | 9 | DI-1C |  | DI |  | 3 |  | TRP05 |  | Arc Flash | Tripped |  | BCV131BVS01 |  |  | BR4-2150-E-00049 | A | BR4-2150-E-00579
| BCV131B | VS1 |  |  |  |  | 1 | 10 | DI-2C |  | DI |  | 3 |  | TRP07 |  | PCVMR Trip | Healthy |  | BCV131BVS01 |  |  | BR4-2150-E-00049 | A | BR4-2150-E-00579
| BCV131B | VS1 |  |  |  |  | 1 | 11 | DI-3C |  | DI |  | 6 |  | TS01 |  | Transformer Cabinet Thermal Over Temp Alarm | Healthy |  | BCV131BVS01 |  |  | BR4-2150-E-00049 | A | BR4-2150-E-00579
| BCV131B | VS1 |  |  |  |  | 1 | 12 | DI-0D |  | DI |  | 6 |  | TS02 |  | Transformer Cabinet Thermal Over Temp Trip | Healthy |  | BCV131BVS01 |  |  | BR4-2150-E-00049 | A | BR4-2150-E-00579
| BCV131B | VS1 |  |  |  |  | 1 | 13 | DI-1D |  | DI |  | 3 |  | TRP02 |  | Blower 1 | Healthy |  | BCV131BVS01 |  |  | BR4-2150-E-00049 | A | BR4-2150-E-00579
| BCV131B | VS1 |  |  |  |  | 1 | 14 | DI-2D |  | DI |  | 3 |  | TRP03 |  | Blower 2 | Healthy |  | BCV131BVS01 |  |  | BR4-2150-E-00049 | A | BR4-2150-E-00579
| BCV131B | VS1 |  |  |  |  | 1 | 15 | DI-3D |  | DI |  | 3 |  | TRP04 |  | Blower 3 | Healthy |  | BCV131BVS01 |  |  | BR4-2150-E-00049 | A | BR4-2150-E-00579
| BCV131B | VS1 |  |  |  |  | 1 | 16 | DI-0E |  | DI |  | 6 |  | TRP08 |  | Blower 4 | Healthy |  | BCV131BVS01 |  |  | BR4-2150-E-00049 | A | BR4-2150-E-00580
| BCV131B | VS1 |  |  |  |  | 1 | 17 | DI-1E |  | DI |  | 6 |  | TRP09 |  | Blower 5 | Healthy |  | BCV131BVS01 |  |  | BR4-2150-E-00049 | A | BR4-2150-E-00580
| BCV131B | VS1 |  |  |  |  | 1 | 18 | DI-2E |  | DI |  | 3 |  | XS03 |  | Output Disconnector | Closed |  | BCV131BVS01 |  |  | BR4-2150-E-00049 | A | BR4-2150-E-00580
| BCV131B | VS1 |  |  |  |  | 1 | 19 | DI-3E |  | DI |  | 3 |  | TRP06 |  | LFR Feedback | Healthy |  | BCV131BVS01 |  |  | BR4-2150-E-00049 | A | BR4-2150-E-00580
| BCV131B | VS1 |  |  |  |  | 1 | 0 | DO-0 |  | DO |  | 3 |  | XS04 |  | Speed Demand in Local at VFD |  |  | BCV131BVS01 |  |  | BR4-2150-E-00049 | A | BR4-2150-E-00577
| BCV131B | VS1 |  |  |  |  | 1 | 1 | DO-1 |  | DO |  | 3 |  | XS05 |  | Drive Ready to Run |  |  | BCV131BVS01 |  |  | BR4-2150-E-00049 | A | BR4-2150-E-00577
| BCV131B | VS1 |  |  |  |  | 1 | 2 | DO-2 |  | DO |  | 3 |  | XS06 |  | Drive Running |  |  | BCV131BVS01 |  |  | BR4-2150-E-00049 | A | BR4-2150-E-00577
| BCV131B | VS1 |  |  |  |  | 1 | 3 | DO-3 |  | DO |  | 3 |  | XS07 |  | Drive Alarm |  |  | BCV131BVS01 |  |  | BR4-2150-E-00049 | A | BR4-2150-E-00577
| BCV131B | VS1 |  |  |  |  | 1 | 4 | DO-4 |  | DO |  | 6 |  | XS08 |  | Drive Fault |  |  | BCV131BVS01 |  |  | BR4-2150-E-00049 | A | BR4-2150-E-00577
| BCV131B | VS1 |  |  |  |  | 1 | 5 | DO-5 |  | DO |  | 3 |  |  |  | Spare |  |  | BCV131BVS01 |  |  | BR4-2150-E-00049 | A | BR4-2150-E-00577
| BCV131B | VS1 |  |  |  |  | 1 | 6 | DO-6 |  | DO |  | 3 |  |  |  | Spare |  |  | BCV131BVS01 |  |  | BR4-2150-E-00049 | A | BR4-2150-E-00577
| BCV131B | VS1 |  |  |  |  | 1 | 7 | DO-7 |  | DO |  | 3 |  | XS09 |  | VSD Running Interlock |  |  | BCV131BVS01 |  |  | BR4-2150-E-00049 | A | BR4-2150-E-00577
| BCV131B | VS1 |  |  |  |  | 1 | 8 | DO-8 |  | DO |  | 3 |  | SR01 |  | Blower 1 Control |  |  | BCV131BVS01 |  |  | BR4-2150-E-00049 | A | BR4-2150-E-00578
| BCV131B | VS1 |  |  |  |  | 1 | 9 | DO-9 |  | DO |  | 3 |  | SR02 |  | Blower 2 Control |  |  | BCV131BVS01 |  |  | BR4-2150-E-00049 | A | BR4-2150-E-00578
| BCV131B | VS1 |  |  |  |  | 1 | 10 | DO-10 |  | DO |  | 3 |  | SR03 |  | Blower 3 Control |  |  | BCV131BVS01 |  |  | BR4-2150-E-00049 | A | BR4-2150-E-00578
| BCV131B | VS1 |  |  |  |  | 1 | 11 | DO-11 |  | DO |  | 6 |  | SR06 |  | Blower 4 Control |  |  | BCV131BVS01 |  |  | BR4-2150-E-00049 | A | BR4-2150-E-00578
| BCV131B | VS1 |  |  |  |  | 1 | 12 | DO-12 |  | DO |  | 6 |  | SR07 |  | Blower 5 Control |  |  | BCV131BVS01 |  |  | BR4-2150-E-00049 | A | BR4-2150-E-00578
| BCV131B | VS1 |  |  |  |  | 1 | 13 | DO-13 |  | DO |  | 6 |  | XS10 |  | Spare |  |  | BCV131BVS01 |  |  | BR4-2150-E-00049 | A | BR4-2150-E-00578
| BCV131B | VS1 |  |  |  |  | 1 | 14 | DO-14 |  | DO |  | 3 |  | SR04 |  | Arc Flash Trip Reset |  |  | BCV131BVS01 |  |  | BR4-2150-E-00049 | A | BR4-2150-E-00578
| BCV131B | VS1 |  |  |  |  | 1 | 15 | DO-15 |  | DO |  | 3 |  | SR05 |  | Fault Lock |  |  | BCV131BVS01 |  |  | BR4-2150-E-00049 | A | BR4-2150-E-00578
| BCV131C | VS1 |  |  |  |  | 1 |  |  | G180 NXGpro+
| BCV131C | VSD3 |  |  |  |  | 1 | 0 | DI-0A | NEP1ES5 | DI |  | 3 |  | SW01 |  | Remote Inhibit |  |  | BCV131CVS01 |  |  | BR4-2150-E-00052 | A | BR4-2150-E-00639
| BCV131C | VSD3 |  |  |  |  | 1 | 1 | DI-1A | DX2ES2 | DI |  | 3 |  | SW02A |  | Remote Start |  |  | BCV131CVS01 |  |  | BR4-2150-E-00052 | A | BR4-2150-E-00639
| BCV131C | VSD3 |  |  |  |  | 1 | 2 | DI-2A |  | DI |  | 3 |  | SW02B |  | Remote Stop |  |  | BCV131CVS01 |  |  | BR4-2150-E-00052 | A | BR4-2150-E-00639
| BCV131C | VSD3 |  |  |  |  | 1 | 3 | DI-3A |  | DI |  | 3 |  | SW03 |  | Remot Fault Reset |  |  | BCV131CVS01 |  |  | BR4-2150-E-00052 | A | BR4-2150-E-00639
| BCV131C | VSD3 |  |  |  |  | 1 | 4 | DI-0B |  | DI |  | 3 |  | SW04B |  | Sel SW-Off |  |  | BCV131CVS01 |  |  | BR4-2150-E-00052 | A | BR4-2150-E-00639
| BCV131C | VSD3 |  |  |  |  | 1 | 5 | DI-1B |  | DI |  | 3 |  | SW04A |  | SEL SW-Remote |  |  | BCV131CVS01 |  |  | BR4-2150-E-00052 | A | BR4-2150-E-00639
| BCV131C | VSD3 |  |  |  |  | 1 | 6 | DI-2B |  | DI |  | 3 |  |  |  | Spare |  |  | BCV131CVS01 |  |  | BR4-2150-E-00052 | A | BR4-2150-E-00639
| BCV131C | VSD3 |  |  |  |  | 1 | 7 | DI-3B |  | DI |  | 3 |  | XS02 |  | Arc Flash Alarm |  |  | BCV131CVS01 |  |  | BR4-2150-E-00052 | A | BR4-2150-E-00639
| BCV131C | VSD3 |  |  |  |  | 1 | 8 | DI-0C |  | DI |  | 3 |  | XS01 |  | Output Ground Switch | Closed |  | BCV131CVS01 |  |  | BR4-2150-E-00052 | A | BR4-2150-E-00639
| BCV131C | VSD3 |  |  |  |  | 1 | 9 | DI-1C |  | DI |  | 3 |  | TRP05 |  | Arc Flash | Tripped |  | BCV131CVS01 |  |  | BR4-2150-E-00052 | A | BR4-2150-E-00639
| BCV131C | VSD3 |  |  |  |  | 1 | 10 | DI-2C |  | DI |  | 3 |  | TRP07 |  | PCVMR Trip | Healthy |  | BCV131CVS01 |  |  | BR4-2150-E-00052 | A | BR4-2150-E-00639
| BCV131C | VSD3 |  |  |  |  | 1 | 11 | DI-3C |  | DI |  | 6 |  | TS01 |  | Transformer Cabinet Thermal Over Temp Alarm | Healthy |  | BCV131CVS01 |  |  | BR4-2150-E-00052 | A | BR4-2150-E-00639
| BCV131C | VSD3 |  |  |  |  | 1 | 12 | DI-0D |  | DI |  | 6 |  | TS02 |  | Transformer Cabinet Thermal Over Temp Trip | Healthy |  | BCV131CVS01 |  |  | BR4-2150-E-00052 | A | BR4-2150-E-00639
| BCV131C | VSD3 |  |  |  |  | 1 | 13 | DI-1D |  | DI |  | 3 |  | TRP02 |  | Blower 1 | Healthy |  | BCV131CVS01 |  |  | BR4-2150-E-00052 | A | BR4-2150-E-00639
| BCV131C | VSD3 |  |  |  |  | 1 | 14 | DI-2D |  | DI |  | 3 |  | TRP03 |  | Blower 2 | Healthy |  | BCV131CVS01 |  |  | BR4-2150-E-00052 | A | BR4-2150-E-00639
| BCV131C | VSD3 |  |  |  |  | 1 | 15 | DI-3D |  | DI |  | 3 |  | TRP04 |  | Blower 3 | Healthy |  | BCV131CVS01 |  |  | BR4-2150-E-00052 | A | BR4-2150-E-00639
| BCV131C | VSD3 |  |  |  |  | 1 | 16 | DI-0E |  | DI |  | 6 |  | TRP08 |  | Blower 4 | Healthy |  | BCV131CVS01 |  |  | BR4-2150-E-00052 | A | BR4-2150-E-00640
| BCV131C | VSD3 |  |  |  |  | 1 | 17 | DI-1E |  | DI |  | 6 |  | TRP09 |  | Blower 5 | Healthy |  | BCV131CVS01 |  |  | BR4-2150-E-00052 | A | BR4-2150-E-00640
| BCV131C | VSD3 |  |  |  |  | 1 | 18 | DI-2E |  | DI |  | 3 |  | XS03 |  | Output Disconnector | Closed |  | BCV131CVS01 |  |  | BR4-2150-E-00052 | A | BR4-2150-E-00640
| BCV131C | VSD3 |  |  |  |  | 1 | 19 | DI-3E |  | DI |  | 3 |  | TRP06 |  | LFR Feedback | Healthy |  | BCV131CVS01 |  |  | BR4-2150-E-00052 | A | BR4-2150-E-00640
| BCV131C | VSD3 |  |  |  |  | 1 | 0 | DO-0 |  | DO |  | 3 |  | XS04 |  | Speed Demand in Local at VFD |  |  | BCV131CVS01 |  |  | BR4-2150-E-00052 | A | BR4-2150-E-00637
| BCV131C | VSD3 |  |  |  |  | 1 | 1 | DO-1 |  | DO |  | 3 |  | XS05 |  | Drive Ready to Run |  |  | BCV131CVS01 |  |  | BR4-2150-E-00052 | A | BR4-2150-E-00637
| BCV131C | VSD3 |  |  |  |  | 1 | 2 | DO-2 |  | DO |  | 3 |  | XS06 |  | Drive Running |  |  | BCV131CVS01 |  |  | BR4-2150-E-00052 | A | BR4-2150-E-00637
| BCV131C | VSD3 |  |  |  |  | 1 | 3 | DO-3 |  | DO |  | 3 |  | XS07 |  | Drive Alarm |  |  | BCV131CVS01 |  |  | BR4-2150-E-00052 | A | BR4-2150-E-00637
| BCV131C | VSD3 |  |  |  |  | 1 | 4 | DO-4 |  | DO |  | 6 |  | XS08 |  | Drive Fault |  |  | BCV131CVS01 |  |  | BR4-2150-E-00052 | A | BR4-2150-E-00637
| BCV131C | VSD3 |  |  |  |  | 1 | 5 | DO-5 |  | DO |  | 3 |  |  |  | Spare |  |  | BCV131CVS01 |  |  | BR4-2150-E-00052 | A | BR4-2150-E-00637
| BCV131C | VSD3 |  |  |  |  | 1 | 6 | DO-6 |  | DO |  | 3 |  |  |  | Spare |  |  | BCV131CVS01 |  |  | BR4-2150-E-00052 | A | BR4-2150-E-00637
| BCV131C | VSD3 |  |  |  |  | 1 | 7 | DO-7 |  | DO |  | 3 |  | XS09 |  | VSD Running Interlock |  |  | BCV131CVS01 |  |  | BR4-2150-E-00052 | A | BR4-2150-E-00637
| BCV131C | VSD3 |  |  |  |  | 1 | 8 | DO-8 |  | DO |  | 3 |  | SR01 |  | Blower 1 Control |  |  | BCV131CVS01 |  |  | BR4-2150-E-00052 | A | BR4-2150-E-00638
| BCV131C | VSD3 |  |  |  |  | 1 | 9 | DO-9 |  | DO |  | 3 |  | SR02 |  | Blower 2 Control |  |  | BCV131CVS01 |  |  | BR4-2150-E-00052 | A | BR4-2150-E-00638
| BCV131C | VSD3 |  |  |  |  | 1 | 10 | DO-10 |  | DO |  | 3 |  | SR03 |  | Blower 3 Control |  |  | BCV131CVS01 |  |  | BR4-2150-E-00052 | A | BR4-2150-E-00638
| BCV131C | VSD3 |  |  |  |  | 1 | 11 | DO-11 |  | DO |  | 6 |  | SR06 |  | Blower 4 Control |  |  | BCV131CVS01 |  |  | BR4-2150-E-00052 | A | BR4-2150-E-00638
| BCV131C | VSD3 |  |  |  |  | 1 | 12 | DO-12 |  | DO |  | 6 |  | SR07 |  | Blower 5 Control |  |  | BCV131CVS01 |  |  | BR4-2150-E-00052 | A | BR4-2150-E-00638
| BCV131C | VSD3 |  |  |  |  | 1 | 13 | DO-13 |  | DO |  | 6 |  | XS10 |  | Spare |  |  | BCV131CVS01 |  |  | BR4-2150-E-00052 | A | BR4-2150-E-00638
| BCV131C | VSD3 |  |  |  |  | 1 | 14 | DO-14 |  | DO |  | 3 |  | SR04 |  | Arc Flash Trip Reset |  |  | BCV131CVS01 |  |  | BR4-2150-E-00052 | A | BR4-2150-E-00638
| BCV131C | VSD3 |  |  |  |  | 1 | 15 | DO-15 |  | DO |  | 3 |  | SR05 |  | Fault Lock |  |  | BCV131CVS01 |  |  | BR4-2150-E-00052 | A | BR4-2150-E-00638
|  | PR |  |  |  |  | 1 |  |  | MASTERPACT_VAMP |  |  | 3 | [6 empty] | BMC1322INC01 |  |  | BR4-2150-E-00083 | A | Process Bus A Incomer
|  | PR |  |  |  |  | 1 |  | VAMP RJ45 | DX01ES01 |  |  | 3
|  | PR |  |  |  |  | 1 |  | CUB RJ45 | DX01ES01 |  |  | 3
|  | PR |  |  |  |  | 1 |  |  | MASTERPACT |  |  | 3 | [6 empty] | BMC1322INC02 |  |  | BR4-2150-E-00085 | A | Essential Bus Incomer
|  | PR |  |  |  |  | 1 | [5 empty] | 3
|  | PR |  |  |  |  | 1 |  | CUB RJ45 | DX01ES01 |  |  | 3
|  | PR |  |  |  |  | 1 |  |  | MASTERPACT |  |  | 3 | [6 empty] | BMC1322INC03 |  |  | BR4-2150-E-00087 | A | Generator Incomer
|  | PR |  |  |  |  | 1 | [5 empty] | 3
|  | PR |  |  |  |  | 1 |  | CUB RJ45 | DX01ES01 |  |  | 3
|  | SHMI1 | [6 empty] | X1 | NEP01ES04 | DO |  | 3 |  |  |  | Spare |  |  | BMC1321SHMI1
|  | PR1 |  |  |  |  | G | RF | X1G 3/4/5 | REX640 SLOT G | DO |  | 3 |  | XS10 |  | Relay Internal | Fault |  | BMC1321INC01 |  |  | BR4-2150-E-00034 | A
|  | PR1 |  |  |  |  | G | SO1 | X1G 6/7/8 | NEP01ES04 | DO |  | 3 |  | XS08A |  | Disconnector Switch (Command) | Close |  | BMC1321INC01 |  |  | BR4-2150-E-00034 | A
|  | PR1 |  |  |  |  | G | SO2 | X1G 9/10 |  | DO |  | 3 |  | XS08B |  | Disconnector Switch (Command) | Open |  | BMC1321INC01 |  |  | BR4-2150-E-00034 | A
|  | PR1 |  |  |  |  | G | SSO1 | X1G 11/12 |  | DO |  | 3 |  |  |  | Spare |  |  | BMC1321INC01 |  |  | BR4-2150-E-00034 | A
|  | PR1 |  |  |  |  | G | SSO2 | X1G 13/14 |  | DO |  | 3 |  |  |  | Spare |  |  | BMC1321INC01 |  |  | BR4-2150-E-00034 | A
|  | PR1 |  |  |  |  | G | POSP1 | X1G 15/16 |  | DO |  | 3 |  | XS09A |  | Circuit Breaker (Command) | Close |  | BMC1321INC01 |  |  | BR4-2150-E-00034 | A
|  | PR1 |  |  |  |  | G | POSP2 | X1G 17/18 |  | DO |  | 3 |  | XS09B |  | Circuit Breaker (Command) | Open |  | BMC1321INC01 |  |  | BR4-2150-E-00034 | A
|  | PR1 |  |  |  |  | G | SO3 | X2G 1/2/3 |  | DO |  | 3 |  |  |  | Spare | Healthy |  | BMC1321INC01 |  |  | BR4-2150-E-00034 | A
|  | PR1 |  |  |  |  | G | PODP1 | X2G 4/6/21/7/8 |  | DI |  | 3 |  | TRP01 |  | Protection Trip and Trip Circuit Supervision | Tripped |  | BMC1321INC01 |  |  | BR4-2150-E-00034 | A
|  | PR1 |  |  |  |  | G | PODP2 | X2G 9/10/11/12/13 |  | DI |  | 3 |  | TRP02 |  | Arc Fault to Upstream | Tripped |  | BMC1321INC01 |  |  | BR4-2150-E-00034 | A
|  | PR1 |  |  |  |  | G | PODP3 | X2G 14/16/21/17/18 |  | DIO |  | 3 |  |  |  | Spare |  |  | BMC1321INC01 |  |  | BR4-2150-E-00034 | A
|  | PR1 |  |  |  |  | B | BI1 | X1B 1/4 | REX640 SLOT B | DI |  | 3 |  | CB01A |  | Circuit Breaker | Closed |  | BMC1321INC01 |  |  | BR4-2150-E-00034 | A
|  | PR1 |  |  |  |  | B | BI2 | X1B 2/4 |  | DI |  | 3 |  | CB01B |  | Circuit Breaker | Open |  | BMC1321INC01 |  |  | BR4-2150-E-00034 | A
|  | PR1 |  |  |  |  | B | BI3 | X1B 3/4 |  | DI |  | 3 |  | XS04 |  | Circuit Breaker Spring | Charged |  | BMC1321INC01 |  |  | BR4-2150-E-00034 | A
|  | PR1 |  |  |  |  | B | BI4 | X1B 5/8 |  | DI |  | 3 |  | XS01A |  | Disconnector | Closed |  | BMC1321INC01 |  |  | BR4-2150-E-00034 | A
|  | PR1 |  |  |  |  | B | BI5 | X1B 6/8 |  | DI |  | 3 |  | XS01B |  | Disconnector | Open |  | BMC1321INC01 |  |  | BR4-2150-E-00034 | A
|  | PR1 |  |  |  |  | B | BI6 | X1B 7/8 |  | DI |  | 3 |  | XS02A |  | Earth Switch | Closed |  | BMC1321INC01 |  |  | BR4-2150-E-00034 | A
|  | PR1 |  |  |  |  | B | BI7 | X1B 9/12 |  | DI |  | 3 |  | XS02B |  | Earth Switch | Open |  | BMC1321INC01 |  |  | BR4-2150-E-00034 | A
|  | PR1 |  |  |  |  | B | BI8 | X1B 10/12 |  | DI |  | 3 |  | XS03A |  | Gas Pressure | Healthy |  | BMC1321INC01 |  |  | BR4-2150-E-00034 | A
|  | PR1 |  |  |  |  | B | BI9 | X1B 11/12 |  | DI |  | 3 |  | XS03B |  | Gas Pressure | High |  | BMC1321INC01 |  |  | BR4-2150-E-00034 | A
|  | PR1 |  |  |  |  | B | BI10 | X1B 13/16 |  | DI |  | 3 |  | XS03C |  | Gas Pressure | Low |  | BMC1321INC01 |  |  | BR4-2150-E-00034 | A
|  | PR1 |  |  |  |  | B | BI11 | X1B 14/16 |  | DI |  | 3 |  | CB02 |  | Control Supply MCBs | Healthy |  | BMC1321INC01 |  |  | BR4-2150-E-00034 | A
|  | PR1 |  |  |  |  | B | BI12 | X1B 15/16 |  | DI |  | 3 |  | CB03 |  | Motor Control Supply MCBs | Healthy |  | BMC1321INC01 |  |  | BR4-2150-E-00034 | A
|  | PR1 |  |  |  |  | B | BI13 | X1B 17/18 |  | DI |  | 3 |  |  |  | Spare |  |  | BMC1321INC01 |  |  | BR4-2150-E-00034 | A
|  | PR1 |  |  |  |  | B | BI14 | X2B 1/2 |  | DI |  | 3 |  |  |  | Spare |  |  | BMC1321INC01 |  |  | BR4-2150-E-00034 | A
|  | PR1 |  |  |  |  | B | SO1 | X2B 3/4 |  | DO |  | 3 |  |  |  | Spare |  |  | BMC1321INC01 |  |  | BR4-2150-E-00034 | A
|  | PR1 |  |  |  |  | B | SO2 | X2B 5/6 |  | DO |  | 3 |  |  |  | Spare |  |  | BMC1321INC01 |  |  | BR4-2150-E-00034 | A
|  | PR1 |  |  |  |  | B | SO3 | X2B 7/8 |  | DO |  | 3 |  |  |  | Spare |  |  | BMC1321INC01 |  |  | BR4-2150-E-00034 | A
|  | PR1 |  |  |  |  | B | SO4 | X2B 9/10 |  | DO |  | 3 |  |  |  | Spare |  |  | BMC1321INC01 |  |  | BR4-2150-E-00034 | A
|  | PR1 |  |  |  |  | B | SO5 | X2B 11/12 |  | DO |  | 3 |  |  |  | Spare |  |  | BMC1321INC01 |  |  | BR4-2150-E-00034 | A
|  | PR1 |  |  |  |  | B | SO6 | X2B 13/14 |  | DO |  | 3 |  |  |  | Spare |  |  | BMC1321INC01 |  |  | BR4-2150-E-00034 | A
|  | PR1 |  |  |  |  | B | SO7 | X2B 15/16 |  | DO |  | 3 |  |  |  | Spare |  |  | BMC1321INC01 |  |  | BR4-2150-E-00034 | A
|  | PR1 |  |  |  |  | B | SO8 | X2B 17/18 |  | DO |  | 3 |  |  |  | Spare |  |  | BMC1321INC01 |  |  | BR4-2150-E-00034 | A
|  | PR1 |  |  |  |  | C | BI1 | X1C 1/4 | REX640 SLOT C | DI |  | 3 |  | XS06 |  | Cable Side No Power |  |  | BMC1321INC01 |  |  | BR4-2150-E-00034 | A
|  | PR1 |  |  |  |  | C | BI2 | X1C 2/4 |  | DI |  | 3 |  | SW01A |  | Local Mode | Selected |  | BMC1321INC01 |  |  | BR4-2150-E-00034 | A
|  | PR1 |  |  |  |  | C | BI3 | X1C 3/4 |  | DI |  | 3 |  | SW01B |  | Remote Mode | Selected |  | BMC1321INC01 |  |  | BR4-2150-E-00034 | A
|  | PR1 |  |  |  |  | C | BI4 | X1C 5/8 |  | DI |  | 3 |  | SW02 |  | Circuit Breaker Spring Charge Control Supply Switch | Closed |  | BMC1321INC01 |  |  | BR4-2150-E-00034 | A
|  | PR1 |  |  |  |  | C | BI5 | X1C 6/8 |  | DI |  | 3 |  | SW03 |  | TPS Control Supply Switch | Closed |  | BMC1321INC01 |  |  | BR4-2150-E-00034 | A
|  | PR1 |  |  |  |  | C | BI6 | X1C 7/8 |  | DI |  | 3 |  | CB04 |  | Voltage Transformer MCB | Closed |  | BMC1321INC01 |  |  | BR4-2150-E-00034 | A
|  | PR1 |  |  |  |  | C | BI7 | X1C 9/12 |  | DI |  | 3 |  |  |  | Spare |  |  | BMC1321INC01 |  |  | BR4-2150-E-00034 | A
|  | PR1 |  |  |  |  | C | BI8 | X1C 10/12 |  | DI |  | 3 |  | XS07 |  | Arc Fault | Healthy |  | BMC1321INC01 |  |  | BR4-2150-E-00034 | A
|  | PR1 |  |  |  |  | C | BI9 | X1C 11/12 |  | DI |  | 3 |  |  |  | Spare |  |  | BMC1321INC01 |  |  | BR4-2150-E-00034 | A
|  | PR1 |  |  |  |  | C | BI10 | X1C 13/16 |  | DI |  | 3 |  | TRP03 |  | Inter Trip from Upstream | Activated |  | BMC1321INC01 |  |  | BR4-2150-E-00034 | A
|  | PR1 |  |  |  |  | C | BI11 | X1C 14/16 |  | DI |  | 3 |  | TRP04 |  | Inter Trip Signal form Shutdown Button | Activated |  | BMC1321INC01 |  |  | BR4-2150-E-00034 | A
|  | PR1 |  |  |  |  | C | BI12 | X1C 15/16 |  | DI |  | 3 |  | TRP05 |  | Inter Trip Signal from Fire Panel | Activated |  | BMC1321INC01 |  |  | BR4-2150-E-00034 | A
|  | PR1 |  |  |  |  | C | BI13 | X1C 17/18 |  | DI |  | 3 |  |  |  | Spare |  |  | BMC1321INC01 |  |  | BR4-2150-E-00034 | A
|  | PR1 |  |  |  |  | C | BI14 | X2C 1/2 |  | DI |  | 3 |  |  |  | Spare |  |  | BMC1321INC01 |  |  | BR4-2150-E-00034 | A
|  | PR1 |  |  |  |  | C | SO1 | X2C 3/4 |  | DO |  | 3 |  | XS11 |  | Circuit Breaker Closing (Blocking Command) | Release |  | BMC1321INC01 |  |  | BR4-2150-E-00034 | A
|  | PR1 |  |  |  |  | C | SO2 | XCC 5/6 |  | DO |  | 3 |  | XS05A |  | Earth Switch (Command) | Close |  | BMC1321INC01 |  |  | BR4-2150-E-00034 | A
|  | PR1 |  |  |  |  | C | SO3 | XCC 7/8 |  | DO |  | 3 |  | XS05B |  | Earth Switch (Command) | Open |  | BMC1321INC01 |  |  | BR4-2150-E-00034 | A
|  | PR1 |  |  |  |  | C | SO4 | XCC 9/10 |  | DO |  | 3 |  |  |  | Spare |  |  | BMC1321INC01 |  |  | BR4-2150-E-00034 | A
|  | PR1 |  |  |  |  | C | SO5 | XCC 11/12 |  | DO |  | 3 |  |  |  | Spare |  |  | BMC1321INC01 |  |  | BR4-2150-E-00034 | A
|  | PR1 |  |  |  |  | C | SO6 | XCC 13/14 |  | DO |  | 3 |  |  |  | Spare |  |  | BMC1321INC01 |  |  | BR4-2150-E-00034 | A
|  | PR1 |  |  |  |  | C | SO7 | XCC 15/16 |  | DO |  | 3 |  |  |  | Spare |  |  | BMC1321INC01 |  |  | BR4-2150-E-00034 | A
|  | PR1 |  |  |  |  | C | SO8 | XCC 17/18 |  | DO |  | 3 |  |  |  | Spare |  |  | BMC1321INC01 |  |  | BR4-2150-E-00034 | A
|  | PR2 |  |  |  |  | G | RF | X1G 3/4/5 | REX640 SLOT G | DO |  | 3 |  | XS10 |  | Relay Internal | Fault |  | BMC1321FDR01 |  |  | BR4-2150-E-00037 | A | BCV131AVS01
|  | PR2 |  |  |  |  | G | SO1 | X1G 6/7/8 | NEP01ES04 | DO |  | 3 |  | XS08A |  | Disconnector Switch (Command) | Close |  | BMC1321FDR01 |  |  | BR4-2150-E-00037 | A
|  | PR2 |  |  |  |  | G | SO2 | X1G 9/10 |  | DO |  | 3 |  | XS08B |  | Disconnector Switch (Command) | Open |  | BMC1321FDR01 |  |  | BR4-2150-E-00037 | A
|  | PR2 |  |  |  |  | G | SSO1 | X1G 11/12 |  | DO |  | 3 |  |  |  | Spare |  |  | BMC1321FDR01 |  |  | BR4-2150-E-00037 | A
|  | PR2 |  |  |  |  | G | SSO2 | X1G 13/14 |  | DO |  | 3 |  |  |  | Spare |  |  | BMC1321FDR01 |  |  | BR4-2150-E-00037 | A
|  | PR2 |  |  |  |  | G | POSP1 | X1G 15/16 |  | DO |  | 3 |  | XS09A |  | Circuit Breaker (Command) | Close |  | BMC1321FDR01 |  |  | BR4-2150-E-00037 | A
|  | PR2 |  |  |  |  | G | POSP2 | X1G 17/18 |  | DO |  | 3 |  | XS09B |  | Circuit Breaker (Command) | Open |  | BMC1321FDR01 |  |  | BR4-2150-E-00037 | A
|  | PR2 |  |  |  |  | G | SO3 | X2G 1/2/3 |  | DO |  | 3 |  |  |  | Spare | Healthy |  | BMC1321FDR01 |  |  | BR4-2150-E-00037 | A
|  | PR2 |  |  |  |  | G | PODP1 | X2G 4/6/21/7/8 |  | DI |  | 3 |  | TRP01 |  | Protection Trip and Trip Circuit Supervision | Tripped |  | BMC1321FDR01 |  |  | BR4-2150-E-00037 | A
|  | PR2 |  |  |  |  | G | PODP2 | X2G 9/10/11/12/13 |  | DI |  | 3 |  | TRP02 |  | Arc Fault to Upstream | Tripped |  | BMC1321FDR01 |  |  | BR4-2150-E-00037 | A
|  | PR2 |  |  |  |  | G | PODP3 | X2G 14/16/21/17/18 |  | DIO |  | 3 |  |  |  | Spare |  |  | BMC1321FDR01 |  |  | BR4-2150-E-00037 | A
|  | PR2 |  |  |  |  | B | BI1 | X1B 1/4 | REX640 SLOT B | DI |  | 3 |  | CB01A |  | Circuit Breaker | Closed |  | BMC1321FDR01 |  |  | BR4-2150-E-00037 | A
|  | PR2 |  |  |  |  | B | BI2 | X1B 2/4 |  | DI |  | 3 |  | CB01B |  | Circuit Breaker | Open |  | BMC1321FDR01 |  |  | BR4-2150-E-00037 | A
|  | PR2 |  |  |  |  | B | BI3 | X1B 3/4 |  | DI |  | 3 |  | XS04 |  | Circuit Breaker Spring | Charged |  | BMC1321FDR01 |  |  | BR4-2150-E-00037 | A
|  | PR2 |  |  |  |  | B | BI4 | X1B 5/8 |  | DI |  | 3 |  | XS01A |  | Disconnector | Closed |  | BMC1321FDR01 |  |  | BR4-2150-E-00037 | A
|  | PR2 |  |  |  |  | B | BI5 | X1B 6/8 |  | DI |  | 3 |  | XS01B |  | Disconnector | Open |  | BMC1321FDR01 |  |  | BR4-2150-E-00037 | A
|  | PR2 |  |  |  |  | B | BI6 | X1B 7/8 |  | DI |  | 3 |  | XS02A |  | Earth Switch | Closed |  | BMC1321FDR01 |  |  | BR4-2150-E-00037 | A
|  | PR2 |  |  |  |  | B | BI7 | X1B 9/12 |  | DI |  | 3 |  | XS02B |  | Earth Switch | Open |  | BMC1321FDR01 |  |  | BR4-2150-E-00037 | A
|  | PR2 |  |  |  |  | B | BI8 | X1B 10/12 |  | DI |  | 3 |  | XS03A |  | Gas Pressure | Healthy |  | BMC1321FDR01 |  |  | BR4-2150-E-00037 | A
|  | PR2 |  |  |  |  | B | BI9 | X1B 11/12 |  | DI |  | 3 |  | XS03B |  | Gas Pressure | High |  | BMC1321FDR01 |  |  | BR4-2150-E-00037 | A
|  | PR2 |  |  |  |  | B | BI10 | X1B 13/16 |  | DI |  | 3 |  | XS03C |  | Gas Pressure | Low |  | BMC1321FDR01 |  |  | BR4-2150-E-00037 | A
|  | PR2 |  |  |  |  | B | BI11 | X1B 14/16 |  | DI |  | 3 |  | CB02 |  | Control Supply MCBs | Healthy |  | BMC1321FDR01 |  |  | BR4-2150-E-00037 | A
|  | PR2 |  |  |  |  | B | BI12 | X1B 15/16 |  | DI |  | 3 |  | CB03 |  | Motor Control Supply MCBs | Healthy |  | BMC1321FDR01 |  |  | BR4-2150-E-00037 | A
|  | PR2 |  |  |  |  | B | BI13 | X1B 17/18 |  | DI |  | 3 |  |  |  | Spare |  |  | BMC1321FDR01 |  |  | BR4-2150-E-00037 | A
|  | PR2 |  |  |  |  | B | BI14 | X2B 1/2 |  | DI |  | 3 |  |  |  | Spare |  |  | BMC1321FDR01 |  |  | BR4-2150-E-00037 | A
|  | PR2 |  |  |  |  | B | SO1 | X2B 3/4 |  | DO |  | 3 |  |  |  | Spare |  |  | BMC1321FDR01 |  |  | BR4-2150-E-00037 | A
|  | PR2 |  |  |  |  | B | SO2 | X2B 5/6 |  | DO |  | 3 |  |  |  | Spare |  |  | BMC1321FDR01 |  |  | BR4-2150-E-00037 | A
|  | PR2 |  |  |  |  | B | SO3 | X2B 7/8 |  | DO |  | 3 |  |  |  | Spare |  |  | BMC1321FDR01 |  |  | BR4-2150-E-00037 | A
|  | PR2 |  |  |  |  | B | SO4 | X2B 9/10 |  | DO |  | 3 |  |  |  | Spare |  |  | BMC1321FDR01 |  |  | BR4-2150-E-00037 | A
|  | PR2 |  |  |  |  | B | SO5 | X2B 11/12 |  | DO |  | 3 |  |  |  | Spare |  |  | BMC1321FDR01 |  |  | BR4-2150-E-00037 | A
|  | PR2 |  |  |  |  | B | SO6 | X2B 13/14 |  | DO |  | 3 |  |  |  | Spare |  |  | BMC1321FDR01 |  |  | BR4-2150-E-00037 | A
|  | PR2 |  |  |  |  | B | SO7 | X2B 15/16 |  | DO |  | 3 |  |  |  | Spare |  |  | BMC1321FDR01 |  |  | BR4-2150-E-00037 | A
|  | PR2 |  |  |  |  | B | SO8 | X2B 17/18 |  | DO |  | 3 |  |  |  | Spare |  |  | BMC1321FDR01 |  |  | BR4-2150-E-00037 | A
|  | PR2 |  |  |  |  | C | BI1 | X1C 1/4 | REX640 SLOT C | DI |  | 3 |  | XS06 |  | Cable Side No Power |  |  | BMC1321FDR01 |  |  | BR4-2150-E-00037 | A
|  | PR2 |  |  |  |  | C | BI2 | X1C 2/4 |  | DI |  | 3 |  | SW01A |  | Local Mode | Selected |  | BMC1321FDR01 |  |  | BR4-2150-E-00037 | A
|  | PR2 |  |  |  |  | C | BI3 | X1C 3/4 |  | DI |  | 3 |  | SW01B |  | Remote Mode | Selected |  | BMC1321FDR01 |  |  | BR4-2150-E-00037 | A
|  | PR2 |  |  |  |  | C | BI4 | X1C 5/8 |  | DI |  | 3 |  | SW02 |  | Circuit Breaker Spring Charge Control Supply Switch | Closed |  | BMC1321FDR01 |  |  | BR4-2150-E-00037 | A
|  | PR2 |  |  |  |  | C | BI5 | X1C 6/8 |  | DI |  | 3 |  | SW03 |  | TPS Control Supply Switch | Closed |  | BMC1321FDR01 |  |  | BR4-2150-E-00037 | A
|  | PR2 |  |  |  |  | C | BI6 | X1C 7/8 |  | DI |  | 3 |  | CB04 |  | Voltage Transformer MCB | Closed |  | BMC1321FDR01 |  |  | BR4-2150-E-00037 | A
|  | PR2 |  |  |  |  | C | BI7 | X1C 9/12 |  | DI |  | 3 |  |  |  | Spare |  |  | BMC1321FDR01 |  |  | BR4-2150-E-00037 | A
|  | PR2 |  |  |  |  | C | BI8 | X1C 10/12 |  | DI |  | 3 |  | XS07 |  | Arc Fault | Healthy |  | BMC1321FDR01 |  |  | BR4-2150-E-00037 | A
|  | PR2 |  |  |  |  | C | BI9 | X1C 11/12 |  | DI |  | 4 |  | XS08 |  | Ready to Precharge from VSD | Healthy |  | BMC1321FDR01 |  |  | BR4-2150-E-00037 | A
|  | PR2 |  |  |  |  | C | BI10 | X1C 13/16 |  | DI |  | 3 |  | TRP03 |  | VSD Arc Flash Trip | Activated |  | BMC1321FDR01 |  |  | BR4-2150-E-00037 | A
|  | PR2 |  |  |  |  | C | BI11 | X1C 14/16 |  | DI |  | 3 |  | TRP04 |  | Inter Trip Signal form VSD | Activated |  | BMC1321FDR01 |  |  | BR4-2150-E-00037 | A
|  | PR2 |  |  |  |  | C | BI12 | X1C 15/16 |  | DI |  | 6 |  | XS12 |  | VSD Healthy | Activated |  | BMC1321FDR01 |  |  | BR4-2150-E-00037 | A
|  | PR2 |  |  |  |  | C | BI13 | X1C 17/18 |  | DI |  | 4 |  | XS09 |  | Close Breaker (Permissive K3) | Activated |  | BMC1321FDR01 |  |  | BR4-2150-E-00037 | A
|  | PR2 |  |  |  |  | C | BI14 | X2C 1/2 |  | DI |  | 4 | [6 empty] | BMC1321FDR01 |  |  | BR4-2150-E-00037 | A
|  | PR2 |  |  |  |  | C | SO1 | X2C 3/4 |  | DO |  | 3 |  | XS11 |  | Circuit Breaker Closing (Blocking Command) | Release |  | BMC1321FDR01 |  |  | BR4-2150-E-00037 | A
|  | PR2 |  |  |  |  | C | SO2 | XCC 5/6 |  | DO |  | 3 |  | XS05A |  | Earth Switch (Command) | Close |  | BMC1321FDR01 |  |  | BR4-2150-E-00037 | A
|  | PR2 |  |  |  |  | C | SO3 | XCC 7/8 |  | DO |  | 3 |  | XS05B |  | Earth Switch (Command) | Open |  | BMC1321FDR01 |  |  | BR4-2150-E-00037 | A
|  | PR2 |  |  |  |  | C | SO4 | XCC 9/10 |  | DO |  | 6 |  | XS13 |  | Feeder Ready to Close (to VSD) | Healthy |  | BMC1321FDR01 |  |  | BR4-2150-E-00037 | A
|  | PR2 |  |  |  |  | C | SO5 | XCC 11/12 |  | DO |  | 6 |  | XS14 |  | VSD Precharge Start | Activated |  | BMC1321FDR01 |  |  | BR4-2150-E-00037 | A
|  | PR2 |  |  |  |  | C | SO6 | XCC 13/14 |  | DO |  | 3 |  |  |  | Spare |  |  | BMC1321FDR01 |  |  | BR4-2150-E-00037 | A
|  | PR2 |  |  |  |  | C | SO7 | XCC 15/16 |  | DO |  | 3 |  |  |  | Spare |  |  | BMC1321FDR01 |  |  | BR4-2150-E-00037 | A
|  | PR2 |  |  |  |  | C | SO8 | XCC 17/18 |  | DO |  | 3 |  |  |  | Spare |  |  | BMC1321FDR01 |  |  | BR4-2150-E-00037 | A
|  | PR3 |  |  |  |  | G | RF | X1G 3/4/5 | REX640 SLOT G | DO |  | 3 |  | XS10 |  | Relay Internal | Fault |  | BMC1321FDR02 |  |  | BR4-2150-E-00040 | A | BCV131BVS01
|  | PR3 |  |  |  |  | G | SO1 | X1G 6/7/8 | NEP01ES04 | DO |  | 3 |  | XS08A |  | Disconnector Switch (Command) | Close |  | BMC1321FDR02 |  |  | BR4-2150-E-00040 | A
|  | PR3 |  |  |  |  | G | SO2 | X1G 9/10 |  | DO |  | 3 |  | XS08B |  | Disconnector Switch (Command) | Open |  | BMC1321FDR02 |  |  | BR4-2150-E-00040 | A
|  | PR3 |  |  |  |  | G | SSO1 | X1G 11/12 |  | DO |  | 3 |  |  |  | Spare |  |  | BMC1321FDR02 |  |  | BR4-2150-E-00040 | A
|  | PR3 |  |  |  |  | G | SSO2 | X1G 13/14 |  | DO |  | 3 |  |  |  | Spare |  |  | BMC1321FDR02 |  |  | BR4-2150-E-00040 | A
|  | PR3 |  |  |  |  | G | POSP1 | X1G 15/16 |  | DO |  | 3 |  | XS09A |  | Circuit Breaker (Command) | Close |  | BMC1321FDR02 |  |  | BR4-2150-E-00040 | A
|  | PR3 |  |  |  |  | G | POSP2 | X1G 17/18 |  | DO |  | 3 |  | XS09B |  | Circuit Breaker (Command) | Open |  | BMC1321FDR02 |  |  | BR4-2150-E-00040 | A
|  | PR3 |  |  |  |  | G | SO3 | X2G 1/2/3 |  | DO |  | 3 |  |  |  | Spare | Healthy |  | BMC1321FDR02 |  |  | BR4-2150-E-00040 | A
|  | PR3 |  |  |  |  | G | PODP1 | X2G 4/6/21/7/8 |  | DI |  | 3 |  | TRP01 |  | Protection Trip and Trip Circuit Supervision | Tripped |  | BMC1321FDR02 |  |  | BR4-2150-E-00040 | A
|  | PR3 |  |  |  |  | G | PODP2 | X2G 9/10/11/12/13 |  | DI |  | 3 |  | TRP02 |  | Arc Fault to Upstream | Tripped |  | BMC1321FDR02 |  |  | BR4-2150-E-00040 | A
|  | PR3 |  |  |  |  | G | PODP3 | X2G 14/16/21/17/18 |  | DIO |  | 3 |  |  |  | Spare |  |  | BMC1321FDR02 |  |  | BR4-2150-E-00040 | A
|  | PR3 |  |  |  |  | B | BI1 | X1B 1/4 | REX640 SLOT B | DI |  | 3 |  | CB01A |  | Circuit Breaker | Closed |  | BMC1321FDR02 |  |  | BR4-2150-E-00040 | A
|  | PR3 |  |  |  |  | B | BI2 | X1B 2/4 |  | DI |  | 3 |  | CB01B |  | Circuit Breaker | Open |  | BMC1321FDR02 |  |  | BR4-2150-E-00040 | A
|  | PR3 |  |  |  |  | B | BI3 | X1B 3/4 |  | DI |  | 3 |  | XS04 |  | Circuit Breaker Spring | Charged |  | BMC1321FDR02 |  |  | BR4-2150-E-00040 | A
|  | PR3 |  |  |  |  | B | BI4 | X1B 5/8 |  | DI |  | 3 |  | XS01A |  | Disconnector | Closed |  | BMC1321FDR02 |  |  | BR4-2150-E-00040 | A
|  | PR3 |  |  |  |  | B | BI5 | X1B 6/8 |  | DI |  | 3 |  | XS01B |  | Disconnector | Open |  | BMC1321FDR02 |  |  | BR4-2150-E-00040 | A
|  | PR3 |  |  |  |  | B | BI6 | X1B 7/8 |  | DI |  | 3 |  | XS02A |  | Earth Switch | Closed |  | BMC1321FDR02 |  |  | BR4-2150-E-00040 | A
|  | PR3 |  |  |  |  | B | BI7 | X1B 9/12 |  | DI |  | 3 |  | XS02B |  | Earth Switch | Open |  | BMC1321FDR02 |  |  | BR4-2150-E-00040 | A
|  | PR3 |  |  |  |  | B | BI8 | X1B 10/12 |  | DI |  | 3 |  | XS03A |  | Gas Pressure | Healthy |  | BMC1321FDR02 |  |  | BR4-2150-E-00040 | A
|  | PR3 |  |  |  |  | B | BI9 | X1B 11/12 |  | DI |  | 3 |  | XS03B |  | Gas Pressure | High |  | BMC1321FDR02 |  |  | BR4-2150-E-00040 | A
|  | PR3 |  |  |  |  | B | BI10 | X1B 13/16 |  | DI |  | 3 |  | XS03C |  | Gas Pressure | Low |  | BMC1321FDR02 |  |  | BR4-2150-E-00040 | A
|  | PR3 |  |  |  |  | B | BI11 | X1B 14/16 |  | DI |  | 3 |  | CB02 |  | Control Supply MCBs | Healthy |  | BMC1321FDR02 |  |  | BR4-2150-E-00040 | A
|  | PR3 |  |  |  |  | B | BI12 | X1B 15/16 |  | DI |  | 3 |  | CB03 |  | Motor Control Supply MCBs | Healthy |  | BMC1321FDR02 |  |  | BR4-2150-E-00040 | A
|  | PR3 |  |  |  |  | B | BI13 | X1B 17/18 |  | DI |  | 3 |  |  |  | Spare |  |  | BMC1321FDR02 |  |  | BR4-2150-E-00040 | A
|  | PR3 |  |  |  |  | B | BI14 | X2B 1/2 |  | DI |  | 3 |  |  |  | Spare |  |  | BMC1321FDR02 |  |  | BR4-2150-E-00040 | A
|  | PR3 |  |  |  |  | B | SO1 | X2B 3/4 |  | DO |  | 3 |  |  |  | Spare |  |  | BMC1321FDR02 |  |  | BR4-2150-E-00040 | A
|  | PR3 |  |  |  |  | B | SO2 | X2B 5/6 |  | DO |  | 3 |  |  |  | Spare |  |  | BMC1321FDR02 |  |  | BR4-2150-E-00040 | A
|  | PR3 |  |  |  |  | B | SO3 | X2B 7/8 |  | DO |  | 3 |  |  |  | Spare |  |  | BMC1321FDR02 |  |  | BR4-2150-E-00040 | A
|  | PR3 |  |  |  |  | B | SO4 | X2B 9/10 |  | DO |  | 3 |  |  |  | Spare |  |  | BMC1321FDR02 |  |  | BR4-2150-E-00040 | A
|  | PR3 |  |  |  |  | B | SO5 | X2B 11/12 |  | DO |  | 3 |  |  |  | Spare |  |  | BMC1321FDR02 |  |  | BR4-2150-E-00040 | A
|  | PR3 |  |  |  |  | B | SO6 | X2B 13/14 |  | DO |  | 3 |  |  |  | Spare |  |  | BMC1321FDR02 |  |  | BR4-2150-E-00040 | A
|  | PR3 |  |  |  |  | B | SO7 | X2B 15/16 |  | DO |  | 3 |  |  |  | Spare |  |  | BMC1321FDR02 |  |  | BR4-2150-E-00040 | A
|  | PR3 |  |  |  |  | B | SO8 | X2B 17/18 |  | DO |  | 3 |  |  |  | Spare |  |  | BMC1321FDR02 |  |  | BR4-2150-E-00040 | A
|  | PR3 |  |  |  |  | C | BI1 | X1C 1/4 | REX640 SLOT C | DI |  | 3 |  | XS06 |  | Cable Side No Power |  |  | BMC1321FDR02 |  |  | BR4-2150-E-00040 | A
|  | PR3 |  |  |  |  | C | BI2 | X1C 2/4 |  | DI |  | 3 |  | SW01A |  | Local Mode | Selected |  | BMC1321FDR02 |  |  | BR4-2150-E-00040 | A
|  | PR3 |  |  |  |  | C | BI3 | X1C 3/4 |  | DI |  | 3 |  | SW01B |  | Remote Mode | Selected |  | BMC1321FDR02 |  |  | BR4-2150-E-00040 | A
|  | PR3 |  |  |  |  | C | BI4 | X1C 5/8 |  | DI |  | 3 |  | SW02 |  | Circuit Breaker Spring Charge Control Supply Switch | Closed |  | BMC1321FDR02 |  |  | BR4-2150-E-00040 | A
|  | PR3 |  |  |  |  | C | BI5 | X1C 6/8 |  | DI |  | 3 |  | SW03 |  | TPS Control Supply Switch | Closed |  | BMC1321FDR02 |  |  | BR4-2150-E-00040 | A
|  | PR3 |  |  |  |  | C | BI6 | X1C 7/8 |  | DI |  | 3 |  | CB04 |  | Voltage Transformer MCB | Closed |  | BMC1321FDR02 |  |  | BR4-2150-E-00040 | A
|  | PR3 |  |  |  |  | C | BI7 | X1C 9/12 |  | DI |  | 3 |  |  |  | Spare |  |  | BMC1321FDR02 |  |  | BR4-2150-E-00040 | A
|  | PR3 |  |  |  |  | C | BI8 | X1C 10/12 |  | DI |  | 3 |  | XS07 |  | Arc Fault | Healthy |  | BMC1321FDR02 |  |  | BR4-2150-E-00040 | A
|  | PR3 |  |  |  |  | C | BI9 | X1C 11/12 |  | DI |  | 6 |  | XS08 |  | Ready to Precharge from VSD | Healthy |  | BMC1321FDR02 |  |  | BR4-2150-E-00040 | A
|  | PR3 |  |  |  |  | C | BI10 | X1C 13/16 |  | DI |  | 3 |  | TRP03 |  | Inter Trip from Upstream | Activated |  | BMC1321FDR02 |  |  | BR4-2150-E-00040 | A
|  | PR3 |  |  |  |  | C | BI11 | X1C 14/16 |  | DI |  | 3 |  | TRP04 |  | Inter Trip Signal form Shutdown Button | Activated |  | BMC1321FDR02 |  |  | BR4-2150-E-00040 | A
|  | PR3 |  |  |  |  | C | BI12 | X1C 15/16 |  | DI |  | 6 |  | XS12 |  | VSD Healthy | Activated |  | BMC1321FDR02 |  |  | BR4-2150-E-00040 | A
|  | PR3 |  |  |  |  | C | BI13 | X1C 17/18 |  | DI |  | 6 |  | XS09 |  | Close Breaker (Permissive K3) | Activated |  | BMC1321FDR02 |  |  | BR4-2150-E-00040 | A
|  | PR3 |  |  |  |  | C | BI14 | X2C 1/2 |  | DI |  | 6 | [6 empty] | BMC1321FDR02 |  |  | BR4-2150-E-00040 | A
|  | PR3 |  |  |  |  | C | SO1 | X2C 3/4 |  | DO |  | 3 |  | XS11 |  | Circuit Breaker Closing (Blocking Command) | Release |  | BMC1321FDR02 |  |  | BR4-2150-E-00040 | A
|  | PR3 |  |  |  |  | C | SO2 | XCC 5/6 |  | DO |  | 3 |  | XS05A |  | Earth Switch (Command) | Close |  | BMC1321FDR02 |  |  | BR4-2150-E-00040 | A
|  | PR3 |  |  |  |  | C | SO3 | XCC 7/8 |  | DO |  | 3 |  | XS05B |  | Earth Switch (Command) | Open |  | BMC1321FDR02 |  |  | BR4-2150-E-00040 | A
|  | PR3 |  |  |  |  | C | SO4 | XCC 9/10 |  | DO |  | 6 |  | XS13 |  | Feeder Ready to Close (to VSD) | Healthy |  | BMC1321FDR02 |  |  | BR4-2150-E-00040 | A
|  | PR3 |  |  |  |  | C | SO5 | XCC 11/12 |  | DO |  | 6 |  | XS14 |  | VSD Precharge Start | Activated |  | BMC1321FDR02 |  |  | BR4-2150-E-00040 | A
|  | PR3 |  |  |  |  | C | SO6 | XCC 13/14 |  | DO |  | 3 |  |  |  | Spare |  |  | BMC1321FDR02 |  |  | BR4-2150-E-00040 | A
|  | PR3 |  |  |  |  | C | SO7 | XCC 15/16 |  | DO |  | 3 |  |  |  | Spare |  |  | BMC1321FDR02 |  |  | BR4-2150-E-00040 | A
|  | PR3 |  |  |  |  | C | SO8 | XCC 17/18 |  | DO |  | 3 |  |  |  | Spare |  |  | BMC1321FDR02 |  |  | BR4-2150-E-00040 | A
|  | PR4 |  |  |  |  | G | RF | X1G 3/4/5 | REX640 SLOT G | DO |  | 3 |  | XS10 |  | Relay Internal | Fault |  | BMC1321FDR03 |  |  | BR4-2150-E-00043 | A | BCV131BVS01
|  | PR4 |  |  |  |  | G | SO1 | X1G 6/7/8 | NEP01ES04 | DO |  | 3 |  | XS08A |  | Disconnector Switch (Command) | Close |  | BMC1321FDR03 |  |  | BR4-2150-E-00043 | A
|  | PR4 |  |  |  |  | G | SO2 | X1G 9/10 |  | DO |  | 3 |  | XS08B |  | Disconnector Switch (Command) | Open |  | BMC1321FDR03 |  |  | BR4-2150-E-00043 | A
|  | PR4 |  |  |  |  | G | SSO1 | X1G 11/12 |  | DO |  | 3 |  |  |  | Spare |  |  | BMC1321FDR03 |  |  | BR4-2150-E-00043 | A
|  | PR4 |  |  |  |  | G | SSO2 | X1G 13/14 |  | DO |  | 3 |  |  |  | Spare |  |  | BMC1321FDR03 |  |  | BR4-2150-E-00043 | A
|  | PR4 |  |  |  |  | G | POSP1 | X1G 15/16 |  | DO |  | 3 |  | XS09A |  | Circuit Breaker (Command) | Close |  | BMC1321FDR03 |  |  | BR4-2150-E-00043 | A
|  | PR4 |  |  |  |  | G | POSP2 | X1G 17/18 |  | DO |  | 3 |  | XS09B |  | Circuit Breaker (Command) | Open |  | BMC1321FDR03 |  |  | BR4-2150-E-00043 | A
|  | PR4 |  |  |  |  | G | SO3 | X2G 1/2/3 |  | DO |  | 3 |  |  |  | Spare | Healthy |  | BMC1321FDR03 |  |  | BR4-2150-E-00043 | A
|  | PR4 |  |  |  |  | G | PODP1 | X2G 4/6/21/7/8 |  | DI |  | 3 |  | TRP01 |  | Protection Trip and Trip Circuit Supervision | Tripped |  | BMC1321FDR03 |  |  | BR4-2150-E-00043 | A
|  | PR4 |  |  |  |  | G | PODP2 | X2G 9/10/11/12/13 |  | DI |  | 3 |  | TRP02 |  | Arc Fault to Upstream | Tripped |  | BMC1321FDR03 |  |  | BR4-2150-E-00043 | A
|  | PR4 |  |  |  |  | G | PODP3 | X2G 14/16/21/17/18 |  | DIO |  | 3 |  |  |  | Spare |  |  | BMC1321FDR03 |  |  | BR4-2150-E-00043 | A
|  | PR4 |  |  |  |  | B | BI1 | X1B 1/4 | REX640 SLOT B | DI |  | 3 |  | CB01A |  | Circuit Breaker | Closed |  | BMC1321FDR03 |  |  | BR4-2150-E-00043 | A
|  | PR4 |  |  |  |  | B | BI2 | X1B 2/4 |  | DI |  | 3 |  | CB01B |  | Circuit Breaker | Open |  | BMC1321FDR03 |  |  | BR4-2150-E-00043 | A
|  | PR4 |  |  |  |  | B | BI3 | X1B 3/4 |  | DI |  | 3 |  | XS04 |  | Circuit Breaker Spring | Charged |  | BMC1321FDR03 |  |  | BR4-2150-E-00043 | A
|  | PR4 |  |  |  |  | B | BI4 | X1B 5/8 |  | DI |  | 3 |  | XS01A |  | Disconnector | Closed |  | BMC1321FDR03 |  |  | BR4-2150-E-00043 | A
|  | PR4 |  |  |  |  | B | BI5 | X1B 6/8 |  | DI |  | 3 |  | XS01B |  | Disconnector | Open |  | BMC1321FDR03 |  |  | BR4-2150-E-00043 | A
|  | PR4 |  |  |  |  | B | BI6 | X1B 7/8 |  | DI |  | 3 |  | XS02A |  | Earth Switch | Closed |  | BMC1321FDR03 |  |  | BR4-2150-E-00043 | A
|  | PR4 |  |  |  |  | B | BI7 | X1B 9/12 |  | DI |  | 3 |  | XS02B |  | Earth Switch | Open |  | BMC1321FDR03 |  |  | BR4-2150-E-00043 | A
|  | PR4 |  |  |  |  | B | BI8 | X1B 10/12 |  | DI |  | 3 |  | XS03A |  | Gas Pressure | Healthy |  | BMC1321FDR03 |  |  | BR4-2150-E-00043 | A
|  | PR4 |  |  |  |  | B | BI9 | X1B 11/12 |  | DI |  | 3 |  | XS03B |  | Gas Pressure | High |  | BMC1321FDR03 |  |  | BR4-2150-E-00043 | A
|  | PR4 |  |  |  |  | B | BI10 | X1B 13/16 |  | DI |  | 3 |  | XS03C |  | Gas Pressure | Low |  | BMC1321FDR03 |  |  | BR4-2150-E-00043 | A
|  | PR4 |  |  |  |  | B | BI11 | X1B 14/16 |  | DI |  | 3 |  | CB02 |  | Control Supply MCBs | Healthy |  | BMC1321FDR03 |  |  | BR4-2150-E-00043 | A
|  | PR4 |  |  |  |  | B | BI12 | X1B 15/16 |  | DI |  | 3 |  | CB03 |  | Motor Control Supply MCBs | Healthy |  | BMC1321FDR03 |  |  | BR4-2150-E-00043 | A
|  | PR4 |  |  |  |  | B | BI13 | X1B 17/18 |  | DI |  | 3 |  |  |  | Spare |  |  | BMC1321FDR03 |  |  | BR4-2150-E-00043 | A
|  | PR4 |  |  |  |  | B | BI14 | X2B 1/2 |  | DI |  | 3 |  |  |  | Spare |  |  | BMC1321FDR03 |  |  | BR4-2150-E-00043 | A
|  | PR4 |  |  |  |  | B | SO1 | X2B 3/4 |  | DO |  | 3 |  |  |  | Spare |  |  | BMC1321FDR03 |  |  | BR4-2150-E-00043 | A
|  | PR4 |  |  |  |  | B | SO2 | X2B 5/6 |  | DO |  | 3 |  |  |  | Spare |  |  | BMC1321FDR03 |  |  | BR4-2150-E-00043 | A
|  | PR4 |  |  |  |  | B | SO3 | X2B 7/8 |  | DO |  | 3 |  |  |  | Spare |  |  | BMC1321FDR03 |  |  | BR4-2150-E-00043 | A
|  | PR4 |  |  |  |  | B | SO4 | X2B 9/10 |  | DO |  | 3 |  |  |  | Spare |  |  | BMC1321FDR03 |  |  | BR4-2150-E-00043 | A
|  | PR4 |  |  |  |  | B | SO5 | X2B 11/12 |  | DO |  | 3 |  |  |  | Spare |  |  | BMC1321FDR03 |  |  | BR4-2150-E-00043 | A
|  | PR4 |  |  |  |  | B | SO6 | X2B 13/14 |  | DO |  | 3 |  |  |  | Spare |  |  | BMC1321FDR03 |  |  | BR4-2150-E-00043 | A
|  | PR4 |  |  |  |  | B | SO7 | X2B 15/16 |  | DO |  | 3 |  |  |  | Spare |  |  | BMC1321FDR03 |  |  | BR4-2150-E-00043 | A
|  | PR4 |  |  |  |  | B | SO8 | X2B 17/18 |  | DO |  | 3 |  |  |  | Spare |  |  | BMC1321FDR03 |  |  | BR4-2150-E-00043 | A
|  | PR4 |  |  |  |  | C | BI1 | X1C 1/4 | REX640 SLOT C | DI |  | 3 |  | XS06 |  | Cable Side No Power |  |  | BMC1321FDR03 |  |  | BR4-2150-E-00043 | A
|  | PR4 |  |  |  |  | C | BI2 | X1C 2/4 |  | DI |  | 3 |  | SW01A |  | Local Mode | Selected |  | BMC1321FDR03 |  |  | BR4-2150-E-00043 | A
|  | PR4 |  |  |  |  | C | BI3 | X1C 3/4 |  | DI |  | 3 |  | SW01B |  | Remote Mode | Selected |  | BMC1321FDR03 |  |  | BR4-2150-E-00043 | A
|  | PR4 |  |  |  |  | C | BI4 | X1C 5/8 |  | DI |  | 3 |  | SW02 |  | Circuit Breaker Spring Charge Control Supply Switch | Closed |  | BMC1321FDR03 |  |  | BR4-2150-E-00043 | A
|  | PR4 |  |  |  |  | C | BI5 | X1C 6/8 |  | DI |  | 3 |  | SW03 |  | TPS Control Supply Switch | Closed |  | BMC1321FDR03 |  |  | BR4-2150-E-00043 | A
|  | PR4 |  |  |  |  | C | BI6 | X1C 7/8 |  | DI |  | 3 |  | CB04 |  | Voltage Transformer MCB | Closed |  | BMC1321FDR03 |  |  | BR4-2150-E-00043 | A
|  | PR4 |  |  |  |  | C | BI7 | X1C 9/12 |  | DI |  | 3 |  |  |  | Spare |  |  | BMC1321FDR03 |  |  | BR4-2150-E-00043 | A
|  | PR4 |  |  |  |  | C | BI8 | X1C 10/12 |  | DI |  | 3 |  | XS07 |  | Arc Fault | Healthy |  | BMC1321FDR03 |  |  | BR4-2150-E-00043 | A
|  | PR4 |  |  |  |  | C | BI9 | X1C 11/12 |  | DI |  | 6 |  | XS08 |  | Ready to Precharge from VSD | Healthy |  | BMC1321FDR03 |  |  | BR4-2150-E-00043 | A
|  | PR4 |  |  |  |  | C | BI10 | X1C 13/16 |  | DI |  | 3 |  | TRP03 |  | Inter Trip from Upstream | Activated |  | BMC1321FDR03 |  |  | BR4-2150-E-00043 | A
|  | PR4 |  |  |  |  | C | BI11 | X1C 14/16 |  | DI |  | 3 |  | TRP04 |  | Inter Trip Signal form Shutdown Button | Activated |  | BMC1321FDR03 |  |  | BR4-2150-E-00043 | A
|  | PR4 |  |  |  |  | C | BI12 | X1C 15/16 |  | DI |  | 6 |  | XS12 |  | VSD Healthy | Activated |  | BMC1321FDR03 |  |  | BR4-2150-E-00043 | A
|  | PR4 |  |  |  |  | C | BI13 | X1C 17/18 |  | DI |  | 6 |  | XS09 |  | Close Breaker (Permissive K3) | Activated |  | BMC1321FDR03 |  |  | BR4-2150-E-00043 | A
|  | PR4 |  |  |  |  | C | BI14 | X2C 1/2 |  | DI |  | 6 | [6 empty] | BMC1321FDR03 |  |  | BR4-2150-E-00043 | A
|  | PR4 |  |  |  |  | C | SO1 | X2C 3/4 |  | DO |  | 3 |  | XS11 |  | Circuit Breaker Closing (Blocking Command) | Release |  | BMC1321FDR03 |  |  | BR4-2150-E-00043 | A
|  | PR4 |  |  |  |  | C | SO2 | XCC 5/6 |  | DO |  | 3 |  | XS05A |  | Earth Switch (Command) | Close |  | BMC1321FDR03 |  |  | BR4-2150-E-00043 | A
|  | PR4 |  |  |  |  | C | SO3 | XCC 7/8 |  | DO |  | 3 |  | XS05B |  | Earth Switch (Command) | Open |  | BMC1321FDR03 |  |  | BR4-2150-E-00043 | A
|  | PR4 |  |  |  |  | C | SO4 | XCC 9/10 |  | DO |  | 6 |  | XS13 |  | Feeder Ready to Close (to VSD) | Healthy |  | BMC1321FDR03 |  |  | BR4-2150-E-00043 | A
|  | PR4 |  |  |  |  | C | SO5 | XCC 11/12 |  | DO |  | 6 |  | XS14 |  | VSD Precharge Start | Activated |  | BMC1321FDR03 |  |  | BR4-2150-E-00043 | A
|  | PR4 |  |  |  |  | C | SO6 | XCC 13/14 |  | DO |  | 3 |  |  |  | Spare |  |  | BMC1321FDR03 |  |  | BR4-2150-E-00043 | A
|  | PR4 |  |  |  |  | C | SO7 | XCC 15/16 |  | DO |  | 3 |  |  |  | Spare |  |  | BMC1321FDR03 |  |  | BR4-2150-E-00043 | A
|  | PR4 |  |  |  |  | C | SO8 | XCC 17/18 |  | DO |  | 3 |  |  |  | Spare |  |  | BMC1321FDR03 |  |  | BR4-2150-E-00043 | A
BCV131SLC01 Flexisoft - Odd AXs
DX01ES01
|  |  |  | 1 | 0 | 0 | 0 | CPU SLC1 |  | 1059305 | Type 1 |  |  |  | FlexiSoft Bus | [6 empty] | 1.0\0.0:CPU SLC1 | BR4-2150-E-00202 | 0
|  |  |  | 1 | 0 | 0 | 13 | COMMS |  | 1044073 | [11 empty] | 1.0\0.13:COMMS | BR4-2150-E-00202 | 0
BSR132 | DX01 | SIO1 | SLC01 | 1 | 0 | 0 | 1 | 1 | I1 | IgnoreMUG | SDI |  | 3 |  | XE01 |  | Emergency Stop Reset Request (programmed not wired) | enabled |  | BCV131 |  | 1.0\0.1:1 | BR4-2150-E-00202 | 0
BSR132 | DX01 |  |  | 1 | 0 | 0 | 1 | 2 | I2 |  | SDI |  | 3 |  | YA01 |  | Start-up Warning Request (programmed not wired) | enabled |  | BCV131 |  | 1.0\0.1:2 | BR4-2150-E-00202 | 0
BSR132 | DX01 |  |  | 1 | 0 | 0 | 1 | 3 | I3 | 1044125 | SDI |  | 3 | BCV131WN01LOS01 | LOS01A |  | Lock Off Stop 1 ChA | Healthy |  | BCV131WN01 |  | 1.0\0.1:3 | BR4-2150-E-00202 | 0
BSR132 | DX01 |  |  | 1 | 0 | 0 | 1 | 4 | I4 | 1047162 | SDI |  | 3 | BCV131WN01LOS01 | LOS01B |  | Lock Off Stop 1 ChB | Healthy |  | BCV131WN01 |  | 1.0\0.1:4 | BR4-2150-E-00202 | 0
BSR132 | DX01 |  |  | 1 | 0 | 0 | 1 | 5 | I5 < Y2 | SN# | SDI |  | 3 |  | CAX01 |  | 4RO module 6 Y1 / Y2 feedback | Closed |  | BCV131 |  | 1.0\0.1:5 | BR4-2150-E-00202 | 0
BSR132 | DX01 |  |  | 1 | 0 | 0 | 1 | 6 | I6 < Y4 |  | SDI |  | 3 |  | CAX02 |  | 4RO module 6 Y3 / Y4 feedback | Closed |  | BCV131 |  | 1.0\0.1:6 | BR4-2150-E-00202 | 0
BSR132 | DX01 |  |  | 1 | 0 | 0 | 1 | 7 | I7 |  | SDI |  | 3 | [6 empty] | BCV131 |  | 1.0\0.1:7 | BR4-2150-E-00202 | 0
BSR132 | DX01 |  |  | 1 | 0 | 0 | 1 | 8 | I8 |  | SDI |  | 3 | [6 empty] | BCV131 |  | 1.0\0.1:8 | BR4-2150-E-00202 | 0
BSR132 | DX01 |  |  | 1 | 0 | 0 | 1 | 1 | Q1 > B1 |  | SDO |  | 3 |  | SIL01 |  | Safety Interlock B1 - immediate | Healthy (Solid State Output) |  | BCV131 |  | 1.0\0.1:1 | BR4-2150-E-00202 | 0
BSR132 | DX01 |  |  | 1 | 0 | 0 | 1 | 2 | Q2 > B2 |  | SDO |  | 3 |  | SIL02 |  | Safety Interlock B2 - immediate | Healthy (Solid State Output) |  | BCV131 |  | 1.0\0.1:2 | BR4-2150-E-00202 | 0
BSR132 | DX01 |  |  | 1 | 0 | 0 | 1 | 3 | Q3 > B1 |  | SDO |  | 3 | [6 empty] | BCV131 |  | 1.0\0.1:3 | BR4-2150-E-00202 | 0
BSR132 | DX01 |  |  | 1 | 0 | 0 | 1 | 4 | Q4 > B2 |  | SDO |  | 3 | [6 empty] | BCV131 |  | 1.0\0.1:4 | BR4-2150-E-00202 | 0
BSR132 | DX01 |  |  | 1 | 0 | 0 | 2 | 1A | 13 / 14 | 4RO | SRO |  | 3 |  | SIL01A |  | FLEXISOFT PWS Bus 1 Statutory immediate circuit 1 | Healthy |  | BCV131 |  | 1.0\0.2:1A | BR4-2150-E-00202 | 0 | wired to stat CCT
BSR132 | DX01 |  |  | 1 | 0 | 0 | 2 | 1B | 23 / 24 | 6026143 | SRO |  | 3 |  | SIL01B |  | FLEXISOFT PWS Bus 1 Statutory immediate circuit 1 | Healthy |  | BCV131 |  | 1.0\0.2:1B | BR4-2150-E-00202 | 0 | monitored
BSR132 | DX01 |  |  | 1 | 0 | 0 | 2 | 1C | Y14 |  | SSDO |  | 3 |  | SIL01C |  | FLEXISOFT PWS Bus 1 Statutory immediate circuit 1 | Healthy (Solid State Output) |  | BCV131 |  | 1.0\0.2:1C | BR4-2150-E-00202 | 0
BSR132 | DX01 |  |  | 1 | 0 | 0 | 2 | 1M | Y1>+ / Y2>I5 |  | SRMO |  | 3 |  | SIL01M |  | Feedback Channel 1A / 1B closed | Healthy Relay (Feedback) |  | BCV131 |  | 1.0\0.2:1M | BR4-2150-E-00202 | 0
BSR132 | DX01 |  |  | 1 | 0 | 0 | 2 | 2A | 33 / 34 |  | SRO |  | 3 |  | SIL02A |  | FLEXISOFT PWS Bus 1 Statutory immediate circuit 2 | Healthy |  | BCV131 |  | 1.0\0.2:2A | BR4-2150-E-00202 | 0 | wired to stat CCT
BSR132 | DX01 |  |  | 1 | 0 | 0 | 2 | 2B | 43 / 44 |  | SRO |  | 3 |  | SIL02B |  | FLEXISOFT PWS Bus 1 Statutory immediate circuit 2 | Healthy |  | BCV131 |  | 1.0\0.2:2B | BR4-2150-E-00202 | 0 | monitored
BSR132 | DX01 |  |  | 1 | 0 | 0 | 2 | 2C | Y24 |  | SSDO |  | 3 |  | SIL02C |  | FLEXISOFT PWS Bus 1 Statutory immediate circuit 2 | Healthy (Solid State Output) |  | BCV131 |  | 1.0\0.2:2C | BR4-2150-E-00202 | 0
BSR132 | DX01 |  |  | 1 | 0 | 0 | 2 | 2M | Y3>+ / Y4>I6 |  | SRMO |  | 3 |  | SIL02M |  | Feedback Channel 2A / 2B closed | Healthy Relay (Feedback) |  | BCV131 |  | 1.0\0.2:2M | BR4-2150-E-00202 | 0
BCV131SLC02 Flexisoft - Even AXs
|  |  |  | 2 | 0 | 0 | 0 | CPU SLC1 |  | 1059305 | Type |  |  |  | FlexiSoft Bus | [6 empty] | 2.0\0.0:CPU SLC1 | BR4-2150-E-00203 | 0
|  |  |  | 2 | 0 | 0 |  | COMMS | [13 empty] | 2.0\0.:COMMS | BR4-2150-E-00203 | 0
BSR132 | DX01 | SIO1 | SLC02 | 2 | 0 | 0 | 1 | 1 | I1 | IgnoreMUG | SDI |  | 3 |  | XE01 |  | Emergency Stop Reset Request (programmed not wired) | enabled |  | BCV131 |  | 2.0\0.1:1 | BR4-2150-E-00203 | 0
BSR132 | DX01 |  |  | 2 | 0 | 0 | 1 | 2 | I2 |  | SDI |  | 3 |  | YA01 |  | Start-up Warning Request (programmed not wired) | enabled |  | BCV131 |  | 2.0\0.1:2 | BR4-2150-E-00203 | 0
BSR132 | DX01 |  |  | 2 | 0 | 0 | 1 | 3 | I3 | 1044125 | SDI |  | 3 |  | SY01A |  | Safety Relay 1 ChA | Healthy |  | BCV131BBN131 |  | 2.0\0.1:3 | BR4-2150-E-00203 | 0
BSR132 | DX01 |  |  | 2 | 0 | 0 | 1 | 4 | I4 | 1047162 | SDI |  | 3 |  | SY01B |  | Safety Relay 1 ChB | Healthy |  | BCV131BBN131 |  | 2.0\0.1:4 | BR4-2150-E-00203 | 0
BSR132 | DX01 |  |  | 2 | 0 | 0 | 1 | 5 | I5 < Y2 | SN# | SDI |  | 3 |  | CAX01 |  | 4RO module 6 Y1 / Y2 feedback | Closed |  | BCV131 |  | 2.0\0.1:5 | BR4-2150-E-00203 | 0
BSR132 | DX01 |  |  | 2 | 0 | 0 | 1 | 6 | I6 < Y4 |  | SDI |  | 3 |  | CAX02 |  | 4RO module 6 Y3 / Y4 feedback | Closed |  | BCV131 |  | 2.0\0.1:6 | BR4-2150-E-00203 | 0
BSR132 | DX01 |  |  | 2 | 0 | 0 | 1 | 7 | I7 |  | SDI |  | 3 | [6 empty] | BCV131 |  | 2.0\0.1:7 | BR4-2150-E-00203 | 0
BSR132 | DX01 |  |  | 2 | 0 | 0 | 1 | 8 | I8 |  | SDI |  | 3 | [6 empty] | BCV131 |  | 2.0\0.1:8 | BR4-2150-E-00203 | 0
BSR132 | DX01 |  |  | 2 | 0 | 0 | 1 | 1 | Q1 > B1 |  | SDO |  | 3 |  | SIL01 |  | Safety Interlock B1 - immediate | Healthy (Solid State Output) |  | BCV131 |  | 2.0\0.1:1 | BR4-2150-E-00203 | 0
BSR132 | DX01 |  |  | 2 | 0 | 0 | 1 | 2 | Q2 > B2 |  | SDO |  | 3 |  | SIL02 |  | Safety Interlock B2 - immediate | Healthy (Solid State Output) |  | BCV131 |  | 2.0\0.1:2 | BR4-2150-E-00203 | 0
BSR132 | DX01 |  |  | 2 | 0 | 0 | 1 | 3 | Q3 > B1 |  | SDO |  | 3 | [6 empty] | BCV131 |  | 2.0\0.1:3 | BR4-2150-E-00203 | 0
BSR132 | DX01 |  |  | 2 | 0 | 0 | 1 | 4 | Q4 > B2 |  | SDO |  | 3 | [6 empty] | BCV131 |  | 2.0\0.1:4 | BR4-2150-E-00203 | 0
BSR132 | DX01 |  |  | 2 | 0 | 0 | 2 | 1A | 13 / 14 | 4RO | SRO |  | 3 |  | SIL01A |  | FLEXISOFT PWS Bus 1 Statutory immediate circuit 1 | Healthy |  | BCV131 |  | 2.0\0.2:1A | BR4-2150-E-00203 | 0 | wired to stat CCT
BSR132 | DX01 |  |  | 2 | 0 | 0 | 2 | 1B | 23 / 24 | 6026143 | SRO |  | 3 |  | SIL01B |  | FLEXISOFT PWS Bus 1 Statutory immediate circuit 1 | Healthy |  | BCV131 |  | 2.0\0.2:1B | BR4-2150-E-00203 | 0 | monitored
BSR132 | DX01 |  |  | 2 | 0 | 0 | 2 | 1C | Y14 |  | SSDO |  | 3 |  | SIL01C |  | FLEXISOFT PWS Bus 1 Statutory immediate circuit 1 | Healthy (Solid State Output) |  | BCV131 |  | 2.0\0.2:1C | BR4-2150-E-00203 | 0
BSR132 | DX01 |  |  | 2 | 0 | 0 | 2 | 1M | Y1>+ / Y2>I5 |  | SRMO |  | 3 |  | SIL01M |  | Feedback Channel 1A / 1B closed | Healthy Relay (Feedback) |  | BCV131 |  | 2.0\0.2:1M | BR4-2150-E-00203 | 0
BSR132 | DX01 |  |  | 2 | 0 | 0 | 2 | 2A | 33 / 34 |  | SRO |  | 3 |  | SIL02A |  | FLEXISOFT PWS Bus 1 Statutory immediate circuit 2 | Healthy |  | BCV131 |  | 2.0\0.2:2A | BR4-2150-E-00203 | 0 | wired to stat CCT
BSR132 | DX01 |  |  | 2 | 0 | 0 | 2 | 2B | 43 / 44 |  | SRO |  | 3 |  | SIL02B |  | FLEXISOFT PWS Bus 1 Statutory immediate circuit 2 | Healthy |  | BCV131 |  | 2.0\0.2:2B | BR4-2150-E-00203 | 0 | monitored
BSR132 | DX01 |  |  | 2 | 0 | 0 | 2 | 2C | Y24 |  | SSDO |  | 3 |  | SIL02C |  | FLEXISOFT PWS Bus 1 Statutory immediate circuit 2 | Healthy (Solid State Output) |  | BCV131 |  | 2.0\0.2:2C | BR4-2150-E-00203 | 0
BSR132 | DX01 |  |  | 2 | 0 | 0 | 2 | 2M | Y3>+ / Y4>I6 |  | SRMO |  | 3 |  | SIL02M |  | Feedback Channel 2A / 2B closed | Healthy Relay (Feedback) |  | BCV131 |  | 2.0\0.2:2M | BR4-2150-E-00203 | 0
[38 empty] | MULTICORE IN | CABLE DX TO BUCKET | STATUS
[11 empty] | PNOZs4 |  |  | BSR132DX01 | BCV131 | BCV131 | BCV131 MASTER RELAY |  | K155-1 | BSR132DX01 |  |  | BR4-2150-E-00202 | [9 empty] | F12 | 1 | 2 | 3 | 4 | INTERNAL |  | status to 2.1\0.9.11
[14 empty] | BSR132DX01 | BCV131WN01 | BCV131WN01 | BCV131 MASTER TO WN01 |  |  | BSR132DX01 |  |  | BR4-2150-E-00202 | [9 empty] | F12 | 5 | 6 | 7 | 8 | NO CABLE?
[11 empty] | PNOZs7.1 |  |  | BSR132DX01 | BCV131AVS01 | BCV131AVS01 | BCV131 MASTER TO VSD01 STO |  | K155-2 | BSR132DX01 |  |  | BR4-2150-E-00202 | [9 empty] | F12 | 9 | 10 | 11 | 12 | BCV131AVS01-C4 2 PAIR
[11 empty] | PNOZs7.2 |  |  | BSR132DX01 | BCV131BVS01 | BCV131BVS01 | BCV131 MASTER TO VSD02 STO |  | K155-3 | BSR132DX01 |  |  | BR4-2150-E-00202 | [9 empty] | F12 | 13 | 14 | 15 | 16 | BCV131BVS01-C4 2 PAIR
[11 empty] | PNOZs7.2 |  |  | BSR132DX01 | BCV131CVS01 | BCV131CVS01 | BCV131 MASTER TO VSD03 STO |  | K155-4 | BSR132DX01 |  |  | BR4-2150-E-00202 | [9 empty] | F12 | 17 | 18 | 19 | 20 | BCV131CVS01-C4 2 PAIR
[11 empty] | PNOZs4 |  |  | BSR132DX01 | BBN131LS0X | BBN131LS0X | BBN131 LS MASTER (TO FLEXISOFT) |  | K255-1 | BSR132DX01 |  |  | BR4-2150-E-00202 | [9 empty] | F12 | 21 | 22 | 23 | 24 |  |  | status to 2.1\0.9.14
[33 empty] | F12 | 25 | 26 | 27 | 28
[14 empty] | BBD131DX03 |  |  | BDU131FN01 FIELD LOS TO BBD131FN01 BUCKET |  |  | BBD131DX03 |  |  | BR4-2150-E-00202 | [9 empty] | F12 | 29 | 30 | 31 | 32 | BBD131DX03-C1 20 PAIR - ONLY 4 PAIR REQUIRED 6 PAIR USED
[15 empty] | BBN131LS0X | BBN131LS0X | BBN131 LS MASTER (FROM FIELD) | [5 empty] | BR4-2150-E-00203 | [9 empty] | F12 | 33 | 34 | 35 | 36
[33 empty] | F12 | 37 | 38 | 39 | 40 | BBD131DX04-C1 20 PAIR - ONLY 12 PAIR REQUIRED 16 PAIR USED
[33 empty] | F12 | 41 | 42 | 43 | 44
[14 empty] | BBD131DX04 |  |  | BAF131LU01 FIELD LOS TO BAF131PP02 BUCKET |  |  | BBD131DX04 |  |  | BR4-2150-E-00204 | [9 empty] | F12 | 45 | 46 | 47 | 48
[11 empty] | PNOZs4 |  |  | BBD131DX04 | BAF131 | BAF131 | BAF131 MASTER TO BAF131PP01 BUCKET |  | K355-1 | BBD131DX04 | [12 empty] | F12 | 49 | 50 | 51 | 52 |  |  | status to 2.1\0.9.2
[11 empty] | PNOZs7.1 |  |  | BBD131DX04 | BAF131 | BAF131 | BAF131 MASTER TO BAF131PP04 BUCKET |  | K355-2 | BBD131DX04 | [12 empty] | F12 | 53 | 54 | 55 | 56
[14 empty] | BBD131DX04 | BAF131 | BAF131 | BAF131 DX04 FIELD RELAYS TO BAF131 MASTER |  |  | BBD131DX04 | [12 empty] | F12 | 57 | 58 | 59 | 60
[14 empty] | BBD131DX04 | BAF131FN01 | BAF131FN01 | BAF131FN01 FIELD LOS TO BAF131FN01 BUCKET |  |  | BBD131DX04 | [12 empty] | F12 | 61 | 62 | 63 | 64
[14 empty] | BBD131DX04 | BBD131PP01LCS01 | BBD131PP01LCS01 | BBD131PP01 FIELD LOS TO BBD131PP01 BUCKET |  |  | BBD131DX04 |  |  | BR4-2150-E-00108 | [9 empty] | F12 | 65 | 66 | 67 | 68
[11 empty] | PNOZs4 |  |  | BBD131DX05 | BPP2104LCS01 | BPP2104LCS01 | BPP2104 FIELD LOS TO BPP2104 BUCKET |  |  | BBD131DX05 |  |  | BR4-2150-E-00109 | [9 empty] | F12 | 69 | 70 | 71 | 72 | BBD131DX05-C1 20 PAIR - ONLY 4 PAIR REQUIRED 6 PAIR ON DX05 TERM | BPP2105EM01-C2 2 PAIR | status to 2.1\0.8.4
[11 empty] | PNOZs4 |  |  | BBD131DX05 | BPP2105LCS01 | BPP2105LCS01 | BPP2105 FIELD LOS TO BPP2105 BUCKET |  |  | BBD131DX05 |  |  | BR4-2150-E-00077 | [9 empty] | F12 | 73 | 74 | 75 | 76 |  | BPP2105EM01-C2 2 PAIR | status to 2.1\0.8.8
[14 empty] | BCV131DX06 | BCV131PP02LCS01 | BCV131PP02LCS01 | BCV131PP02 FIELD LOS TO BCV131PP02 BUCKET |  |  | BCV131DX06 | [12 empty] | F12 | 77 | 78 | 79 | 80 | BCV131DX06-C1 20 PAIR - ONLY 10 PAIR REQUIRED 16 PAIR USED
[14 empty] | BCV131DX06 | BCV131AGB01LCS01 | BCV131AGB01LCS01 | BCV131AGB01LCS01 MASTER TO BCV131AFN01 BUCKET |  |  | BCV131DX06 | [12 empty] | F12 | 81 | 82 | 83 | 84
[14 empty] | BCV131DX06 | BCV131AFN02LCS01 | BCV131AFN02LCS01 | BCV131AFN02 SUB DX RELAY |  |  | BCV131DX06 | [12 empty] | F12 | 85 | 86 | 87 | 88
[11 empty] | PNOZs4 |  |  | BCV131DX06 | BCV131AFN02LCS01 | BCV131AFN02LCS01 | BCV131AFN02 MASTER TO BCV131AFAN02 BUCKET |  |  | BCV131DX06 |  |  | BR4-2150-E-00204 | [9 empty] | F12 | 89 | 90 | 91 | 92 |  |  | status to 2.1\0.9.3
[11 empty] | PNOZs7.1 |  |  | BCV131DX06 | BCV131AFN02LCS01 | BCV131AFN02LCS01 | BCV131AFN03 MASTER TO BCV131AFAN03 BUCKET |  | K405-1 | BCV131DX06 | [12 empty] | F12 | 93 | 94 | 95 | 96
[14 empty] | BCV131DX06 | BCV131BGB01LCS01 | BCV131BGB01LCS01 | BCV131BGB01LCS01 MASTER TO BCV131BFN01 BUCKET |  | K405-2 | BCV131DX06 | [12 empty] | F12 | 97 | 98 | 99 | 100
[14 empty] | BCV131DX06 | BCV131BFN02LCS01 | BCV131BFN02LCS01 | BCV131BFN02 SUB DX RELAY |  |  | BCV131DX06 | [12 empty] | F12 | 101 | 102 | 103 | 104
[11 empty] | PNOZs4 |  |  | BCV131DX06 | BCV131BFN02LCS01 | BCV131BFN02LCS01 | BCV131BFN02 FIELD LOS TO BCV131BFAN02 BUCKET |  |  | BCV131DX06 |  |  | BR4-2150-E-00205 | [9 empty] | F12 | 105 | 106 | 107 | 108 |  |  | status to 2.1\0.9.4
[11 empty] | PNOZs7.1 |  |  | BCV131DX06 | BCV131BFN02LCS01 | BCV131BFN02LCS01 | BCV131BFN03 FIELD LOS TO BCV131BFAN03 BUCKET |  | K420-1 | BCV131DX06 | [12 empty] | F12 | 109 | 110 | 111 | 112
[14 empty] | BCV131DX07 | BCV131PP03LCS01 | BCV131PP03LCS01 | BCV131PP03 FIELD LOS TO BCV131PP03 BUCKET |  | K420-2 | BCV131DX07 | [12 empty] | F12 | 113 | 114 | 115 | 116 | BCV131DX07-C1 20 PAIR - ONLY 6 PAIR REQUIRED 10 PAIR USED
[14 empty] | BCV131DX07 | BCV131CGB01LCS01 | BCV131CFN01LCS01 | BCV131CGB01LCS01 MASTER TO BCV131CFN01 BUCKET |  |  | BCV131DX07 | [12 empty] | F12 | 117 | 118 | 119 | 120
[14 empty] | BCV131DX07 | BCV131CFN02LCS01 | BCV131CFN02LCS01 | BCV131CFN02 SUB DX RELAY |  |  | BCV131DX07 |  |  | BR4-2150-E-00205 | [9 empty] | F12 | 121 | 122 | 123 | 124 |  |  | status to 2.1\0.9.5
[11 empty] | PNOZs4 |  |  | BCV131DX07 | BCV131CFN02LCS01 | BCV131CFN02LCS01 | BCV131CFN02 FIELD LOS TO BCV131CFAN02 BUCKET |  | K435-1 | BCV131DX07 | [12 empty] | F12 | 125 | 126 | 127 | 128
[11 empty] | PNOZs7.1 |  |  | BCV131DX07 | BCV131CFN02LCS01 | BCV131CFN02LCS01 | BCV131CFN03 FIELD LOS TO BCV131CFAN03 BUCKET |  | K435-2 | BCV131DX07 | [12 empty] | F12 | 129 | 130 | 131 | 132
[33 empty] | F12 | 133 | 134 | 135 | 136
[11 empty] | PNOZs7.1 |  |  | BCV131DX06 | BCV131AGB01LCS01 | BCV131AGB01LCS01 | BCV131AGB01LCS01 MASTER TO BCV131APP02 BUCKET |  |  | BCV131DX06 | [12 empty] | F12 | 137 | 138 | 139 | 140
[11 empty] | PNOZs7.1 |  |  | BCV131DX06 | BCV131BGB01LCS01 | BCV131BGB01LCS01 | BCV131BGB01LCS01 MASTER TO BCV131BPP02 BUCKET |  |  | BCV131DX06 | [12 empty] | F12 | 141 | 142 | 143 | 144
[11 empty] | PNOZs7.1 |  |  | BCV131DX07 | BCV131CGB01LCS01 | BCV131CFN01LCS01 | BCV131CGB01LCS01 MASTER TO BCV131CPP02 BUCKET |  |  | BCV131DX07 | [12 empty] | F12 | 145 | 146 | 147 | 148

## Field IO Assignment
Item | Box | Node | PLC | Bus | Drop | Rack | Slot | Ch | Terminal | Node Type | IO Type | Rev | Instrument Tag | Device | Instrument List Description | Desc2 | State | Location | Drive | Datatype | Address | Drawing | Rev | Notes | FAT | SAT | Raw_Zero | Raw_Full | Eng_Zero | Eng_Full | Format | T S | T1 | T2 | T3 | T4 |  | Alm_AREA | Alm_PRIV | Alm_HELP | Alm_CATEGORY | Alm_CUSTOM1 | Alm_CUSTOM2 | Alm_CUSTOM3 | Alm_CUSTOM4 | Alm_CUSTOM5 | Alm_CUSTOM6 | Alm_CUSTOM7 | Alm_CUSTOM8
BBD131DX03 - Surge Bin Facility - Top Floor
EIO node #3 | DX03 | DIO1 | 132 | 2 | 3 | 0
BBD131 | DX03 | DIO1 | 132 | 2 | 3 | 0 |  | Chassis |  | BMEXBP1200
BBD131 | DX03 | DIO1 | 132 | 2 | 3 | 0 |  | Power |  | BMXCPS4022 |  | total |  | spare |  | % spare
BBD131 | DX03 | DIO1 | 132 | 2 | 3 | 0 | 0 | Comms |  | BMECRA31210 | I/O1 | 40 |  | 56 |  | 140%
BBD131 | DX03 | DIO1 | 132 | 2 | 3 | 0 | 1 | 0 | BMXFCW303 | BMXDDI3202K | DI | 4 |  | CB01 |  | 240VAC Circuit Breaker - TO BDU131PN01 | Closed | Q106 | BBD131DX03 |  | 2.3\0.1:0 | BR4-2150-E-00128 | 0 |  | D | [6 empty] | F1 |  | 1
BBD131 | DX03 | DIO1 | 132 | 2 | 3 | 0 | 1 | 1 |  |  | DI | 4 |  | VDC01 |  | 24VDC DIO1 Output Control Supply | Healthy | Q143 | BBD131DX03 |  | 2.3\0.1:1 | BR4-2150-E-00128 | 0 |  | D | [6 empty] | F1 |  | 2
BBD131 | DX03 | DIO1 | 132 | 2 | 3 | 0 | 1 | 2 |  |  | DI | 4 |  | VDC02 |  | 24VDC GW1 Control Supply | Healthy | Q157 | BBD131DX03 |  | 2.3\0.1:2 | BR4-2150-E-00128 | 0 |  | D | [6 empty] | F1 |  | 3
BBD131 | DX03 | DIO1 | 132 | 2 | 3 | 0 | 1 | 3 |  |  | DI | 4 |  | VDC03 |  | 24VDC Instrument Supply | Healthy | Q164 | BBD131DX03 |  | 2.3\0.1:3 | BR4-2150-E-00128 | 0 |  | D | [6 empty] | F1 |  | 4
BBD131 | DX03 | DIO1 | 132 | 2 | 3 | 0 | 1 | 4 |  |  | DI | 4 |  | VDC04 |  | 24VDC Transmitter Supply | Healthy | Q168 | BBD131DX03 |  | 2.3\0.1:4 | BR4-2150-E-00128 | 0 |  | D | [6 empty] | F1 |  | 5
BBD131 | DX03 | DIO1 | 132 | 2 | 3 | 0 | 1 | 5 |  |  | DI | 4 |  | VDC05 |  | 24VDC BBD131DX03 Control Supply | Healthy | Q172 | BBD131DX03 |  | 2.3\0.1:5 | BR4-2150-E-00128 | 0 |  | D | [6 empty] | F1 |  | 6
BBD131 | DX03 | DIO1 | 132 | 2 | 3 | 0 | 1 | 6 |  |  | DI | 4 |  | VDC06 |  | 24VDC Spare Control Supply | Healthy | Q176 | BBD131DX03 |  | 2.3\0.1:6 | BR4-2150-E-00128 | 0 |  | D | [6 empty] | F1 |  | 7
BBD131 | DX03 | DIO1 | 132 | 2 | 3 | 0 | 1 | 7 |  |  | DI | 4 |  | VDC07 |  | 24VDC Spare Control Supply | Healthy | Q180 | BBD131DX03 |  | 2.3\0.1:7 | BR4-2150-E-00128 | 0 |  | D | [6 empty] | F1 |  | 8
BBD131 | DX03 | DIO1 | 132 | 2 | 3 | 0 | 1 | 8 |  |  | DI | 4 |  | VDC08 |  | 24VDC Spare Control Supply | Healthy | Q184 | BBD131DX03 |  | 2.3\0.1:8 | BR4-2150-E-00128 | 0 |  | D | [6 empty] | F1 |  | 9
BBD131 | DX03 | DIO1 | 132 | 2 | 3 | 0 | 1 | 9 |  |  | DI | 4 |  | VDC09 |  | 24VDC Spare Control Supply | Healthy | Q188 | BBD131DX03 |  | 2.3\0.1:9 | BR4-2150-E-00128 | 0 |  | D | [6 empty] | F1 |  | 10
BBD131 | DX03 | DIO1 | 132 | 2 | 3 | 0 | 1 | 10 |  |  | DI | 4 |  | VDC10 |  | 24VDC Spare Control Supply | Healthy | Q192 | BBD131DX03 |  | 2.3\0.1:10 | BR4-2150-E-00128 | 0 |  | D | [6 empty] | F1 |  | 11
BBD131 | DX03 | DIO1 | 132 | 2 | 3 | 0 | 1 | 11 |  |  | DI | 4 |  | VDC11 |  | 24VDC Spare Control Supply | Healthy | Q196 | BBD131DX03 |  | 2.3\0.1:11 | BR4-2150-E-00128 | 0 |  | D | [6 empty] | F1 |  | 12
BBD131 | DX03 | DIO1 | 132 | 2 | 3 | 0 | 1 | 12 |  |  | DI | [9 empty] | 2.3\0.1:12 |  |  |  | S | [6 empty] | F1 |  | 13
BBD131 | DX03 | DIO1 | 132 | 2 | 3 | 0 | 1 | 13 |  |  | DI | [9 empty] | 2.3\0.1:13 |  |  |  | S | [6 empty] | F1 |  | 14
BBD131 | DX03 | DIO1 | 132 | 2 | 3 | 0 | 1 | 14 |  |  | DI | [9 empty] | 2.3\0.1:14 |  |  |  | S | [6 empty] | F1 |  | 15
BBD131 | DX03 | DIO1 | 132 | 2 | 3 | 0 | 1 | 15 |  |  | DI | [9 empty] | 2.3\0.1:15 |  |  |  | S | [6 empty] | F1 |  | 16
BBD131 | DX03 | DIO1 | 132 | 2 | 3 | 0 | 1 | 16 |  |  | DI | 4 | BBN131LS01 | LS01 | LEVEL SWITCH HIGH-HIGH | Surge Bin Level Switch HiHi | Healthy | K203 | BBN131 |  | 2.3\0.1:16 | BR4-2150-E-00129 | 0 |  | D | [6 empty] | F1 | 17 | 18
BBD131 | DX03 | DIO1 | 132 | 2 | 3 | 0 | 1 | 17 |  |  | DI | 4 | BBN131LS02 | LS02 | LEVEL SWITCH HIGH-HIGH | Surge Bin Level Switch HiHi | Healthy | K216 | BBN131 |  | 2.3\0.1:17 | BR4-2150-E-00129 | 0 |  | D | [6 empty] | F1 | 19 | 20
BBD131 | DX03 | DIO1 | 132 | 2 | 3 | 0 | 1 | 18 |  |  | DI | 4 | BCV131CH01BCS01 | BCS01 | BCV131 HEAD CHUTE | Blocked Chute Switch | Healthy |  | BCV131CH01 |  | 2.3\0.1:18 | BR4-2150-E-00129 | 0 |  | S | [6 empty] | F1 | 21 | 22
BBD131 | DX03 | DIO1 | 132 | 2 | 3 | 0 | 1 | 19 |  |  | DI | 4 | BDU131FN01LCS01 | STT01 | SURGE BIN DUST COLLECTOR FAN | Start Pushbutton | Activated |  | BDU131FN01 |  | 2.3\0.1:19 | BR4-2150-E-00106 | A |  | S | [6 empty] | F1 | 23 | 24
BBD131 | DX03 | DIO1 | 132 | 2 | 3 | 0 | 1 | 20 |  |  | DI | 4 | BDU131FN01LCS01 | STP01 | SURGE BIN DUST COLLECTOR FAN | Stop Pushbutton | Activated |  | BDU131FN01 |  | 2.3\0.1:20 | BR4-2150-E-00106 | A |  | S | [6 empty] | F1 | 25 | 26
BBD131 | DX03 | DIO1 | 132 | 2 | 3 | 0 | 1 | 21 |  |  | DI | [9 empty] | 2.3\0.1:21 |  |  |  | S | [6 empty] | F1 | 27 | 28
BBD131 | DX03 | DIO1 | 132 | 2 | 3 | 0 | 1 | 22 |  |  | DI | [9 empty] | 2.3\0.1:22 |  |  |  | S | [6 empty] | F1 | 29 | 30
BBD131 | DX03 | DIO1 | 132 | 2 | 3 | 0 | 1 | 23 |  |  | DI | [9 empty] | 2.3\0.1:23 |  |  |  | S | [6 empty] | F1 | 31 | 32
BBD131 | DX03 | DIO1 | 132 | 2 | 3 | 0 | 1 | 24 |  |  | DI | [9 empty] | 2.3\0.1:24 |  |  |  | S | [6 empty] | F1 | 33 | 34
BBD131 | DX03 | DIO1 | 132 | 2 | 3 | 0 | 1 | 25 |  |  | DI | [9 empty] | 2.3\0.1:25 |  |  |  | S | [6 empty] | F1 | 35 | 36
BBD131 | DX03 | DIO1 | 132 | 2 | 3 | 0 | 1 | 26 |  |  | DI | [9 empty] | 2.3\0.1:26 |  |  |  | S | [6 empty] | F1 | 37 | 38
BBD131 | DX03 | DIO1 | 132 | 2 | 3 | 0 | 1 | 27 |  |  | DI | [9 empty] | 2.3\0.1:27 |  |  |  | S | [6 empty] | F1 | 39 | 40
BBD131 | DX03 | DIO1 | 132 | 2 | 3 | 0 | 1 | 28 |  |  | DI | [9 empty] | 2.3\0.1:28 |  |  |  | S | [6 empty] | F1 | 41 | 42
BBD131 | DX03 | DIO1 | 132 | 2 | 3 | 0 | 1 | 29 |  |  | DI | [9 empty] | 2.3\0.1:29 |  |  |  | S | [6 empty] | F1 | 43 | 44
BBD131 | DX03 | DIO1 | 132 | 2 | 3 | 0 | 1 | 30 |  |  | DI | [9 empty] | 2.3\0.1:30 |  |  |  | S | [6 empty] | F1 | 45 | 46
BBD131 | DX03 | DIO1 | 132 | 2 | 3 | 0 | 1 | 31 |  |  | DI | [9 empty] | 2.3\0.1:31 |  |  |  | S | [6 empty] | F1 | 47 | 48
BBD131 | DX03 | DIO1 | 132 | 2 | 3 | 0 | 2 |  |  | BMXXEM010 | [10 empty] | 2.3\0.2:
BBD131 | DX03 | DIO1 | 132 | 2 | 3 | 0 | 2 | [13 empty] | 2.3\0.2:
BBD131 | DX03 | DIO1 | 132 | 2 | 3 | 0 | 2 | [13 empty] | 2.3\0.2:
BBD131 | DX03 | DIO1 | 132 | 2 | 3 | 0 | 2 | [13 empty] | 2.3\0.2:
BBD131 | DX03 | DIO1 | 132 | 2 | 3 | 0 | 3 | 0 | BMXFTW301S | BMEAHI0812 | AI | 4 | BBN131LIT01 | LIT01 | SURGE BIN | Bin Level |  | mm | BBN131 | REAL | 2.3\0.3:0 | BR4-2150-E-00129 | 0 |  | S |  | 0 | 15000 | 0 | 15000 | #.# EU | F5 | 33 | 34
BBD131 | DX03 | DIO1 | 132 | 2 | 3 | 0 | 3 | 1 |  |  | AI | 4 | BBN131LIT02 | LIT02 | SURGE BIN | Bin Level |  | mm | BBN131 | REAL | 2.3\0.3:1 | BR4-2150-E-00129 | 0 |  | S |  | 0 | 15000 | 0 | 15000 | #.# EU | F5 | 35 | 36
BBD131 | DX03 | DIO1 | 132 | 2 | 3 | 0 | 3 | 2 |  |  | AI | 4 | BDU131PN01PDT01 | PDT01 | SURGE BIN DUST COLLECTOR FAN | Filter Bag Pressure Differential |  | kPa | BDU131PN01 | REAL | 2.3\0.3:2 | BR4-2150-E-00129 | 0 |  | S |  | 0 | 10 | 0 | 10 | #.# EU | F5 | 37 | 38
BBD131 | DX03 | DIO1 | 132 | 2 | 3 | 0 | 3 | 3 |  |  | AI | [9 empty] | 2.3\0.3:3 |  |  |  | S | [6 empty] | F5 | 39 | 40
BBD131 | DX03 | DIO1 | 132 | 2 | 3 | 0 | 3 | 4 |  |  | AI | [9 empty] | 2.3\0.3:4 |  |  |  | S | [6 empty] | F5 | 41 | 42
BBD131 | DX03 | DIO1 | 132 | 2 | 3 | 0 | 3 | 5 |  |  | AI | [9 empty] | 2.3\0.3:5 |  |  |  | S | [6 empty] | F5 | 43 | 44
BBD131 | DX03 | DIO1 | 132 | 2 | 3 | 0 | 3 | 6 |  |  | AI | [9 empty] | 2.3\0.3:6 |  |  |  | S | [6 empty] | F5 | 45 | 46
BBD131 | DX03 | DIO1 | 132 | 2 | 3 | 0 | 3 | 7 |  |  | AI | [9 empty] | 2.3\0.3:7 |  |  |  | S | [6 empty] | F5 | 47 | 48
BBD131 | DX03 | DIO1 | 132 | 2 | 3 | 0 | 4 |  |  | BMXXEM010 | [10 empty] | 2.3\0.4:
BBD131 | DX03 | DIO1 | 132 | 2 | 3 | 0 | 4 | [13 empty] | 2.3\0.4:
BBD131 | DX03 | DIO1 | 132 | 2 | 3 | 0 | 4 | [13 empty] | 2.3\0.4:
BBD131 | DX03 | DIO1 | 132 | 2 | 3 | 0 | 4 | [13 empty] | 2.3\0.4:
BBD131 | DX03 | DIO1 | 132 | 2 | 3 | 0 | 5 |  |  | BMXXEM010 | [10 empty] | 2.3\0.5:
BBD131 | DX03 | DIO1 | 132 | 2 | 3 | 0 | 5 | [13 empty] | 2.3\0.5:
BBD131 | DX03 | DIO1 | 132 | 2 | 3 | 0 | 5 | [13 empty] | 2.3\0.5:
BBD131 | DX03 | DIO1 | 132 | 2 | 3 | 0 | 5 | [13 empty] | 2.3\0.5:
BBD131 | DX03 | DIO1 | 132 | 2 | 3 | 0 | 6 |  |  | BMXXEM010 | [10 empty] | 2.3\0.6:
BBD131 | DX03 | DIO1 | 132 | 2 | 3 | 0 | 6 | [13 empty] | 2.3\0.6:
BBD131 | DX03 | DIO1 | 132 | 2 | 3 | 0 | 6 | [13 empty] | 2.3\0.6:
BBD131 | DX03 | DIO1 | 132 | 2 | 3 | 0 | 6 | [13 empty] | 2.3\0.6:
BBD131 | DX03 | DIO1 | 132 | 2 | 3 | 0 | 7 |  |  | BMXXEM010 | [10 empty] | 2.3\0.7:
BBD131 | DX03 | DIO1 | 132 | 2 | 3 | 0 | 7 | [13 empty] | 2.3\0.7:
BBD131 | DX03 | DIO1 | 132 | 2 | 3 | 0 | 7 | [13 empty] | 2.3\0.7:
BBD131 | DX03 | DIO1 | 132 | 2 | 3 | 0 | 7 | [13 empty] | 2.3\0.7:
BBD131 | DX03 | DIO1 | 132 | 2 | 3 | 0 | 8 |  |  | BMXXEM010 | [10 empty] | 2.3\0.8:
BBD131 | DX03 | DIO1 | 132 | 2 | 3 | 0 | 8 | [13 empty] | 2.3\0.8:
BBD131 | DX03 | DIO1 | 132 | 2 | 3 | 0 | 8 | [13 empty] | 2.3\0.8:
BBD131 | DX03 | DIO1 | 132 | 2 | 3 | 0 | 8 | [13 empty] | 2.3\0.8:
BBD131 | DX03 | DIO1 | 132 | 2 | 3 | 0 | 9 |  |  | BMXXEM010 | [10 empty] | 2.3\0.9:
BBD131 | DX03 | DIO1 | 132 | 2 | 3 | 0 | 9 | [13 empty] | 2.3\0.9:
BBD131 | DX03 | DIO1 | 132 | 2 | 3 | 0 | 9 | [13 empty] | 2.3\0.9:
BBD131 | DX03 | DIO1 | 132 | 2 | 3 | 0 | 9 | [13 empty] | 2.3\0.9:
BBD131 | DX03 | DIO1 | 132 | 2 | 3 | 0 | 10 |  |  | BMXXEM010 | [10 empty] | 2.3\0.10:
BBD131 | DX03 | DIO1 | 132 | 2 | 3 | 0 | 10 | [13 empty] | 2.3\0.10:
BBD131 | DX03 | DIO1 | 132 | 2 | 3 | 0 | 10 | [13 empty] | 2.3\0.10:
BBD131 | DX03 | DIO1 | 132 | 2 | 3 | 0 | 10 | [13 empty] | 2.3\0.10:
BBD131 | DX03 | DIO1 | 132 | 2 | 3 | 0 | 11 |  |  | BMXXEM010 | [10 empty] | 2.3\0.11:
BBD131 | DX03 | DIO1 | 132 | 2 | 3 | 0 | 11 | [13 empty] | 2.3\0.11:
BBD131 | DX03 | DIO1 | 132 | 2 | 3 | 0 | 11 | [13 empty] | 2.3\0.11:
BBD131 | DX03 | DIO1 | 132 | 2 | 3 | 0 | 11 | [13 empty] | 2.3\0.11:
[13 empty] | BDU131FN01LCS01 | LOS01 |  | BDU131FN01 Field LOS To Swrm DX/Bucket |  | SUB LINK | BDU131FN01 |  |  | BR4-2150-E-00106 | [9 empty] | F7 | 1 | 2 | 3 | 4
[13 empty] | BBN131 | LS01 |  | BBN131LS Field DX Panel Relay To Swrm DX |  | SUB LINK | BBN131 |  |  | BR4-2150-E-00203 | [9 empty] | F7 | 5 | 6 | 7 | 8
[32 empty] | F7 | 9 | 10 | 11 | 12
[32 empty] | F7 | 13 | 14 | 15 | 16
[32 empty] | F7 | 17 | 18 | 19 | 20
[32 empty] | F7 | 21 | 22 | 23 | 24
[32 empty] | F7 | 25 | 26 | 27 | 28
[32 empty] | F7 | 29 | 30 | 31 | 32
[32 empty] | F7 | 33 | 34 | 35 | 36
[32 empty] | F7 | 37 | 38 | 39 | 40
BBD131 | DX03 |  | 132 | [6 empty] | PNOZs4 |  | 3 | BBN131LS01 | LS01 |  | BBN131LS01 To Field DX Relay |  | K203 | BBN131 |  |  | BR4-2150-E-00129 | [9 empty] | F7 | 41 | 42 | 43 | 44
BBD131 | DX03 |  | 132 | [6 empty] | PNOZs4 |  | 3 | BBN131LS02 | LS02 |  | BBN131LS02 To Field DX Relay |  | K216 | BBN131 |  |  | BR4-2150-E-00129 | [9 empty] | F7 | 45 | 46 | 47 | 48
BBD131DX04 - Surge Bin Facility - Apron Feeder
EIO node #4 | DX04 | DIO1 | 132 | 2 | 4 | 0
BBD131 | DX04 | DIO1 | 132 | 2 | 4 | 0 |  | Chassis |  | BMEXBP1200
BBD131 | DX04 | DIO1 | 132 | 2 | 4 | 0 |  | Power |  | BMXCPS4022 |  | total |  | spare |  | % spare
BBD131 | DX04 | DIO1 | 132 | 2 | 4 | 0 | 0 | Comms |  | BMECRA31210 | I/O1 | 104 |  | 44 |  | 42.31%
BBD131 | DX04 | DIO1 | 132 | 2 | 4 | 0 | 1 | 0 | BMXFCW303 | BMXDDI3202K | DI | 3 |  | CB01 |  | 240VAC Circuit Breaker - Spare | Closed | Q106 | BBD131DX04 |  | 2.4\0.1:0 | BR4-2150-E-00131 | 0 |  | D | [6 empty] | F1 |  | 1
BBD131 | DX04 | DIO1 | 132 | 2 | 4 | 0 | 1 | 1 |  |  | DI | 3 |  | VDC01 |  | 24VDC DIO1 Output Control Supply | Healthy | Q143 | BBD131DX04 |  | 2.4\0.1:1 | BR4-2150-E-00131 | 0 |  | D | [6 empty] | F1 |  | 2
BBD131 | DX04 | DIO1 | 132 | 2 | 4 | 0 | 1 | 2 |  |  | DI | 3 |  | VDC02 |  | 24VDC GW1 Control Supply | Healthy | Q157 | BBD131DX04 |  | 2.4\0.1:2 | BR4-2150-E-00131 | 0 |  | D | [6 empty] | F1 |  | 3
BBD131 | DX04 | DIO1 | 132 | 2 | 4 | 0 | 1 | 3 |  |  | DI | 3 |  | VDC03 |  | 24VDC Instrument Supply | Healthy | Q164 | BBD131DX04 |  | 2.4\0.1:3 | BR4-2150-E-00131 | 0 |  | D | [6 empty] | F1 |  | 4
BBD131 | DX04 | DIO1 | 132 | 2 | 4 | 0 | 1 | 4 |  |  | DI | 3 |  | VDC04 |  | 24VDC Transmitter Supply | Healthy | Q168 | BBD131DX04 |  | 2.4\0.1:4 | BR4-2150-E-00131 | 0 |  | D | [6 empty] | F1 |  | 5
BBD131 | DX04 | DIO1 | 132 | 2 | 4 | 0 | 1 | 5 |  |  | DI | 4 |  | VDC05 |  | 24VDC BBD131DX04 Control Supply | Healthy | Q172 | BBD131DX04 |  | 2.4\0.1:5 | BR4-2150-E-00131 | 0 |  | D | [6 empty] | F1 |  | 6
BBD131 | DX04 | DIO1 | 132 | 2 | 4 | 0 | 1 | 6 |  |  | DI | 3 |  | VDC06 |  | 24VDC BAF131 Apron Feeder Control Supply | Healthy | Q176 | BBD131DX04 |  | 2.4\0.1:6 | BR4-2150-E-00131 | 0 |  | D | [6 empty] | F1 |  | 7
BBD131 | DX04 | DIO1 | 132 | 2 | 4 | 0 | 1 | 7 |  |  | DI | 4 |  | VDC07 |  | 24VDC BAF131LU01 Apron Feeder Lube Control Supply | Healthy | Q180 | BBD131DX04 |  | 2.4\0.1:7 | BR4-2150-E-00131 | 0 |  | D | [6 empty] | F1 |  | 8
BBD131 | DX04 | DIO1 | 132 | 2 | 4 | 0 | 1 | 8 |  |  | DI | 4 |  | VDC08 |  | 24VDC BAF131HP01PN01 Spider Control Panel | Healthy | Q184 | BBD131DX04 |  | 2.4\0.1:8 | BR4-2150-E-00131 | 0 |  | D | [6 empty] | F1 |  | 9
BBD131 | DX04 | DIO1 | 132 | 2 | 4 | 0 | 1 | 9 |  |  | DI | 3 |  | VDC09 |  | 24VDC BCV210WM01PN01 Control Panel | Healthy | Q188 | BBD131DX04 |  | 2.4\0.1:9 | BR4-2150-E-00131 | 0 |  | D | [6 empty] | F1 |  | 10
BBD131 | DX04 | DIO1 | 132 | 2 | 4 | 0 | 1 | 10 |  |  | DI | 3 |  | VDC10 |  | 24VDC BCV210AIT01 Control Supply | Healthy | Q192 | BBD131DX04 |  | 2.4\0.1:10 | BR4-2150-E-00131 | 0 |  | D | [6 empty] | F1 |  | 11
BBD131 | DX04 | DIO1 | 132 | 2 | 4 | 0 | 1 | 11 |  |  | DI | 4 |  | VDC11 |  | 24VDC BDU131DY01PN01 Control Supply | Healthy | Q196 | BBD131DX04 |  | 2.4\0.1:11 | BR4-2150-E-00131 | 0 |  | D | [6 empty] | F1 |  | 12
BBD131 | DX04 | DIO1 | 132 | 2 | 4 | 0 | 1 | 12 |  |  | DI | [9 empty] | 2.4\0.1:12 |  |  |  | S | [6 empty] | F1 |  | 13
BBD131 | DX04 | DIO1 | 132 | 2 | 4 | 0 | 1 | 13 |  |  | DI | [9 empty] | 2.4\0.1:13 |  |  |  | S | [6 empty] | F1 |  | 14
BBD131 | DX04 | DIO1 | 132 | 2 | 4 | 0 | 1 | 14 |  |  | DI | [9 empty] | 2.4\0.1:14 |  |  |  | S | [6 empty] | F1 |  | 15
BBD131 | DX04 | DIO1 | 132 | 2 | 4 | 0 | 1 | 15 |  |  | DI | [9 empty] | 2.4\0.1:15 |  |  |  | S | [6 empty] | F1 |  | 16
BBD131 | DX04 | DIO1 | 132 | 2 | 4 | 0 | 1 | 16 |  |  | DI | 4 | BBD131PP01LCS01 | STT01 | SURGE BIN SUMP PUMP | Start Pushbutton | Activated |  | BBD131PP01 |  | 2.4\0.1:16 | BR4-2150-E-00077 | A |  | S | [6 empty] | F1 | 17 | 18
BBD131 | DX04 | DIO1 | 132 | 2 | 4 | 0 | 1 | 17 |  |  | DI | 4 | BBD131PP01LCS01 | STP01 | SURGE BIN SUMP PUMP | Stop Pushbutton | Activated |  | BBD131PP01 |  | 2.4\0.1:17 | BR4-2150-E-00077 | A |  | S | [6 empty] | F1 | 19 | 20
BBD131 | DX04 | DIO1 | 132 | 2 | 4 | 0 | 1 | 18 |  |  | DI | 4 | BBD131PP01LCS01 | IS01 | SURGE BIN SUMP PUMP | Field Isolator | Closed |  | BBD131PP01 |  | 2.4\0.1:18 | BR4-2150-E-00077 | A |  | S | [6 empty] | F1 | 21 | 22
BBD131 | DX04 | DIO1 | 132 | 2 | 4 | 0 | 1 | 19 |  |  | DI | 3 | BAF131CH01BCS01 | BCS01 | SURGE BIN APRON FEEDER DISCHARGE CHUTE | Blocked Chute Switch 1 | Healthy |  | BAF131CH01 |  | 2.4\0.1:19 | BR4-2150-E-00132 | 0 |  | S | [6 empty] | F1 | 23 | 24
BBD131 | DX04 | DIO1 | 132 | 2 | 4 | 0 | 1 | 20 |  |  | DI | 3 | BAF131CH01BCS02 | BCS02 | SURGE BIN APRON FEEDER DISCHARGE CHUTE | Blocked Chute Switch 2 | Healthy |  | BAF131CH01 |  | 2.4\0.1:20 | BR4-2150-E-00132 | 0 |  | S | [6 empty] | F1 | 25 | 26
BBD131 | DX04 | DIO1 | 132 | 2 | 4 | 0 | 1 | 21 |  |  | DI | 3 | BDU131DY01 | XS01 | SURGE BIN DUST COLLECTOR | Air Dryer | Healthy |  | BDU131DY01 |  | 2.4\0.1:21 | BR4-2150-E-00132 | 0 |  | S | [6 empty] | F1 | 27 | 28
BBD131 | DX04 | DIO1 | 132 | 2 | 4 | 0 | 1 | 22 |  |  | DI | 3 | BDU131CP01 | XS01 | SURGE BIN DUST COLLECTOR | Air Compressor | Healthy |  | BDU131CP01 |  | 2.4\0.1:22 | BR4-2150-E-00132 | 0 |  | S | [6 empty] | F1 | 29 | 30
BBD131 | DX04 | DIO1 | 132 | 2 | 4 | 0 | 1 | 23 |  |  | DI | 3 | BDU131CP01 | XS02 | SURGE BIN DUST COLLECTOR | Air Compressor Supply | Healthy |  | BDU131CP01 |  | 2.4\0.1:23 | BR4-2150-E-00132 | 0 |  | S | [6 empty] | F1 | 31 | 32
BBD131 | DX04 | DIO1 | 132 | 2 | 4 | 0 | 1 | 24 |  |  | DI | 3 | BBD131FIT02 | FQ02 | BCV210 DUST SUPPRESSION SPRAY | Flow Totaliser Pulse | Active |  | BBD131 |  | 2.4\0.1:24 | BR4-2150-E-00134 | 0 | To be added to drawing as per markup. | S | [6 empty] | F1 | 33 | 34
BBD131 | DX04 | DIO1 | 132 | 2 | 4 | 0 | 1 | 25 |  |  | DI | 5 | BAF131HP01XS02 | XS02 | SURGE BIN APRON FEEDER HPU | AUXILIARY PUMP START INTERLOCK | Healthy |  | BAF131HP01 |  | 2.4\0.1:25 | BR4-2150-E-00373 | 0 | red pen MU on 134_0 | S | [6 empty] | F1 | 35 | 36
BBD131 | DX04 | DIO1 | 132 | 2 | 4 | 0 | 1 | 26 |  |  | DI | 3 | BAF131HP01XS01 | XS01 | SURGE BIN APRON FEEDER HPU | Spider Interlock | Healthy |  | BAF131HP01 |  | 2.4\0.1:26 | BR4-2150-E-00373 |  | red pen MU on 134_0 | S | [6 empty] | F1 | 37 | 38
BBD131 | DX04 | DIO1 | 132 | 2 | 4 | 0 | 1 | 27 |  |  | DI | 5 | [8 empty] | 2.4\0.1:27 |  |  | Duplicate of 2:11 | S | [6 empty] | F1 | 39 | 40
BBD131 | DX04 | DIO1 | 132 | 2 | 4 | 0 | 1 | 28 |  |  | DI | 3 | BAF131HP01FS01 | FS01 | SURGE BIN APRON FEEDER HPU | Fire Suppression Flow Switch | Healthy |  | BAF131HP01 |  | 2.4\0.1:28 | BR4-2150-E-00132 | 0 |  | S | [6 empty] | F1 | 41 | 42
BBD131 | DX04 | DIO1 | 132 | 2 | 4 | 0 | 1 | 29 |  |  | DI | 2 | BAF131HP01TS03 | TS03 | SURGE BIN APRON FEEDER HPU | FIRE DETECTION TEMPERATURE SWITCH | HIGH |  | BAF131HP01 |  | 2.4\0.1:29 | BR4-2150-E-00374 | 0 | red pen MU on 134_0 | S | [6 empty] | F1 | 43 | 44
BBD131 | DX04 | DIO1 | 132 | 2 | 4 | 0 | 1 | 30 |  |  | DI | [9 empty] | 2.4\0.1:30 |  |  |  | S | [6 empty] | F1 | 45 | 46
BBD131 | DX04 | DIO1 | 132 | 2 | 4 | 0 | 1 | 31 |  |  | DI | [9 empty] | 2.4\0.1:31 |  |  |  | S | [6 empty] | F1 | 47 | 48
BBD131 | DX04 | DIO1 | 132 | 2 | 4 | 0 | 2 | 0 | BMXFCW303 | BMXDDI3202K | DI | 4 | BAF131LCS01 | STT01 | SURGE BIN APRON FEEDER | Start Pushbutton | Activated |  | BAF131 |  | 2.4\0.2:0 | BR4-2150-E-00132 | 0 |  | S | [6 empty] | F2 | 1 | 2
BBD131 | DX04 | DIO1 | 132 | 2 | 4 | 0 | 2 | 1 |  |  | DI | 4 | BAF131LCS01 | REV01 | SURGE BIN APRON FEEDER | Rev Pushbutton | Activated |  | BAF131 |  | 2.4\0.2:1 | BR4-2150-E-00132 | 0 |  | S | [6 empty] | F2 | 3 | 4
BBD131 | DX04 | DIO1 | 132 | 2 | 4 | 0 | 2 | 2 |  |  | DI | 4 | BAF131LCS01 | STP01 | SURGE BIN APRON FEEDER | Stop Pushbutton | Activated |  | BAF131 |  | 2.4\0.2:2 | BR4-2150-E-00132 | 0 |  | S | [6 empty] | F2 | 5 | 6
BBD131 | DX04 | DIO1 | 132 | 2 | 4 | 0 | 2 | 3 |  |  | DI | 4 | BAF131HP01LCS01 | STT01 | SURGE BIN APRON FEEDER HPU PUMP 1 | BAF131PP01 Start Pushbutton | Activated |  | BAF131PP01 |  | 2.4\0.2:3 | BR4-2150-E-00099 | 0 |  | S | [6 empty] | F2 | 7 | 8
BBD131 | DX04 | DIO1 | 132 | 2 | 4 | 0 | 2 | 4 |  |  | DI | 4 | BAF131HP01LCS01 | STP01 | SURGE BIN APRON FEEDER HPU PUMP 1 | BAF131PP01 Stop Pushbutton | Activated |  | BAF131PP01 |  | 2.4\0.2:4 | BR4-2150-E-00099 | 0 |  | S | [6 empty] | F2 | 9 | 10
BBD131 | DX04 | DIO1 | 132 | 2 | 4 | 0 | 2 | 5 |  |  | DI | 4 | BAF131HP01LCS01 | STT02 | SURGE BIN APRON FEEDER HPU AUX. PUMP | BAF131PP04 Start Pushbutton | Activated |  | BAF131PP04 |  | 2.4\0.2:5 | BR4-2150-E-00061 | 0 |  | S | [6 empty] | F2 | 11 | 12
BBD131 | DX04 | DIO1 | 132 | 2 | 4 | 0 | 2 | 6 |  |  | DI | 4 | BAF131HP01LCS01 | STP02 | SURGE BIN APRON FEEDER HPU AUX. PUMP | BAF131PP04 Stop Pushbutton | Activated |  | BAF131PP04 |  | 2.4\0.2:6 | BR4-2150-E-00061 | 0 |  | S | [6 empty] | F2 | 13 | 14
BBD131 | DX04 | DIO1 | 132 | 2 | 4 | 0 | 2 | 7 |  |  | DI | 6 | BAF131FN01LCS01 | STT01 | SURGE BIN APRON FEEDER HPU OIL COOLER FAN | BAF131FN01 Start Pushbutton | Activated |  | BAF131FN01 |  | 2.4\0.2:7 | BR4-2150-E-00104 | 0 |  | S | [6 empty] | F2 | 15 | 16
BBD131 | DX04 | DIO1 | 132 | 2 | 4 | 0 | 2 | 8 |  |  | DI | 6 | BAF131FN01LCS01 | STP01 | SURGE BIN APRON FEEDER HPU OIL COOLER FAN | BAF131FN01 Stop Pushbutton | Activated |  | BAF131FN01 |  | 2.4\0.2:8 | BR4-2150-E-00104 | 0 |  | S | [6 empty] | F2 | 17 | 18
BBD131 | DX04 | DIO1 | 132 | 2 | 4 | 0 | 2 | 9 |  |  | DI | 4 | BAF131PWS01 | PWS01 | SURGE BIN APRON FEEDER | Pullwire Switch Safety Relay | Healthy | K253 | BAF131 |  | 2.4\0.2:9 | BR4-2150-E-00132 | 0 |  | S | [6 empty] | F2 | 19 | 20
BBD131 | DX04 | DIO1 | 132 | 2 | 4 | 0 | 2 | 10 |  |  | DI | 4 | BAF131PWS02 | PWS02 | SURGE BIN APRON FEEDER | Pullwire Switch Safety Relay | Healthy | K264 | BAF131 |  | 2.4\0.2:10 | BR4-2150-E-00132 | 0 |  | S | [6 empty] | F2 | 21 | 22
BBD131 | DX04 | DIO1 | 132 | 2 | 4 | 0 | 2 | 11 |  |  | DI | 5 | BAF131PP01THR01 | THR01 | SURGE BIN APRON FEEDER | BAF131PP01EM01 Thermistor | Healthy | K185 | BAF131PP01 |  | 2.4\0.2:11 | BR4-2150-E-00099 | 0 |  | S | [6 empty] | F2 | 23 | 24
BBD131 | DX04 | DIO1 | 132 | 2 | 4 | 0 | 2 | 12 |  |  | DI | 4 | BAF131LCS01 | SY01 | BAF131LCS01 SAFTEY RELAY | BAF131LCS01 Safety Relay | Healthy | K276 | BAF131 |  | 2.4\0.2:12 | BR4-2150-E-00132 | 0 |  | D | [6 empty] | F2 | 25 | 26
BBD131 | DX04 | DIO1 | 132 | 2 | 4 | 0 | 2 | 13 |  |  | DI | 4 | BAF131HP01LCS01 | SY01 | BAF131HP01LCS01 SAFTEY RELAY | BAF131HP01LCS01 Safety Relay | Healthy | K233 | BAF131HP01 |  | 2.4\0.2:13 | BR4-2150-E-00132 | 0 |  | D | [6 empty] | F2 | 27 | 28
BBD131 | DX04 | DIO1 | 132 | 2 | 4 | 0 | 2 | 14 |  |  | DI | [9 empty] | 2.4\0.2:14 |  |  |  | S | [6 empty] | F2 | 29 | 30
BBD131 | DX04 | DIO1 | 132 | 2 | 4 | 0 | 2 | 15 |  |  | DI | [9 empty] | 2.4\0.2:15 |  |  |  | S | [6 empty] | F2 | 31 | 32
BBD131 | DX04 | DIO1 | 132 | 2 | 4 | 0 | 2 | 16 |  |  | DI | 4 | BAF131PP02LCS01 | STT01 | Surge Bin Apron Fdr Lube Unit Hyd Pump | Start Pushbutton | Activated |  | BAF131PP02 |  | 2.4\0.2:16 | BR4-2150-E-00103 | 0 |  | S | [6 empty] | F3 | 1 | 2
BBD131 | DX04 | DIO1 | 132 | 2 | 4 | 0 | 2 | 17 |  |  | DI | 4 | BAF131PP02LCS01 | STP01 | Surge Bin Apron Fdr Lube Unit Hyd Pump | Stop Pushbutton | Activated |  | BAF131PP02 |  | 2.4\0.2:17 | BR4-2150-E-00103 | 0 |  | S | [6 empty] | F3 | 3 | 4
BBD131 | DX04 | DIO1 | 132 | 2 | 4 | 0 | 2 | 18 |  |  | DI | 4 | BAF131ZS01 | ZS01 | SURGE BIN APRON FEEDER | Chain Locking Aft. Maintenance Proximity Switch | Healthy |  | BAF131 |  | 2.4\0.2:18 | BR4-2150-E-00133 | 0 |  | S | [6 empty] | F3 | 5 | 6
BBD131 | DX04 | DIO1 | 132 | 2 | 4 | 0 | 2 | 19 |  |  | DI | 4 | BAF131ZS02 | ZS02 | SURGE BIN APRON FEEDER | Chain Locking Fwd. Maintenance Proximity Switch | Healthy |  | BAF131 |  | 2.4\0.2:19 | BR4-2150-E-00133 | 0 |  | S | [6 empty] | F3 | 7 | 8
BBD131 | DX04 | DIO1 | 132 | 2 | 4 | 0 | 2 | 20 |  |  | DI | 4 | BAF131ZS03 | ZS03 | SURGE BIN APRON FEEDER | Chain Locking Aft. Maintenance Proximity Switch | Healthy |  | BAF131 |  | 2.4\0.2:20 | BR4-2150-E-00133 | 0 |  | S | [6 empty] | F3 | 9 | 10
BBD131 | DX04 | DIO1 | 132 | 2 | 4 | 0 | 2 | 21 |  |  | DI | 4 | BAF131ZS04 | ZS04 | SURGE BIN APRON FEEDER LASHING LUG FWD. MAINTENACE | Chain Locking Fwd. Maintenance Proximity Switch | Healthy |  | BAF131 |  | 2.4\0.2:21 | BR4-2150-E-00133 | 0 |  | S | [6 empty] | F3 | 11 | 12
BBD131 | DX04 | DIO1 | 132 | 2 | 4 | 0 | 2 | 22 |  |  | DI | 4 | BAF131LU01PS01 | PS01 | SURGE BIN APRON FEEDER Lube Unit | Grease Tank Inlet Filter | Blocked |  | BAF131LU01 |  | 2.4\0.2:22 | BR4-2150-E-00133 | 0 |  | S | [6 empty] | F3 | 13 | 14
BBD131 | DX04 | DIO1 | 132 | 2 | 4 | 0 | 2 | 23 |  |  | DI | 4 | BAF131LU01PS02 | PS02 | SURGE BIN APRON FEEDER Lube Unit | Grease Pump Outlet Filter | Blocked |  | BAF131LU01 |  | 2.4\0.2:23 | BR4-2150-E-00133 | 0 |  | S | [6 empty] | F3 | 15 | 16
BBD131 | DX04 | DIO1 | 132 | 2 | 4 | 0 | 2 | 24 |  |  | DI | 4 | BAF13LU01LS01 | LS01 | SURGE BIN APRON FEEDER Lube Unit | Oil Tank Level Switch | Healthy |  | BAF131LU01 |  | 2.4\0.2:24 | BR4-2150-E-00133 | 0 |  | S | [6 empty] | F3 | 17 | 18
BBD131 | DX04 | DIO1 | 132 | 2 | 4 | 0 | 2 | 25 |  |  | DI | 3 | BAF131LU01FS01 | FQ01 | SURGE BIN APRON FEEDER LUBE UNIT | Grease Pulse Meter | Active |  | BAF131LU01 |  | 2.4\0.2:25 | BR4-2150-E-00133 | 0 |  | S | [6 empty] | F3 | 19 | 20
BBD131 | DX04 | DIO1 | 132 | 2 | 4 | 0 | 2 | 26 |  |  | DI | 3 | BAF131LU01ZS01 | ZS01 | SURGE BIN APRON FEEDER Lube Unit | End Of Line Proximity Switch 1 | Cycled |  | BAF131LU01 |  | 2.4\0.2:26 | BR4-2150-E-00133 | 0 |  | S | [6 empty] | F3 | 21 | 22
BBD131 | DX04 | DIO1 | 132 | 2 | 4 | 0 | 2 | 27 |  |  | DI | 3 | BAF131LU01ZS02 | ZS02 | SURGE BIN APRON FEEDER LUBE UNIT | End Of Line Proximity Switch 2 | Cycled |  | BAF131LU01 |  | 2.4\0.2:27 | BR4-2150-E-00133 | 0 |  | S | [6 empty] | F3 | 23 | 24
BBD131 | DX04 | DIO1 | 132 | 2 | 4 | 0 | 2 | 28 |  |  | DI | 4 | BAF131ZS05 | ZS05 | SURGE BIN APRON FEEDER | Pan Deflection Switch 1 | Activated |  | BAF131 |  | 2.4\0.2:28 | BR4-2150-E-00133 | 0 |  | S | [6 empty] | F3 | 25 | 26
BBD131 | DX04 | DIO1 | 132 | 2 | 4 | 0 | 2 | 29 |  |  | DI | 4 | BAF131ZS06 | ZS06 | SURGE BIN APRON FEEDER | Pan Deflection Switch 2 | Activated |  | BAF131 |  | 2.4\0.2:29 | BR4-2150-E-00133 | 0 |  | S | [6 empty] | F3 | 27 | 28
BBD131 | DX04 | DIO1 | 132 | 2 | 4 | 0 | 2 | 30 |  |  | DI | 7 | BCV210AIT01 | ZS01 | BELT PROFILE SCANNER POSITION SWITCH | POSITION SWITCH | IN POSITION |  | BCV210AIT01 |  | 2.4\0.2:30 |  |  |  | S | [6 empty] | F3 | 29 | 30
BBD131 | DX04 | DIO1 | 132 | 2 | 4 | 0 | 2 | 31 |  |  | DI | [9 empty] | 2.4\0.2:31 |  |  |  | S | [6 empty] | F3 | 31 | 32
BBD131 | DX04 | DIO1 | 132 | 2 | 4 | 0 | 3 | 0 | BMXFTB2010 | BMXDDO1602 | DO | 4 | BBD131PP01SV01 | SV01 | Surge Bin Facility Sump Pump | Sump Pump Solenoid Valve |  |  | BBD131PP01 |  | 2.4\0.3:0 | BR4-2150-E-00133 | 0 |  | S | [6 empty] | F5 | 1 | 2
BBD131 | DX04 | DIO1 | 132 | 2 | 4 | 0 | 3 | 1 |  |  | DO | 3 | BDU131CP01 | SR01 | SURGE BIN DUST COLLECTOR | Air Compressor Run |  |  | BDU131CP01 |  | 2.4\0.3:1 | BR4-2150-E-00133 | 0 |  | S | [6 empty] | F5 | 3 | 4
BBD131 | DX04 | DIO1 | 132 | 2 | 4 | 0 | 3 | 2 |  |  | DO | 3 | BBD131SV02 | SV02 | BCV210 DUST SUPPRESSION SPRAY | BCV210 Dust Suppression Spray |  |  | BBD131 |  | 2.4\0.3:2 | BR4-2150-E-00133 | 0 |  | S | [6 empty] | F5 | 5 | 6
BBD131 | DX04 | DIO1 | 132 | 2 | 4 | 0 | 3 | 3 |  |  | DO | 4 | BSR132DB03 | SR01 | BSR132DB03 | BSR132DB03 Lighting Relay |  |  | BSR132DB03 |  | 2.4\0.3:3 | BR4-2150-E-00117 | A |  | S | [6 empty] | F5 | 7 | 8
BBD131 | DX04 | DIO1 | 132 | 2 | 4 | 0 | 3 | 4 |  |  | DO | 3 | BAF131HP01 | SR01 | SURGE BIN APRON FEEDER HPU | Pump 1 Run Relay |  |  | BAF131HP01 |  | 2.4\0.3:4 | BR4-2150-E-00133 | 0 | red pen MU on 133_0 | S | [6 empty] | F5 | 9 | 10
BBD131 | DX04 | DIO1 | 132 | 2 | 4 | 0 | 3 | 5 |  |  | DO | 3 | BAF131HP01 | SR02 | SURGE BIN APRON FEEDER HPU | Stop Interlock |  |  | BAF131HP01 |  | 2.4\0.3:5 | BR4-2150-E-00133 | 0 | red pen MU on 133_0 | S | [6 empty] | F5 | 11 | 12
BBD131 | DX04 | DIO1 | 132 | 2 | 4 | 0 | 3 | 6 |  |  | DO | 3 | BAF131YA01 | YA01 | SURGE BIN APRON FEEDER | Start Up Warning Siren |  |  | BAF131 |  | 2.4\0.3:6 | BR4-2150-E-00133 | 0 |  | S | [6 empty] | F5 | 13 | 14
BBD131 | DX04 | DIO1 | 132 | 2 | 4 | 0 | 3 | 7 |  |  | DO | [9 empty] | 2.4\0.3:7 |  |  |  | S | [6 empty] | F5 | 15 | 16
BBD131 | DX04 | DIO1 | 132 | 2 | 4 | 0 | 3 | 8 |  |  | DO | 3 | BAF131LU01SV02 | SV02 | SURGE BIN APRON FEEDER Lube Unit | Grease Line 1 Solenoid Valve |  |  | BAF131LU01 |  | 2.4\0.3:8 | BR4-2150-E-00133 | 0 | Grease Reversing Valve Line 1 on dwg | S | [6 empty] | F5 | 17 | 18
BBD131 | DX04 | DIO1 | 132 | 2 | 4 | 0 | 3 | 9 |  |  | DO | 3 | BAF131LU01SV03 | SV03 | SURGE BIN APRON FEEDER Lube Unit | Grease Line 2 Solenoid Valve |  |  | BAF131LU01 |  | 2.4\0.3:9 | BR4-2150-E-00133 | 0 | Grease Reversing Valve Line 2 on dwg | S | [6 empty] | F5 | 19 | 20
BBD131 | DX04 | DIO1 | 132 | 2 | 4 | 0 | 3 | 10 |  |  | DO | 3 | BAF131LU01SV04 | SV04 | SURGE BIN APRON FEEDER Lube Unit | Grease Inlet Shut Off Valve |  |  | BAF131LU01 |  | 2.4\0.3:10 | BR4-2150-E-00133 | 0 |  | S | [6 empty] | F5 | 21 | 22
BBD131 | DX04 | DIO1 | 132 | 2 | 4 | 0 | 3 | 11 |  |  | DO | 3 | BAF131LU01SV01 | SV01 | SURGE BIN APRON FEEDER Lube Unit | Oil Pump Solenoid Valve |  |  | BAF131LU01 |  | 2.4\0.3:11 | BR4-2150-E-00133 | 0 | Oil Direction Control Valve on dwg | S | [6 empty] | F5 | 23 | 24
BBD131 | DX04 | DIO1 | 132 | 2 | 4 | 0 | 3 | 12 |  |  | DO | 3 | BAF131LU01YL01 | YL01 | SURGE BIN APRON FEEDER Lube Unit | Grease End Of Line 1 Cycle Complete Lamp | Activated |  | BAF131LU01 |  | 2.4\0.3:12 | BR4-2150-E-00133 | 0 |  | S | [6 empty] | F5 | 25 | 26
BBD131 | DX04 | DIO1 | 132 | 2 | 4 | 0 | 3 | 13 |  |  | DO | 3 | BAF131LU01YL02 | YL02 | SURGE BIN APRON FEEDER Lube Unit | Grease End Of Line 2 Cycle Complete Lamp | Activated |  | BAF131LU01 |  | 2.4\0.3:13 | BR4-2150-E-00133 | 0 |  | S | [6 empty] | F5 | 27 | 28
BBD131 | DX04 | DIO1 | 132 | 2 | 4 | 0 | 3 | 14 |  |  | DO | [9 empty] | 2.4\0.3:14 |  |  |  | S | [6 empty] | F5 | 29 | 30
BBD131 | DX04 | DIO1 | 132 | 2 | 4 | 0 | 3 | 15 |  |  | DO | [9 empty] | 2.4\0.3:15 |  |  |  | S | [6 empty] | F5 | 31 | 32
BBD131 | DX04 | DIO1 | 132 | 2 | 4 | 0 | 4 | 0 | BMXFTW301S | BMEAHI0812 | AI | 4 | BAF131LU01PT01 | PT01 | SURGE BIN APRON FEEDER Lube Unit | End Of Line 1 Pressure Transducer |  | PSI | BAF131LU01 | REAL | 2.4\0.4:0 | BR4-2150-E-00134 | 0 |  | S |  | 0 | 5000 | 0 | 5000 | # EU | F5 | 33 | 34
BBD131 | DX04 | DIO1 | 132 | 2 | 4 | 0 | 4 | 1 |  |  | AI | 4 | BAF131LU01PT02 | PT02 | SURGE BIN APRON FEEDER Lube Unit | End Of Line 2 Pressure Transducer |  | PSI | BAF131LU01 | REAL | 2.4\0.4:1 | BR4-2150-E-00134 | 0 |  | S |  | 0 | 5000 | 0 | 5000 | # EU | F5 | 35 | 36
BBD131 | DX04 | DIO1 | 132 | 2 | 4 | 0 | 4 | 2 |  |  | AI | 3 | BAF131LU01PT03 | PT03 | SURGE BIN APRON FEEDER Lube Unit | Oil Pressure Transducer |  | PSI | BAF131LU01 | REAL | 2.4\0.4:2 | BR4-2150-E-00134 | 0 |  | S |  | 0 | 500 | 0 | 500 | # EU | F5 | 37 | 38
BBD131 | DX04 | DIO1 | 132 | 2 | 4 | 0 | 4 | 3 |  |  | AI | 4 | BAF131LU01PT04 | PT04 | SURGE BIN APRON FEEDER Lube Unit | Pump Line 1 Pressure Transducer |  | PSI | BAF131LU01 | REAL | 2.4\0.4:3 | BR4-2150-E-00134 | 0 |  | S |  | 0 | 5000 | 0 | 5000 | # EU | F5 | 39 | 40
BBD131 | DX04 | DIO1 | 132 | 2 | 4 | 0 | 4 | 4 |  |  | AI | 4 | BAF131LU01PT05 | PT05 | SURGE BIN APRON FEEDER Lube Unit | Pump Line 2 Pressure Transducer |  | PSI | BAF131LU01 | REAL | 2.4\0.4:4 | BR4-2150-E-00134 | 0 |  | S |  | 0 | 5000 | 0 | 5000 | # EU | F5 | 41 | 42
BBD131 | DX04 | DIO1 | 132 | 2 | 4 | 0 | 4 | 5 |  |  | AI | 3 | BAF131LU01LT01 | LT01 | SURGE BIN APRON FEEDER Lube Unit | Grease Level Transducer |  | % | BAF131LU01 | REAL | 2.4\0.4:5 | BR4-2150-E-00134 | 0 |  | S |  | 0 | 100 | 0 | 100 | #.# EU | F5 | 43 | 44
BBD131 | DX04 | DIO1 | 132 | 2 | 4 | 0 | 4 | 6 |  |  | AI | [9 empty] | 2.4\0.4:6 | [10 empty] | F5 | 45 | 46
BBD131 | DX04 | DIO1 | 132 | 2 | 4 | 0 | 4 | 7 |  |  | AI | [9 empty] | 2.4\0.4:7 | [10 empty] | F5 | 47 | 48
BBD131 | DX04 | DIO1 | 132 | 2 | 4 | 0 | 5 | 0 | BMXFTW301S | BMEAHI0812 | AI | 4 | BBD131SM01LIT01 | LIT01 | SURGE BIN FACILITY SUMP | Sump Level |  | % | BBD131SM01 | REAL | 2.4\0.5:0 | BR4-2150-E-00134 | 0 |  | S |  | 0 | 100 | 0 | 100 | #.# EU | F4 | 1 | 2
BBD131 | DX04 | DIO1 | 132 | 2 | 4 | 0 | 5 | 1 |  |  | AI | 4 | BDU131CP01PIT01 | PT01 | SURGE BIN DUST COLLECTOR AIR COMPRESSOR | Pressure |  | kPa | BDU131CP01 | REAL | 2.4\0.5:1 | BR4-2150-E-00134 | 0 |  | S |  | 0 | 10 | 0 | 10 | #.# EU | F4 | 3 | 4
BBD131 | DX04 | DIO1 | 132 | 2 | 4 | 0 | 5 | 2 |  |  | AI | 4 | BBD131FIT02 | FT02 | BCV210 DUST SUPPRESSION SPRAY | Flow Rate |  | L/s | BBD131 | REAL | 2.4\0.5:2 | BR4-2150-E-00134 | 0 | To be added to drawing BR4-2150-E-00134. | S | [6 empty] | F4 | 5 | 6
BBD131 | DX04 | DIO1 | 132 | 2 | 4 | 0 | 5 | 3 |  |  | AI | 3 | BAF131HP01TT02 | TT02 | SURGE BIN APRON FEEDER HPU | Oil Cooler Inlet Temperature |  | C | BAF131HP01 | REAL | 2.4\0.5:3 | BR4-2150-E-00374/BR4-2150-E-00250 | B | MISSING - needs addition to schematic & termination | S |  | 0 | 100 | 0 | 100 | #.# EU | F4 | 7 | 8
BBD131 | DX04 | DIO1 | 132 | 2 | 4 | 0 | 5 | 4 |  |  | AI | 3 | BAF131HP01TT03 | TT03 | SURGE BIN APRON FEEDER HPU | Oil Cooler Outlet Temperature |  | C | BAF131HP01 | REAL | 2.4\0.5:4 | BR4-2150-E-00374/BR4-2150-E-00250 | B | MISSING - needs addition to schematic & termination | S |  | 0 | 100 | 0 | 100 | #.# EU | F4 | 9 | 10
BBD131 | DX04 | DIO1 | 132 | 2 | 4 | 0 | 5 | 5 |  |  | AI | [9 empty] | 2.4\0.5:5 | [10 empty] | F4 | 11 | 12
BBD131 | DX04 | DIO1 | 132 | 2 | 4 | 0 | 5 | 6 |  |  | AI | [9 empty] | 2.4\0.5:6 | [10 empty] | F4 | 13 | 14
BBD131 | DX04 | DIO1 | 132 | 2 | 4 | 0 | 5 | 7 |  |  | AI | [9 empty] | 2.4\0.5:7 | [10 empty] | F4 | 15 | 16
BBD131 | DX04 | DIO1 | 132 | 2 | 4 | 0 | 6 | 0 | BMXFTB2010 | BMXEHC0800 | HSCI | 3 | BAF131SS01 | SS01 | SURGE BIN APRON FEEDER | Underspeed Pulse |  |  | BAF131 |  | 2.4\0.6:0 | BR4-2150-E-00132 | 0 |  | S | [6 empty] | F2 | 33 | 34
BBD131 | DX04 | DIO1 | 132 | 2 | 4 | 0 | 6 | 1 |  |  | HSCI | 3 | BAF131SS01 | ZQ01 | SURGE BIN APRON FEEDER | Distance Pulse |  |  | BAF131 |  | 2.4\0.6:1 | BR4-2150-E-00132 | 0 |  | S | [6 empty] | F2 | 35 | 36
BBD131 | DX04 | DIO1 | 132 | 2 | 4 | 0 | 6 | 2 |  |  | HSCI | [9 empty] | 2.4\0.6:2 |  |  |  | S | [6 empty] | F2 | 37 | 38
BBD131 | DX04 | DIO1 | 132 | 2 | 4 | 0 | 6 | 3 |  |  | HSCI | [9 empty] | 2.4\0.6:3 |  |  |  | S | [6 empty] | F2 | 39 | 40
BBD131 | DX04 | DIO1 | 132 | 2 | 4 | 0 | 6 | 4 |  |  | HSCI | [9 empty] | 2.4\0.6:4 |  |  |  | S | [6 empty] | F2 | 41 | 42
BBD131 | DX04 | DIO1 | 132 | 2 | 4 | 0 | 6 | 5 |  |  | HSCI | [9 empty] | 2.4\0.6:5 |  |  |  | S | [6 empty] | F2 | 43 | 44
BBD131 | DX04 | DIO1 | 132 | 2 | 4 | 0 | 6 | 6 |  |  | HSCI | [9 empty] | 2.4\0.6:6 |  |  |  | S | [6 empty] | F2 | 45 | 46
BBD131 | DX04 | DIO1 | 132 | 2 | 4 | 0 | 6 | 7 |  |  | HSCI | [9 empty] | 2.4\0.6:7 |  |  |  | S | [6 empty] | F2 | 47 | 48
BBD131 | DX04 | DIO1 | 132 | 2 | 4 | 0 | 7 |  |  | BMXXEM010 | [10 empty] | 2.4\0.7:
BBD131 | DX04 | DIO1 | 132 | 2 | 4 | 0 | 7 | [13 empty] | 2.4\0.7:
BBD131 | DX04 | DIO1 | 132 | 2 | 4 | 0 | 7 | [13 empty] | 2.4\0.7:
BBD131 | DX04 | DIO1 | 132 | 2 | 4 | 0 | 7 | [13 empty] | 2.4\0.7:
BBD131 | DX04 | DIO1 | 132 | 2 | 4 | 0 | 8 |  |  | BMXXEM010 | [10 empty] | 2.4\0.8:
BBD131 | DX04 | DIO1 | 132 | 2 | 4 | 0 | 8 | [13 empty] | 2.4\0.8:
BBD131 | DX04 | DIO1 | 132 | 2 | 4 | 0 | 8 | [13 empty] | 2.4\0.8:
BBD131 | DX04 | DIO1 | 132 | 2 | 4 | 0 | 8 | [13 empty] | 2.4\0.8:
BBD131 | DX04 | DIO1 | 132 | 2 | 4 | 0 | 9 |  |  | BMXXEM010 | [10 empty] | 2.4\0.9:
BBD131 | DX04 | DIO1 | 132 | 2 | 4 | 0 | 9 | [13 empty] | 2.4\0.9:
BBD131 | DX04 | DIO1 | 132 | 2 | 4 | 0 | 9 | [13 empty] | 2.4\0.9:
BBD131 | DX04 | DIO1 | 132 | 2 | 4 | 0 | 9 | [13 empty] | 2.4\0.9:
BBD131 | DX04 | DIO1 | 132 | 2 | 4 | 0 | 10 |  |  | BMXXEM010 | [10 empty] | 2.4\0.10:
BBD131 | DX04 | DIO1 | 132 | 2 | 4 | 0 | 10 | [13 empty] | 2.4\0.10:
BBD131 | DX04 | DIO1 | 132 | 2 | 4 | 0 | 10 | [13 empty] | 2.4\0.10:
BBD131 | DX04 | DIO1 | 132 | 2 | 4 | 0 | 10 | [13 empty] | 2.4\0.10:
BBD131 | DX04 | DIO1 | 132 | 2 | 4 | 0 | 11 |  |  | BMXXEM010 | [10 empty] | 2.4\0.11:
BBD131 | DX04 | DIO1 | 132 | 2 | 4 | 0 | 11 | [13 empty] | 2.4\0.11:
BBD131 | DX04 | DIO1 | 132 | 2 | 4 | 0 | 11 | [13 empty] | 2.4\0.11:
BBD131 | DX04 | DIO1 | 132 | 2 | 4 | 0 | 11 | [13 empty] | 2.4\0.11:
[12 empty] | 5 | BAF131PP02LCS01 | LOS01 |  | BAF131PP02 Field LOS To Swrm DX Panel/Bucket |  | SUB LINK | BAF131PP02 |  |  | BR4-2150-E-00103 | [9 empty] | F7 | 1 | 2 | 3 | 4
[13 empty] | BAF131 | LOS01 |  | BAF131Field LOS To Swrm DX Panel Master Relay |  | SUB LINK | BAF131 |  |  | BR4-2150-E-00204 | [9 empty] | F7 | 5 | 6 | 7 | 8
[12 empty] | 5 | BAF131FN01LCS01 | LOS01 |  | BAF131FN01 Field LOS To Swrm DX Panel/Bucket |  | SUB LINK | BAF131FN01 |  |  | BR4-2150-E-00104 | [9 empty] | F7 | 9 | 10 | 11 | 12
[12 empty] | 5 | BBD131PP01LCS01 | LOS01 |  | BBD131PP01 Field LOS To Swrm DX Panel/Bucket |  | SUB LINK | BBD131PP01 |  |  | BR4-2150-E-00077 | [9 empty] | F7 | 13 | 14 | 15 | 16
[32 empty] | F7 | 17 | 18 | 19 | 20
[32 empty] | F7 | 21 | 22 | 23 | 24
BBD131 | DX04 |  | 132 | [6 empty] | PNOZs4 |  | 3 | BAF131HP01LCS01 |  |  | BAF131HP01LCS01To Field DX Relay |  | KXXX | BAF131HP01 |  |  | BR4-2150-E-00132 | [9 empty] | F7 | 25 | 26 | 27 | 28
BBD131 | DX04 |  | 132 | [6 empty] | PNOZs4 |  | 5 | BAF131LCS01 |  |  | BAF131LCS01 To Field DX Relay |  | K276 | BAF131 |  |  | BR4-2150-E-00132 | [9 empty] | F7 | 29 | 30 | 31 | 32
BBD131 | DX04 |  | 132 | [6 empty] | PNOZs4 |  | 3 | BAF131PWS01 | PWS01 |  | BAF131PWS01 To Field DX Relay |  | K253 | BAF131 |  |  | BR4-2150-E-00132 | [9 empty] | F7 | 33 | 34 | 35 | 36
BBD131 | DX04 |  | 132 | [6 empty] | PNOZs4 |  | 3 | BAF131PWS02 | PWS02 |  | BAF131PWS02 To Field DX Relay |  | K264 | BAF131 |  |  | BR4-2150-E-00132 | [9 empty] | F7 | 37 | 38 | 39 | 40
[32 empty] | F7 | 41 | 42 | 43 | 44
[32 empty] | F7 | 45 | 46 | 47 | 48
[32 empty] | F7 | 49 | 50 | 51 | 52
[32 empty] | F7 | 53 | 54 | 55 | 56
BBD131DX05 - Surge Bin Facility - Pump Station
EIO node #5 | DX05 | DIO1 | 132 | 2 | 5 | 0
BBD131 | DX05 | DIO1 | 132 | 2 | 5 | 0 |  | Chassis |  | BMEXBP1200
BBD131 | DX05 | DIO1 | 132 | 2 | 5 | 0 |  | Power |  | BMXCPS4022 |  | total |  | spare |  | % spare
BBD131 | DX05 | DIO1 | 132 | 2 | 5 | 0 | 0 | Comms |  | BMECRA31210 | I/O1 | 112 |  | 61 |  | 54.46%
BBD131 | DX05 | DIO1 | 132 | 2 | 5 | 0 | 1 | 0 | BMXFCW303 | BMXDDI3202K | DI | 4 |  | CB01 |  | 240VAC Circuit Breaker | Closed | Q106 | BBD131DX05 |  | 2.5\0.1:0 | BR4-2150-E-00136 | 0 |  | D | [6 empty] | F1 |  | 1
BBD131 | DX05 | DIO1 | 132 | 2 | 5 | 0 | 1 | 1 |  |  | DI | 4 |  | VDC01 |  | 24VDC DIO1 Output Control Supply | Healthy | Q143 | BBD131DX05 |  | 2.5\0.1:1 | BR4-2150-E-00136 | 0 |  | D | [6 empty] | F1 |  | 2
BBD131 | DX05 | DIO1 | 132 | 2 | 5 | 0 | 1 | 2 |  |  | DI | 4 |  | VDC02 |  | 24VDC GW1 Control Supply | Healthy | Q157 | BBD131DX05 |  | 2.5\0.1:2 | BR4-2150-E-00136 | 0 |  | D | [6 empty] | F1 |  | 3
BBD131 | DX05 | DIO1 | 132 | 2 | 5 | 0 | 1 | 3 |  |  | DI | 4 |  | VDC03 |  | 24VDC Instrument Supply | Healthy | Q164 | BBD131DX05 |  | 2.5\0.1:3 | BR4-2150-E-00136 | 0 |  | D | [6 empty] | F1 |  | 4
BBD131 | DX05 | DIO1 | 132 | 2 | 5 | 0 | 1 | 4 |  |  | DI | 4 |  | VDC04 |  | 24VDC Transmitter Supply | Healthy | Q168 | BBD131DX05 |  | 2.5\0.1:4 | BR4-2150-E-00136 | 0 |  | D | [6 empty] | F1 |  | 5
BBD131 | DX05 | DIO1 | 132 | 2 | 5 | 0 | 1 | 5 |  |  | DI | 4 |  | VDC05 |  | 24VDC BBD131DX05 Control Supply | Healthy | Q172 | BBD131DX05 |  | 2.5\0.1:5 | BR4-2150-E-00136 | 0 |  | D | [6 empty] | F1 |  | 6
BBD131 | DX05 | DIO1 | 132 | 2 | 5 | 0 | 1 | 6 |  |  | DI | 4 |  | VDC06 |  | 24VDC Spare Control Supply | Healthy | Q176 | BBD131DX05 |  | 2.5\0.1:6 | BR4-2150-E-00136 | 0 |  | D | [6 empty] | F1 |  | 7
BBD131 | DX05 | DIO1 | 132 | 2 | 5 | 0 | 1 | 7 |  |  | DI | 4 |  | VDC07 |  | 24VDC Spare Control Supply | Healthy | Q180 | BBD131DX05 |  | 2.5\0.1:7 | BR4-2150-E-00136 | 0 |  | D | [6 empty] | F1 |  | 8
BBD131 | DX05 | DIO1 | 132 | 2 | 5 | 0 | 1 | 8 |  |  | DI | 4 |  | VDC08 |  | 24VDC Spare Control Supply | Healthy | Q184 | BBD131DX05 |  | 2.5\0.1:8 | BR4-2150-E-00136 | 0 |  | D | [6 empty] | F1 |  | 9
BBD131 | DX05 | DIO1 | 132 | 2 | 5 | 0 | 1 | 9 |  |  | DI | 4 |  | VDC09 |  | 24VDC Spare Control Supply | Healthy | Q188 | BBD131DX05 |  | 2.5\0.1:9 | BR4-2150-E-00136 | 0 |  | D | [6 empty] | F1 |  | 10
BBD131 | DX05 | DIO1 | 132 | 2 | 5 | 0 | 1 | 10 |  |  | DI | 4 |  | VDC10 |  | 24VDC Spare Control Supply | Healthy | Q192 | BBD131DX05 |  | 2.5\0.1:10 | BR4-2150-E-00136 | 0 |  | D | [6 empty] | F1 |  | 11
BBD131 | DX05 | DIO1 | 132 | 2 | 5 | 0 | 1 | 11 |  |  | DI | 4 |  | VDC11 |  | 24VDC Spare Control Supply | Healthy | Q196 | BBD131DX05 |  | 2.5\0.1:11 | BR4-2150-E-00136 | 0 |  | D | [6 empty] | F1 |  | 12
BBD131 | DX05 | DIO1 | 132 | 2 | 5 | 0 | 1 | 12 |  |  | DI | 4 | BPP2104THR01 | THR01 |  | BPP2104EM01 Thermistor Relay | Healthy | K190 | BPP2104 |  | 2.5\0.1:12 | BR4-2150-E-00108 | A |  | S | [6 empty] | F1 |  | 13
BBD131 | DX05 | DIO1 | 132 | 2 | 5 | 0 | 1 | 13 |  |  | DI | 4 | BPP2105THR01 | THR01 |  | BPP2105EM01 Thermistor Relay | Healthy | K190 | BPP2105 |  | 2.5\0.1:13 | BR4-2150-E-00109 | A |  | S | [6 empty] | F1 |  | 14
BBD131 | DX05 | DIO1 | 132 | 2 | 5 | 0 | 1 | 14 |  |  | DI | [9 empty] | 2.5\0.1:14 |  |  |  | S | [6 empty] | F1 |  | 15
BBD131 | DX05 | DIO1 | 132 | 2 | 5 | 0 | 1 | 15 |  |  | DI | [9 empty] | 2.5\0.1:15 |  |  |  | S | [6 empty] | F1 |  | 16
BBD131 | DX05 | DIO1 | 132 | 2 | 5 | 0 | 1 | 16 |  |  | DI | 4 | BPP2104LCS01 | STT01 | SURGE BIN FACILITY PROCESS WATER PUMP 3 (DUTY) | Start Pushbutton | Activated |  | BPP2104 |  | 2.5\0.1:16 | BR4-2150-E-00108 | A |  | S | [6 empty] | F1 | 17 | 18
BBD131 | DX05 | DIO1 | 132 | 2 | 5 | 0 | 1 | 17 |  |  | DI | 4 | BPP2104LCS01 | STP01 | SURGE BIN FACILITY PROCESS WATER PUMP 3 (DUTY) | Stop Pushbutton | Activated |  | BPP2104 |  | 2.5\0.1:17 | BR4-2150-E-00108 | A |  | S | [6 empty] | F1 | 19 | 20
BBD131 | DX05 | DIO1 | 132 | 2 | 5 | 0 | 1 | 18 |  |  | DI | 4 | BPP2105LCS01 | STT01 | SURGE BIN FACILITY PROCESS WATER PUMP 4 (STANDBY) | Start Pushbutton | Activated |  | BPP2105 |  | 2.5\0.1:18 | BR4-2150-E-00109 | A |  | S | [6 empty] | F1 | 21 | 22
BBD131 | DX05 | DIO1 | 132 | 2 | 5 | 0 | 1 | 19 |  |  | DI | 4 | BPP2105LCS01 | STP01 | SURGE BIN FACILITY PROCESS WATER PUMP 4 (STANDBY) | Stop Pushbutton | Activated |  | BPP2105 |  | 2.5\0.1:19 | BR4-2150-E-00109 | A |  | S | [6 empty] | F1 | 23 | 24
BBD131 | DX05 | DIO1 | 132 | 2 | 5 | 0 | 1 | 20 |  |  | DI | 8 | BTK2104LS02 | LS02 | SURGE BIN FACILITY RAW/FIRE WATER TANK 1 | Level Switch Low-Low | Healthy |  | BTK2104 |  | 2.5\0.1:20 | BR4-2150-E-00253 | 0 | To be added to drawings | S | [6 empty] | F1 | 25 | 26
BBD131 | DX05 | DIO1 | 132 | 2 | 5 | 0 | 1 | 21 |  |  | DI | 8 | BTK2105LS02 | LS02 | SURGE BIN FACILITY RAW/FIRE WATER TANK 2 | Level Switch Low-Low | Healthy |  | BTK2105 |  | 2.5\0.1:21 | BR4-2150-E-00253 | 0 | To be added to drawings | S | [6 empty] | F1 | 27 | 28
BBD131 | DX05 | DIO1 | 132 | 2 | 5 | 0 | 1 | 22 |  |  | DI | 3 | BTK2104FV01 | SW01 | SURGE BIN FACILITY RAW/FIRE WATER TANK 1 | Remote Mode | Selected |  | BTK2104FV01 |  | 2.5\0.1:22 | BR4-2150-E-00139 | 0 |  | S | [6 empty] | F1 | 29 | 30
BBD131 | DX05 | DIO1 | 132 | 2 | 5 | 0 | 1 | 23 |  |  | DI | 3 | BTK2104FV01 | ZS01 | SURGE BIN FACILITY RAW/FIRE WATER TANK 1 | Valve Open Feedback | Open |  | BTK2104FV01 |  | 2.5\0.1:23 | BR4-2150-E-00139 | 0 |  | S | [6 empty] | F1 | 31 | 32
BBD131 | DX05 | DIO1 | 132 | 2 | 5 | 0 | 1 | 24 |  |  | DI | 3 | BTK2104FV01 | ZS02 | SURGE BIN FACILITY RAW/FIRE WATER TANK 1 | Valve Closed Feedback | Closed |  | BTK2104FV01 |  | 2.5\0.1:24 | BR4-2150-E-00139 | 0 |  | S | [6 empty] | F1 | 33 | 34
BBD131 | DX05 | DIO1 | 132 | 2 | 5 | 0 | 1 | 25 |  |  | DI | 3 | BTK2104FV01 | XS01 | SURGE BIN FACILITY RAW/FIRE WATER TANK 1 | Valve Fault | Fault |  | BTK2104FV01 |  | 2.5\0.1:25 | BR4-2150-E-00139 | 0 |  | S | [6 empty] | F1 | 35 | 36
BBD131 | DX05 | DIO1 | 132 | 2 | 5 | 0 | 1 | 26 |  |  | DI | 4 | BTK2104FV01 | CB01 | SURGE BIN FACILITY RAW/FIRE WATER TANK 1 | BTK2104FV01 240VAC Circuit Breaker | Closed | Q407 | BTK2104FV01 |  | 2.5\0.1:26 | BR4-2150-E-00139 | 0 |  | S | [6 empty] | F1 | 37 | 38
BBD131 | DX05 | DIO1 | 132 | 2 | 5 | 0 | 1 | 27 |  |  | DI | [9 empty] | 2.5\0.1:27 |  |  |  | S | [6 empty] | F1 | 39 | 40
BBD131 | DX05 | DIO1 | 132 | 2 | 5 | 0 | 1 | 28 |  |  | DI | 4 | BPP2104FS01 | FS01 | SURGE BIN FACILITY PROCESS WATER PUMP 3 (DUTY) | Flow Switch |  |  | BPP2104 |  | 2.5\0.1:28 | BR4-2150-E-00137 | 0 |  | S | [6 empty] | F1 | 41 | 42
BBD131 | DX05 | DIO1 | 132 | 2 | 5 | 0 | 1 | 29 |  |  | DI | 4 | BPP2105FS02 | FS02 | SURGE BIN FACILITY PROCESS WATER PUMP 4 (STANDBY) | Flow Switch |  |  | BPP2105 |  | 2.5\0.1:29 | BR4-2150-E-00137 | 0 |  | S | [6 empty] | F1 | 43 | 44
BBD131 | DX05 | DIO1 | 132 | 2 | 5 | 0 | 1 | 30 |  |  | DI | [9 empty] | 2.5\0.1:30 |  |  |  | S | [6 empty] | F1 | 45 | 46
BBD131 | DX05 | DIO1 | 132 | 2 | 5 | 0 | 1 | 31 |  |  | DI | [9 empty] | 2.5\0.1:31 |  |  |  | S | [6 empty] | F1 | 47 | 48
BBD131 | DX05 | DIO1 | 132 | 2 | 5 | 0 | 2 | 0 | BMXFCW303 | BMXDDI3202K | DI | 3 | BTK2104FIT01 | FQ01 | SURGE BIN FACILITY RAW/FIRE WATER TANK 1 | Flow Totaliser Pulse | Active |  | BTK2104 |  | 2.5\0.2:0 | BR4-2150-E-00138 | 0 |  | S | [6 empty] | F2 | 1 | 2
BBD131 | DX05 | DIO1 | 132 | 2 | 5 | 0 | 2 | 1 |  |  | DI | 3 | BTK2105FIT01 | FQ01 | SURGE BIN FACILITY RAW/FIRE WATER TANK 2 | Flow Totaliser Pulse | Active |  | BTK2105 |  | 2.5\0.2:1 | BR4-2150-E-00138 | 0 |  | S | [6 empty] | F2 | 3 | 4
BBD131 | DX05 | DIO1 | 132 | 2 | 5 | 0 | 2 | 2 |  |  | DI | 5 | BPP2104FIT05 | FQ05 | SURGE BIN FACILITY PROCESS WATER | Flow Totaliser Pulse | Active |  | BPP2104 |  | 2.5\0.2:2 | BR4-2150-E-00138 | 0 |  | S | [6 empty] | F2 | 5 | 6
BBD131 | DX05 | DIO1 | 132 | 2 | 5 | 0 | 2 | 3 |  |  | DI | 5 | BPP2104FIT06 | FQ06 | SURGE BIN FACILITY PROCESS WATER RECYCLE | Flow Totaliser Pulse | Active |  | BPP2104 |  | 2.5\0.2:3 | BR4-2150-E-00138 | 0 |  | S | [6 empty] | F2 | 7 | 8
BBD131 | DX05 | DIO1 | 132 | 2 | 5 | 0 | 2 | 4 |  |  | DI | 5 | [8 empty] | 2.5\0.2:4 |  |  | Instrument removed in rev 0 of BR4-2150-E-00140. Therefore, removed from IO list. | S | [6 empty] | F2 | 9 | 10
BBD131 | DX05 | DIO1 | 132 | 2 | 5 | 0 | 2 | 5 |  |  | DI | 5 | BBD131FIT03 | FQ03 | SURPLUS WATER BROCKMAN 4 BOOLGEEDA | Flow Totaliser Pulse | Active |  | BBD131 |  | 2.5\0.2:5 | BR4-2150-E-00140 | 0 |  | S | [6 empty] | F2 | 11 | 12
BBD131 | DX05 | DIO1 | 132 | 2 | 5 | 0 | 2 | 6 |  |  | DI | 8 | BTK2104FIP01 | XS01 | FIRE WATER PUMP SKID | Fire Panel Fault | Healthy |  | BTK2104FIP01 |  | 2.5\0.2:6 |  |  | JIMMY Removed 6/8/2026. Hardwired signals no longer required. Will be sent to ESO and read by SCADA via modbus comms | S | [6 empty] | F2 | 13 | 14
BBD131 | DX05 | DIO1 | 132 | 2 | 5 | 0 | 2 | 7 |  |  | DI | 8 | BTK2104FIP01 | IS01 | FIRE WATER PUMP SKID | Fire Panel Isolated | Healthy |  | BTK2104FIP01 |  | 2.5\0.2:7 |  |  | JIMMY Removed 6/8/2026. Hardwired signals no longer required. Will be sent to ESO and read by SCADA via modbus comms | S | [6 empty] | F2 | 15 | 16
BBD131 | DX05 | DIO1 | 132 | 2 | 5 | 0 | 2 | 8 |  |  | DI | 8 | BTK2104FIP01 | XS02 | FIRE WATER PUMP SKID | Fire Alarm | Healthy |  | BTK2104FIP01 |  | 2.5\0.2:8 |  |  | JIMMY Removed 6/8/2026. Hardwired signals no longer required. Will be sent to ESO and read by SCADA via modbus comms | S | [6 empty] | F2 | 17 | 18
BBD131 | DX05 | DIO1 | 132 | 2 | 5 | 0 | 2 | 9 |  |  | DI | 5 | [8 empty] | 2.5\0.2:9 |  |  |  | S | [6 empty] | F2 | 19 | 20
BBD131 | DX05 | DIO1 | 132 | 2 | 5 | 0 | 2 | 10 |  |  | DI | 5 | [8 empty] | 2.5\0.2:10 |  |  | Instrument removed in rev 0 of BR4-2150-E-00140. Therefore, removed from IO list. | S | [6 empty] | F2 | 21 | 22
BBD131 | DX05 | DIO1 | 132 | 2 | 5 | 0 | 2 | 11 |  |  | DI | 5 | [8 empty] | 2.5\0.2:11 |  |  | Instrument removed in rev 0 of BR4-2150-E-00140. Therefore, removed from IO list. | S | [6 empty] | F2 | 23 | 24
BBD131 | DX05 | DIO1 | 132 | 2 | 5 | 0 | 2 | 12 |  |  | DI | 5 | [8 empty] | 2.5\0.2:12 |  |  | Instrument removed in rev 0 of BR4-2150-E-00140. Therefore, removed from IO list. | S | [6 empty] | F2 | 25 | 26
BBD131 | DX05 | DIO1 | 132 | 2 | 5 | 0 | 2 | 13 |  |  | DI | 5 | [8 empty] | 2.5\0.2:13 |  |  | Instrument removed in rev 0 of BR4-2150-E-00140. Therefore, removed from IO list. | S | [6 empty] | F2 | 27 | 28
BBD131 | DX05 | DIO1 | 132 | 2 | 5 | 0 | 2 | 14 |  |  | DI | 5 | [8 empty] | 2.5\0.2:14 |  |  | Instrument removed in rev 0 of BR4-2150-E-00140. Therefore, removed from IO list. | S | [6 empty] | F2 | 29 | 30
BBD131 | DX05 | DIO1 | 132 | 2 | 5 | 0 | 2 | 15 |  |  | DI | 5 | [8 empty] | 2.5\0.2:15 |  |  | Instrument removed in rev 0 of BR4-2150-E-00140. Therefore, removed from IO list. | S | [6 empty] | F2 | 31 | 32
BBD131 | DX05 | DIO1 | 132 | 2 | 5 | 0 | 2 | 16 |  |  | DI | 3 | BTK2105FV01 | SW01 | SURGE BIN FACILITY RAW/FIRE WATER TANK 2 | Remote Mode | Selected |  | BTK2105FV01 |  | 2.5\0.2:16 | BR4-2150-E-00139 | 0 |  | S | [6 empty] | F3 | 1 | 2
BBD131 | DX05 | DIO1 | 132 | 2 | 5 | 0 | 2 | 17 |  |  | DI | 3 | BTK2105FV01 | ZS01 | SURGE BIN FACILITY RAW/FIRE WATER TANK 2 | Valve Open Feedback | Open |  | BTK2105FV01 |  | 2.5\0.2:17 | BR4-2150-E-00139 | 0 |  | S | [6 empty] | F3 | 3 | 4
BBD131 | DX05 | DIO1 | 132 | 2 | 5 | 0 | 2 | 18 |  |  | DI | 3 | BTK2105FV01 | ZS02 | SURGE BIN FACILITY RAW/FIRE WATER TANK 2 | Valve Closed Feedback | Closed |  | BTK2105FV01 |  | 2.5\0.2:18 | BR4-2150-E-00139 | 0 |  | S | [6 empty] | F3 | 5 | 6
BBD131 | DX05 | DIO1 | 132 | 2 | 5 | 0 | 2 | 19 |  |  | DI | 3 | BTK2105FV01 | XS01 | SURGE BIN FACILITY RAW/FIRE WATER TANK 2 | Valve Fault | Fault |  | BTK2105FV01 |  | 2.5\0.2:19 | BR4-2150-E-00139 | 0 |  | S | [6 empty] | F3 | 7 | 8
BBD131 | DX05 | DIO1 | 132 | 2 | 5 | 0 | 2 | 20 |  |  | DI | 4 | BTK2105FV01 | CB01 | SURGE BIN FACILITY RAW/FIRE WATER TANK 2 | BTK2105FV01 240VAC Circuit Breaker | Closed | Q429 | BTK2105FV01 |  | 2.5\0.2:20 | BR4-2150-E-00139 | 0 |  | S | [6 empty] | F3 | 9 | 10
BBD131 | DX05 | DIO1 | 132 | 2 | 5 | 0 | 2 | 21 |  |  | DI | 3 | BPP2104FV01 | SW01 | SURGE BIN FACILITY PROCESS WATER RECYCLE | Remote Mode | Selected |  | BPP2104FV01 |  | 2.5\0.2:21 | BR4-2150-E-00139 | 0 |  | S | [6 empty] | F3 | 11 | 12
BBD131 | DX05 | DIO1 | 132 | 2 | 5 | 0 | 2 | 22 |  |  | DI | 3 | BPP2104FV01 | ZS01 | SURGE BIN FACILITY PROCESS WATER RECYCLE | Valve Open Feedback | Open |  | BPP2104FV01 |  | 2.5\0.2:22 | BR4-2150-E-00139 | 0 |  | S | [6 empty] | F3 | 13 | 14
BBD131 | DX05 | DIO1 | 132 | 2 | 5 | 0 | 2 | 23 |  |  | DI | 3 | BPP2104FV01 | ZS02 | SURGE BIN FACILITY PROCESS WATER RECYCLE | Valve Closed Feedback | Closed |  | BPP2104FV01 |  | 2.5\0.2:23 | BR4-2150-E-00139 | 0 |  | S | [6 empty] | F3 | 15 | 16
BBD131 | DX05 | DIO1 | 132 | 2 | 5 | 0 | 2 | 24 |  |  | DI | 3 | BPP2104FV01 | XS01 | SURGE BIN FACILITY PROCESS WATER RECYCLE | Valve Fault | Fault |  | BPP2104FV01 |  | 2.5\0.2:24 | BR4-2150-E-00139 | 0 |  | S | [6 empty] | F3 | 17 | 18
BBD131 | DX05 | DIO1 | 132 | 2 | 5 | 0 | 2 | 25 |  |  | DI | 4 | BPP2104FV01 | CB01 | SURGE BIN FACILITY PROCESS WATER RECYCLE | BPP2104FV01 240VAC Circuit Breaker | Closed | Q457 | BPP2104FV01 |  | 2.5\0.2:25 | BR4-2150-E-00139 | 0 |  | S | [6 empty] | F3 | 19 | 20
BBD131 | DX05 | DIO1 | 132 | 2 | 5 | 0 | 2 | 26 |  |  | DI | [9 empty] | 2.5\0.2:26 |  |  |  | S | [6 empty] | F3 | 21 | 22
BBD131 | DX05 | DIO1 | 132 | 2 | 5 | 0 | 2 | 27 |  |  | DI | [9 empty] | 2.5\0.2:27 |  |  |  | S | [6 empty] | F3 | 23 | 24
BBD131 | DX05 | DIO1 | 132 | 2 | 5 | 0 | 2 | 28 |  |  | DI | [9 empty] | 2.5\0.2:28 |  |  |  | S | [6 empty] | F3 | 25 | 26
BBD131 | DX05 | DIO1 | 132 | 2 | 5 | 0 | 2 | 29 |  |  | DI | [9 empty] | 2.5\0.2:29 |  |  |  | S | [6 empty] | F3 | 27 | 28
BBD131 | DX05 | DIO1 | 132 | 2 | 5 | 0 | 2 | 30 |  |  | DI | [9 empty] | 2.5\0.2:30 |  |  |  | S | [6 empty] | F3 | 29 | 30
BBD131 | DX05 | DIO1 | 132 | 2 | 5 | 0 | 2 | 31 |  |  | DI | [9 empty] | 2.5\0.2:31 |  |  |  | S | [6 empty] | F3 | 31 | 32
BBD131 | DX05 | DIO1 | 132 | 2 | 5 | 0 | 3 | 0 | BMXFTB2010 | BMXDDO1602 | DO | 5 | BBD131DB04 | SR01 | DB04 Lighting Relay | BBD131DB04 Lighting Relay |  |  | BBD131DB04 |  | 2.5\0.3:0 | BR4-2150-E-00254 | 0 |  | S | [6 empty] | F4 | 1 | 2
BBD131 | DX05 | DIO1 | 132 | 2 | 5 | 0 | 3 | 1 |  |  | DO | [9 empty] | 2.5\0.3:1 |  |  |  | S | [6 empty] | F4 | 3 | 4
BBD131 | DX05 | DIO1 | 132 | 2 | 5 | 0 | 3 | 2 |  |  | DO | [9 empty] | 2.5\0.3:2 |  |  |  | S | [6 empty] | F4 | 5 | 6
BBD131 | DX05 | DIO1 | 132 | 2 | 5 | 0 | 3 | 3 |  |  | DO | [9 empty] | 2.5\0.3:3 |  |  |  | S | [6 empty] | F4 | 7 | 8
BBD131 | DX05 | DIO1 | 132 | 2 | 5 | 0 | 3 | 4 |  |  | DO | [9 empty] | 2.5\0.3:4 |  |  |  | S | [6 empty] | F4 | 9 | 10
BBD131 | DX05 | DIO1 | 132 | 2 | 5 | 0 | 3 | 5 |  |  | DO | [9 empty] | 2.5\0.3:5 |  |  |  | S | [6 empty] | F4 | 11 | 12
BBD131 | DX05 | DIO1 | 132 | 2 | 5 | 0 | 3 | 6 |  |  | DO | [9 empty] | 2.5\0.3:6 |  |  |  | S | [6 empty] | F4 | 13 | 14
BBD131 | DX05 | DIO1 | 132 | 2 | 5 | 0 | 3 | 7 |  |  | DO | [9 empty] | 2.5\0.3:7 |  |  |  | S | [6 empty] | F4 | 15 | 16
BBD131 | DX05 | DIO1 | 132 | 2 | 5 | 0 | 3 | 8 |  |  | DO | [9 empty] | 2.5\0.3:8 |  |  |  | S | [6 empty] | F4 | 17 | 18
BBD131 | DX05 | DIO1 | 132 | 2 | 5 | 0 | 3 | 9 |  |  | DO | [9 empty] | 2.5\0.3:9 |  |  |  | S | [6 empty] | F4 | 19 | 20
BBD131 | DX05 | DIO1 | 132 | 2 | 5 | 0 | 3 | 10 |  |  | DO | [9 empty] | 2.5\0.3:10 |  |  |  | S | [6 empty] | F4 | 21 | 22
BBD131 | DX05 | DIO1 | 132 | 2 | 5 | 0 | 3 | 11 |  |  | DO | [9 empty] | 2.5\0.3:11 |  |  |  | S | [6 empty] | F4 | 23 | 24
BBD131 | DX05 | DIO1 | 132 | 2 | 5 | 0 | 3 | 12 |  |  | DO | [9 empty] | 2.5\0.3:12 |  |  |  | S | [6 empty] | F4 | 25 | 26
BBD131 | DX05 | DIO1 | 132 | 2 | 5 | 0 | 3 | 13 |  |  | DO | [9 empty] | 2.5\0.3:13 |  |  |  | S | [6 empty] | F4 | 27 | 28
BBD131 | DX05 | DIO1 | 132 | 2 | 5 | 0 | 3 | 14 |  |  | DO | [9 empty] | 2.5\0.3:14 |  |  |  | S | [6 empty] | F4 | 29 | 30
BBD131 | DX05 | DIO1 | 132 | 2 | 5 | 0 | 3 | 15 |  |  | DO | [9 empty] | 2.5\0.3:15 |  |  |  | S | [6 empty] | F4 | 31 | 32
BBD131 | DX05 | DIO1 | 132 | 2 | 5 | 0 | 4 | 0 | BMXFTW301S | BMEAHI0812 | AI | 4 | BTK2104FT01 | FT01 | SURGE BIN FACILITY RAW/FIRE WATER TANK 1 | Flow Rate |  | L/s | BTK2104 | REAL | 2.5\0.4:0 | BR4-2150-E-00138 | 0 |  | S |  | 0 | 150 | 0 | 150 | #.# EU | F5 | 33 | 34
BBD131 | DX05 | DIO1 | 132 | 2 | 5 | 0 | 4 | 1 |  |  | AI | 4 | BTK2104LT01 | LT01 | SURGE BIN FACILITY RAW/FIRE WATER TANK 1 | Tank Level |  | % | BTK2104 | REAL | 2.5\0.4:1 | BR4-2150-E-00137 | 0 |  | S |  | 0 | 100 | 0 | 100 | #.# EU | F5 | 35 | 36
BBD131 | DX05 | DIO1 | 132 | 2 | 5 | 0 | 4 | 2 |  |  | AI | 4 | BTK2105FT01 | FT01 | SURGE BIN FACILITY RAW/FIRE WATER TANK 2 | Flow Rate |  | L/s | BTK2105 | REAL | 2.5\0.4:2 | BR4-2150-E-00138 | 0 |  | S |  | 0 | 150 | 0 | 150 | #.# EU | F5 | 37 | 38
BBD131 | DX05 | DIO1 | 132 | 2 | 5 | 0 | 4 | 3 |  |  | AI | 4 | BTK2105LT01 | LT01 | SURGE BIN FACILITY RAW/FIRE WATER TANK 2 | Tank Level |  | % | BTK2105 | REAL | 2.5\0.4:3 | BR4-2150-E-00137 | 0 |  | S |  | 0 | 100 | 0 | 100 | #.# EU | F5 | 39 | 40
BBD131 | DX05 | DIO1 | 132 | 2 | 5 | 0 | 4 | 4 |  |  | AI | 3 | BTK2104FV01 | ZT01 | SURGE BIN FACILITY RAW/FIRE WATER TANK 1 | Valve Position Feedback |  | % | BTK2104FV01 | REAL | 2.5\0.4:4 | BR4-2150-E-00139 | 0 |  | S |  | 0 | 100 | 0 | 100 | #.# EU | F5 | 41 | 42
BBD131 | DX05 | DIO1 | 132 | 2 | 5 | 0 | 4 | 5 |  |  | AI | 3 | BTK2105FV01 | ZT01 | SURGE BIN FACILITY RAW/FIRE WATER TANK 2 | Valve Position Feedback |  | % | BTK2105FV01 | REAL | 2.5\0.4:5 | BR4-2150-E-00139 | 0 |  | S |  | 0 | 100 | 0 | 100 | #.# EU | F5 | 43 | 44
BBD131 | DX05 | DIO1 | 132 | 2 | 5 | 0 | 4 | 6 |  |  | AI | 3 | BPP2104FV01 | ZT01 | SURGE BIN FACILITY PROCESS WATER RECYCLE | Valve Position Feedback |  | % | BPP2104FV01 | REAL | 2.5\0.4:6 | BR4-2150-E-00139 | 0 |  | S |  | 0 | 100 | 0 | 100 | #.# EU | F5 | 45 | 46
BBD131 | DX05 | DIO1 | 132 | 2 | 5 | 0 | 4 | 7 |  |  | AI | 5 | [8 empty] | 2.5\0.4:7 |  |  |  | S | [6 empty] | F5 | 47 | 48
BBD131 | DX05 | DIO1 | 132 | 2 | 5 | 0 | 5 | 0 | BMXFTW301S | BMEAHI0812 | AI | 4 | BPP2104PT01 | PT01 | SURGE BIN FACILITY PROCESS WATER PUMP 3 (DUTY) | Discharge Pressure |  | kPag | BPP2104 | REAL | 2.5\0.5:0 | BR4-2150-E-00137 | 0 |  | S |  | 0 | 1200 | 0 | 1200 | #.# EU | F4 | 33 | 34
BBD131 | DX05 | DIO1 | 132 | 2 | 5 | 0 | 5 | 1 |  |  | AI | 4 | BPP2105PT02 | PT02 | SURGE BIN FACILITY PROCESS WATER PUMP 4 | Discharge Pressure |  | kPag | BPP2105 | REAL | 2.5\0.5:1 | BR4-2150-E-00137 | 0 |  | S |  | 0 | 1200 | 0 | 1200 | #.# EU | F4 | 35 | 36
BBD131 | DX05 | DIO1 | 132 | 2 | 5 | 0 | 5 | 2 |  |  | AI | 4 | BPP2104FIT06 | FT06 | SURGE BIN FACILITY PROCESS WATER RECYCLE | Flow Rate |  | m3/h | BPP2104 | REAL | 2.5\0.5:2 | BR4-2150-E-00138 | 0 |  | S |  | 0 | 50 | 0 | 50 | #.# EU | F4 | 37 | 38
BBD131 | DX05 | DIO1 | 132 | 2 | 5 | 0 | 5 | 3 |  |  | AI | 4 | BPP2104FIT05 | FT05 | SURGE BIN FACILITY PROCESS WATER | Flow Rate |  | m3/h | BPP2104 | REAL | 2.5\0.5:3 | BR4-2150-E-00138 | 0 |  | S |  | 0 | 100 | 0 | 100 | #.# EU | F4 | 39 | 40
BBD131 | DX05 | DIO1 | 132 | 2 | 5 | 0 | 5 | 4 |  |  | AI | 4 | BPP2104PIT03 | PT03 | SURGE BIN FACILITY PROCESS WATER PUMP 3 (DUTY) | Discharge Pressure |  | kPag | BPP2104 | REAL | 2.5\0.5:4 | BR4-2150-E-00137 | 0 |  | S |  | 0 | 1200 | 0 | 1200 | #.# EU | F4 | 41 | 42
BBD131 | DX05 | DIO1 | 132 | 2 | 5 | 0 | 5 | 5 |  |  | AI | 4 | BPP2104PIT04 | PT04 | SURGE BIN FACILITY PROCESS WATER PUMP 4 (STANDBY) | Discharge Pressure |  | kPag | BPP2104 | REAL | 2.5\0.5:5 | BR4-2150-E-00137 | 0 |  | S |  | 0 | 1200 | 0 | 1200 | #.# EU | F4 | 43 | 44
BBD131 | DX05 | DIO1 | 132 | 2 | 5 | 0 | 5 | 6 |  |  | AI | 5 | [8 empty] | 2.5\0.5:6 |  |  |  | S | [6 empty] | F4 | 45 | 46
BBD131 | DX05 | DIO1 | 132 | 2 | 5 | 0 | 5 | 7 |  |  | AI | 4 | BBD131FIT03 | FT03 | SURPLUS WATER BROCKMAN 4 BOOLGEEDA | Flow Rate |  | m3/h | BBD131 | REAL | 2.5\0.5:7 | BR4-2150-E-00140 | 0 |  | S |  | 0 | 2000 | 0 | 2000 |  | F4 | 47 | 48
BBD131 | DX05 | DIO1 | 132 | 2 | 5 | 0 | 6 | 0 | BMXFTW301S | BMEAHI0812 | AI | 5 | [8 empty] | 2.5\0.6:0 |  |  |  | S | [5 empty] | #.# EU | F6 | 1 | 2
BBD131 | DX05 | DIO1 | 132 | 2 | 5 | 0 | 6 | 1 |  |  | AI | [9 empty] | 2.5\0.6:1 |  |  |  | S | [6 empty] | F6 | 3 | 4
BBD131 | DX05 | DIO1 | 132 | 2 | 5 | 0 | 6 | 2 |  |  | AI | [9 empty] | 2.5\0.6:2 |  |  |  | S | [6 empty] | F6 | 5 | 6
BBD131 | DX05 | DIO1 | 132 | 2 | 5 | 0 | 6 | 3 |  |  | AI | [9 empty] | 2.5\0.6:3 |  |  |  | S | [6 empty] | F6 | 7 | 8
BBD131 | DX05 | DIO1 | 132 | 2 | 5 | 0 | 6 | 4 |  |  | AI | [9 empty] | 2.5\0.6:4 |  |  |  | S |  | 0 | 100 | 0 | 100 | #.# EU | F6 | 9 | 10
BBD131 | DX05 | DIO1 | 132 | 2 | 5 | 0 | 6 | 5 |  |  | AI | [9 empty] | 2.5\0.6:5 |  |  |  | S | [6 empty] | F6 | 11 | 12
BBD131 | DX05 | DIO1 | 132 | 2 | 5 | 0 | 6 | 6 |  |  | AI | [9 empty] | 2.5\0.6:6 |  |  |  | S | [6 empty] | F6 | 13 | 14
BBD131 | DX05 | DIO1 | 132 | 2 | 5 | 0 | 6 | 7 |  |  | AI | [9 empty] | 2.5\0.6:7 |  |  |  | S | [6 empty] | F6 | 15 | 16
BBD131 | DX05 | DIO1 | 132 | 2 | 5 | 0 | 7 | 0 | BMXFTW301S | BMEAHO0412 | AO | 3 | BTK2104FV01 | ZC01 | SURGE BIN FACILITY RAW/FIRE WATER TANK 1 | Flow Control Valve Position Setpoint |  | % | BTK2104FV01 | REAL | 2.5\0.7:0 | BR4-2150-E-00139 | 0 |  | S |  | 0 | 110 | 0 | 110 | # EU | F3 | 33 | 34
BBD131 | DX05 | DIO1 | 132 | 2 | 5 | 0 | 7 | 1 |  |  | AO | 3 | BTK2105FV01 | ZC01 | SURGE BIN FACILITY RAW/FIRE WATER TANK 2 | Flow Control Valve Position Setpoint |  |  | BTK2105FV01 | REAL | 2.5\0.7:1 | BR4-2150-E-00139 | 0 |  | S | [6 empty] | F3 | 35 | 36
BBD131 | DX05 | DIO1 | 132 | 2 | 5 | 0 | 7 | 2 |  |  | AO | 3 | BPP2104FV01 | ZC01 | SURGE BIN FACILITY PROCESS WATER RECYCLE | Flow Control Valve Position Setpoint |  |  | BPP2104FV01 | REAL | 2.5\0.7:2 | BR4-2150-E-00139 | 0 |  | S | [6 empty] | F3 | 43 | 44
BBD131 | DX05 | DIO1 | 132 | 2 | 5 | 0 | 7 | 3 |  |  | AO | 5 | [7 empty] | REAL | 2.5\0.7:3 | BR4-2150-E-00140 |  |  | S | [6 empty] | F3 | 49 | 50
BBD131 | DX05 | DIO1 | 132 | 2 | 5 | 0 | 8 |  |  | BMXXEM010 | [10 empty] | 2.5\0.8:
BBD131 | DX05 | DIO1 | 132 | 2 | 5 | 0 | 8 | [13 empty] | 2.5\0.8:
BBD131 | DX05 | DIO1 | 132 | 2 | 5 | 0 | 8 | [13 empty] | 2.5\0.8:
BBD131 | DX05 | DIO1 | 132 | 2 | 5 | 0 | 8 | [13 empty] | 2.5\0.8:
BBD131 | DX05 | DIO1 | 132 | 2 | 5 | 0 | 9 | 0 | BMXFTW301S | BMEAHO0412 | AO | 5 | [7 empty] | REAL | 2.5\0.9:0 |  |  |  | S |  | 0 | 110 | 0 | 110 | # EU | F6 | 21 | 22
BBD131 | DX05 | DIO1 | 132 | 2 | 5 | 0 | 9 | 1 |  |  | AO | [8 empty] | REAL | 2.5\0.9:1 |  |  |  | S | [6 empty] | F6 | 27 | 28
BBD131 | DX05 | DIO1 | 132 | 2 | 5 | 0 | 9 | 2 |  |  | AO | [8 empty] | REAL | 2.5\0.9:2 |  |  |  | S | [6 empty] | F6 | 31 | 32
BBD131 | DX05 | DIO1 | 132 | 2 | 5 | 0 | 9 | 3 |  |  | AO | [8 empty] | REAL | 2.5\0.9:3 |  |  |  | S | [6 empty] | F6 | 37 | 38
BBD131 | DX05 | DIO1 | 132 | 2 | 5 | 0 | 10 |  |  | BMXXEM010 | [10 empty] | 2.5\0.10:
BBD131 | DX05 | DIO1 | 132 | 2 | 5 | 0 | 10 | [13 empty] | 2.5\0.10:
BBD131 | DX05 | DIO1 | 132 | 2 | 5 | 0 | 10 | [13 empty] | 2.5\0.10:
BBD131 | DX05 | DIO1 | 132 | 2 | 5 | 0 | 10 | [13 empty] | 2.5\0.10:
BBD131 | DX05 | DIO1 | 132 | 2 | 5 | 0 | 11 |  |  | BMXXEM010 | [10 empty] | 2.5\0.11:
BBD131 | DX05 | DIO1 | 132 | 2 | 5 | 0 | 11 | [13 empty] | 2.5\0.11:
BBD131 | DX05 | DIO1 | 132 | 2 | 5 | 0 | 11 | [13 empty] | 2.5\0.11:
BBD131 | DX05 | DIO1 | 132 | 2 | 5 | 0 | 11 | [13 empty] | 2.5\0.11:
BBD131 | DX05 |  | 132 | [8 empty] | 5 | BPP2104LCS01 | LOS01 |  | BPP2104 Field LOS To Swrm DX |  | Sub Link | BPP2104 |  |  | BR4-2150-E-00108 | [9 empty] | F7 | 1 | 2 | 3 | 4
BBD131 | DX05 |  | 132 | [8 empty] | 5 | BPP2105LCS01 | LOS01 |  | BPP2105 Field LOS To Swrm DX |  | Sub Link | BPP2105 |  |  | BR4-2150-E-00109 | [9 empty] | F7 | 5 | 6 | 7 | 8
[32 empty] | F7 | 9 | 10 | 11 | 12
[32 empty] | F7 | 13 | 14 | 15 | 16
[32 empty] | F7 | 17 | 18 | 19 | 20
[32 empty] | F7 | 21 | 22 | 23 | 24
[32 empty] | F7 | 25 | 26 | 27 | 28
[32 empty] | F7 | 29 | 30 | 31 | 32
[32 empty] | F7 | 33 | 34 | 35 | 36
[32 empty] | F7 | 37 | 38 | 39 | 40
[32 empty] | F7 | 41 | 42 | 43 | 44
[32 empty] | F7 | 45 | 46 | 47 | 48
BCV131DX06 - BCV131 - Head End Drive Station A&B
EIO node #6 | DX06 | DIO1 | 132 | 2 | 6 | 0
BCV131 | DX06 | DIO1 | 132 | 2 | 6 | 0 |  | Chassis |  | BMEXBP1200
BCV131 | DX06 | DIO1 | 132 | 2 | 6 | 0 |  | Power |  | BMXCPS4022 |  | total |  | spare |  | % spare | [7 empty] | there's enough room for 40 terminals including earthss
BCV131 | DX06 | DIO1 | 132 | 2 | 6 | 0 | 0 | Comms |  | BMECRA31210 | I/O1 | 128 |  | 72 |  | 56.25% | [7 empty] | mm
BCV131 | DX06 | DIO1 | 132 | 2 | 6 | 0 | 1 | 0 | BMXFCW303 | BMXDDI3202K | DI | 4 |  | CB01 |  | 240VAC Circuit - Spare | Closed | Q106 | BCV131DX06 |  | 2.6\0.1:0 | BR4-2150-E-00141 | 0 |  | D | [6 empty] | F1 |  | 1
BCV131 | DX06 | DIO1 | 132 | 2 | 6 | 0 | 1 | 1 |  |  | DI | 4 |  | VDC01 |  | 24VDC DIO1 Output Control Supply | Healthy | Q143 | BCV131DX06 |  | 2.6\0.1:1 | BR4-2150-E-00141 | 0 |  | D | [6 empty] | F1 |  | 2
BCV131 | DX06 | DIO1 | 132 | 2 | 6 | 0 | 1 | 2 |  |  | DI | 4 |  | VDC02 |  | 24VDC GW1 Control Supply | Healthy | Q157 | BCV131DX06 |  | 2.6\0.1:2 | BR4-2150-E-00141 | 0 |  | D | [6 empty] | F1 |  | 3
BCV131 | DX06 | DIO1 | 132 | 2 | 6 | 0 | 1 | 3 |  |  | DI | 4 |  | VDC03 |  | 24VDC Instrument Supply | Healthy | Q164 | BCV131DX06 |  | 2.6\0.1:3 | BR4-2150-E-00141 | 0 |  | D | [6 empty] | F1 |  | 4
BCV131 | DX06 | DIO1 | 132 | 2 | 6 | 0 | 1 | 4 |  |  | DI | 4 |  | VDC04 |  | 24VDC Transmitter Supply | Healthy | Q168 | BCV131DX06 |  | 2.6\0.1:4 | BR4-2150-E-00141 | 0 |  | D | [6 empty] | F1 |  | 5
BCV131 | DX06 | DIO1 | 132 | 2 | 6 | 0 | 1 | 5 |  |  | DI | 4 |  | VDC05 |  | 24VDC BCV131DX06 Control Supply | Healthy | Q172 | BCV131DX06 |  | 2.6\0.1:5 | BR4-2150-E-00141 | 0 |  | D | [6 empty] | F1 |  | 6
BCV131 | DX06 | DIO1 | 132 | 2 | 6 | 0 | 1 | 6 |  |  | DI | 4 |  | VDC06 |  | 24VDC BCV131 Control Supply | Healthy | Q176 | BCV131DX06 |  | 2.6\0.1:6 | BR4-2150-E-00141 | 0 |  | D | [6 empty] | F1 |  | 7
BCV131 | DX06 | DIO1 | 132 | 2 | 6 | 0 | 1 | 7 |  |  | DI | 4 |  | VDC07 |  | 24VDC Spare Control Supply | Healthy | Q180 | BCV131DX06 |  | 2.6\0.1:7 | BR4-2150-E-00141 | 0 |  | D | [6 empty] | F1 |  | 8
BCV131 | DX06 | DIO1 | 132 | 2 | 6 | 0 | 1 | 8 |  |  | DI | 4 |  | VDC08 |  | 24VDC Spare Control Supply | Healthy | Q184 | BCV131DX06 |  | 2.6\0.1:8 | BR4-2150-E-00141 | 0 |  | D | [6 empty] | F1 |  | 9
BCV131 | DX06 | DIO1 | 132 | 2 | 6 | 0 | 1 | 9 |  |  | DI | 4 |  | VDC09 |  | 24VDC Spare Control Supply | Healthy | Q188 | BCV131DX06 |  | 2.6\0.1:9 | BR4-2150-E-00141 | 0 |  | D | [6 empty] | F1 |  | 10
BCV131 | DX06 | DIO1 | 132 | 2 | 6 | 0 | 1 | 10 |  |  | DI | 4 |  | VDC10 |  | 24VDC Spare Control Supply | Healthy | Q192 | BCV131DX06 |  | 2.6\0.1:10 | BR4-2150-E-00141 | 0 |  | D | [6 empty] | F1 |  | 11
BCV131 | DX06 | DIO1 | 132 | 2 | 6 | 0 | 1 | 11 |  |  | DI | 4 |  | VDC11 |  | 24VDC Spare Control Supply | Healthy | Q196 | BCV131DX06 |  | 2.6\0.1:11 | BR4-2150-E-00141 | 0 |  | D | [6 empty] | F1 |  | 12
BCV131 | DX06 | DIO1 | 132 | 2 | 6 | 0 | 1 | 12 |  |  | DI | [9 empty] | 2.6\0.1:12 |  |  |  | S | [6 empty] | F1 |  | 13
BCV131 | DX06 | DIO1 | 132 | 2 | 6 | 0 | 1 | 13 |  |  | DI | [9 empty] | 2.6\0.1:13 |  |  |  | S | [6 empty] | F1 |  | 14
BCV131 | DX06 | DIO1 | 132 | 2 | 6 | 0 | 1 | 14 |  |  | DI | [9 empty] | 2.6\0.1:14 |  |  |  | S | [6 empty] | F1 |  | 15
BCV131 | DX06 | DIO1 | 132 | 2 | 6 | 0 | 1 | 15 |  |  | DI | [9 empty] | 2.6\0.1:15 |  |  |  | S | [6 empty] | F1 |  | 16
BCV131 | DX06 | DIO1 | 132 | 2 | 6 | 0 | 1 | 16 |  |  | DI | 4 | BCV131LCS01 | STT01 | CONVEYOR DRIVE ASSEMBLY 1 | Start Pushbutton | Activated |  | BCV131A |  | 2.6\0.1:16 | BR4-2150-E-00142 | 0 |  | S | [6 empty] | F1 | 17 | 18
BCV131 | DX06 | DIO1 | 132 | 2 | 6 | 0 | 1 | 17 |  |  | DI | 4 | BCV131LCS01 | STP01 | CONVEYOR DRIVE ASSEMBLY 1 | Stop Pushbutton | Activated |  | BCV131A |  | 2.6\0.1:17 | BR4-2150-E-00142 | 0 |  | S | [6 empty] | F1 | 19 | 20
BCV131 | DX06 | DIO1 | 132 | 2 | 6 | 0 | 1 | 18 |  |  | DI | 4 | BCV131AGB01LCS01 | STT01 | CONVEYOR DRIVE 1 REDUCER COOLING FAN | Start Pushbutton - GB Fan | Activated |  | BCV131AFN01 |  | 2.6\0.1:18 | BR4-2150-E-00096 | 0 |  | S | [6 empty] | F1 | 21 | 22
BCV131 | DX06 | DIO1 | 132 | 2 | 6 | 0 | 1 | 19 |  |  | DI | 4 | BCV131AGB01LCS01 | STP01 | CONVEYOR DRIVE 1 REDUCER COOLING FAN | Stop Pushbutton - GB Fan | Activated |  | BCV131AFN01 |  | 2.6\0.1:19 | BR4-2150-E-00096 | 0 |  | S | [6 empty] | F1 | 23 | 24
BCV131 | DX06 | DIO1 | 132 | 2 | 6 | 0 | 1 | 20 |  |  | DI | 4 | BCV131AFN02LCS01 | STT01 | CONVEYOR DRIVE 1 MOTOR COOLING FAN | Start Pushbutton - Motor Fan | Activated |  | BCV131AFN02 |  | 2.6\0.1:20 | BR4-2150-E-00090 | 0 |  | S | [6 empty] | F1 | 25 | 26
BCV131 | DX06 | DIO1 | 132 | 2 | 6 | 0 | 1 | 21 |  |  | DI | 4 | BCV131AFN02LCS01 | STP01 | CONVEYOR DRIVE 1 MOTOR COOLING FAN | Stop Pushbutton - Motor Fan | Activated |  | BCV131AFN02 |  | 2.6\0.1:21 | BR4-2150-E-00090 | 0 |  | S | [6 empty] | F1 | 27 | 28
BCV131 | DX06 | DIO1 | 132 | 2 | 6 | 0 | 1 | 22 |  |  | DI | 5 | [8 empty] | 2.6\0.1:22 | BR4-2150-E-00091 |  |  | S | [6 empty] | F1 | 29 | 30
BCV131 | DX06 | DIO1 | 132 | 2 | 6 | 0 | 1 | 23 |  |  | DI | 5 | [8 empty] | 2.6\0.1:23 | BR4-2150-E-00091 |  |  | S | [6 empty] | F1 | 31 | 32
BCV131 | DX06 | DIO1 | 132 | 2 | 6 | 0 | 1 | 24 |  |  | DI | 4 | BCV131AGB01LCS01 | STT02 | CONVEYOR DRIVE 1 REDUCER LUBRICATION PUMP | Start Pushbutton - GB Pump | Activated |  | BCV131APP02 |  | 2.6\0.1:24 | BR4-2150-E-00058 | 0 | Tag changed to STT02 to avoid duplicate. | S | [6 empty] | F1 | 33 | 34
BCV131 | DX06 | DIO1 | 132 | 2 | 6 | 0 | 1 | 25 |  |  | DI | 4 | BCV131AGB01LCS01 | STP02 | CONVEYOR DRIVE 1 REDUCER LUBRICATION PUMP | Stop Pushbutton - GB Pump | Activated |  | BCV131APP02 |  | 2.6\0.1:25 | BR4-2150-E-00058 | 0 | Tag changed to STP02 to avoid duplicate. | S | [6 empty] | F1 | 35 | 36
BCV131 | DX06 | DIO1 | 132 | 2 | 6 | 0 | 1 | 26 |  |  | DI | [9 empty] | 2.6\0.1:26 |  |  |  | S | [6 empty] | F1 | 37 | 38
BCV131 | DX06 | DIO1 | 132 | 2 | 6 | 0 | 1 | 27 |  |  | DI | [9 empty] | 2.6\0.1:27 |  |  |  | S | [6 empty] | F1 | 39 | 40
BCV131 | DX06 | DIO1 | 132 | 2 | 6 | 0 | 1 | 28 |  |  | DI | [9 empty] | 2.6\0.1:28 |  |  |  | S | [6 empty] | F1 | 41 | 42
BCV131 | DX06 | DIO1 | 132 | 2 | 6 | 0 | 1 | 29 |  |  | DI | [9 empty] | 2.6\0.1:29 |  |  |  | S | [6 empty] | F1 | 43 | 44
BCV131 | DX06 | DIO1 | 132 | 2 | 6 | 0 | 1 | 30 |  |  | DI | [9 empty] | 2.6\0.1:30 |  |  |  | S | [6 empty] | F1 | 45 | 46
BCV131 | DX06 | DIO1 | 132 | 2 | 6 | 0 | 1 | 31 |  |  | DI | [9 empty] | 2.6\0.1:31 |  |  |  | S | [6 empty] | F1 | 47 | 48
BCV131 | DX06 | DIO1 | 132 | 2 | 6 | 0 | 2 | 0 | BMXFCW303 | BMXDDI3202K | DI | 4 | BCV131LCS02 | STT01 | CONVEYOR DRIVE ASSEMBLY 2 | Start Pushbutton | Activated |  | BCV131B |  | 2.6\0.2:0 | BR4-2150-E-00142 | 0 |  | S | [6 empty] | F2 | 1 | 2
BCV131 | DX06 | DIO1 | 132 | 2 | 6 | 0 | 2 | 1 |  |  | DI | 4 | BCV131LCS02 | STP01 | CONVEYOR DRIVE ASSEMBLY 2 | Stop Pushbutton | Activated |  | BCV131B |  | 2.6\0.2:1 | BR4-2150-E-00142 | 0 |  | S | [6 empty] | F2 | 3 | 4
BCV131 | DX06 | DIO1 | 132 | 2 | 6 | 0 | 2 | 2 |  |  | DI | 4 | BCV131BGB01LCS01 | STT01 | CONVEYOR DRIVE 2 REDUCER COOLING FAN | Start Pushbutton - GB Fan | Activated |  | BCV131BFN01 |  | 2.6\0.2:2 | BR4-2150-E-00097 | A |  | S | [6 empty] | F2 | 5 | 6
BCV131 | DX06 | DIO1 | 132 | 2 | 6 | 0 | 2 | 3 |  |  | DI | 4 | BCV131BGB01LCS01 | STP01 | CONVEYOR DRIVE 2 REDUCER COOLING FAN | Stop Pushbutton - GB Fan | Activated |  | BCV131BFN01 |  | 2.6\0.2:3 | BR4-2150-E-00097 | A |  | S | [6 empty] | F2 | 7 | 8
BCV131 | DX06 | DIO1 | 132 | 2 | 6 | 0 | 2 | 4 |  |  | DI | 4 | BCV131BFN02LCS01 | STT01 | CONVEYOR DRIVE 2 MOTOR COOLING FAN | Start Pushbutton - Motor Fan | Activated |  | BCV131BFN02 |  | 2.6\0.2:4 | BR4-2150-E-00092 | A |  | S | [6 empty] | F2 | 9 | 10
BCV131 | DX06 | DIO1 | 132 | 2 | 6 | 0 | 2 | 5 |  |  | DI | 4 | BCV131BFN02LCS01 | STP01 | CONVEYOR DRIVE 2 MOTOR COOLING FAN | Stop Pushbutton - Motor Fan | Activated |  | BCV131BFN02 |  | 2.6\0.2:5 | BR4-2150-E-00092 | A |  | S | [6 empty] | F2 | 11 | 12
BCV131 | DX06 | DIO1 | 132 | 2 | 6 | 0 | 2 | 6 |  |  | DI | 5 | [8 empty] | 2.6\0.2:6 | BR4-2150-E-00093 |  |  | S | [6 empty] | F2 | 13 | 14
BCV131 | DX06 | DIO1 | 132 | 2 | 6 | 0 | 2 | 7 |  |  | DI | 5 | [8 empty] | 2.6\0.2:7 | BR4-2150-E-00093 |  |  | S | [6 empty] | F2 | 15 | 16
BCV131 | DX06 | DIO1 | 132 | 2 | 6 | 0 | 2 | 8 |  |  | DI | 4 | BCV131BDS01 | BDS01 | OVERLAND CONVEYOR | Belt Drift Switch 1 | Healthy |  | BCV131 |  | 2.6\0.2:8 | BR4-2150-E-00142 | 0 |  | S | [6 empty] | F2 | 17 | 18
BCV131 | DX06 | DIO1 | 132 | 2 | 6 | 0 | 2 | 9 |  |  | DI | 4 | BCV131BDS02 | BDS02 | OVERLAND CONVEYOR | Belt Drift Switch 2 | Healthy |  | BCV131 |  | 2.6\0.2:9 | BR4-2150-E-00142 | 0 |  | S | [6 empty] | F2 | 19 | 20
BCV131 | DX06 | DIO1 | 132 | 2 | 6 | 0 | 2 | 10 |  |  | DI | 4 | BCV131BDS03 | BDS03 | OVERLAND CONVEYOR | Belt Drift Switch 3 | Healthy |  | BCV131 |  | 2.6\0.2:10 | BR4-2150-E-00142 | 0 |  | S | [6 empty] | F2 | 21 | 22
BCV131 | DX06 | DIO1 | 132 | 2 | 6 | 0 | 2 | 11 |  |  | DI | 4 | BCV131BDS04 | BDS04 | OVERLAND CONVEYOR | Belt Drift Switch 4 | Healthy |  | BCV131 |  | 2.6\0.2:11 | BR4-2150-E-00142 | 0 |  | S | [6 empty] | F2 | 23 | 24
BCV131 | DX06 | DIO1 | 132 | 2 | 6 | 0 | 2 | 12 |  |  | DI | 4 | BCV131PP02LCS01 | STT01 | BCV131 Drive Station SUMP 1 PUMP | Start Pushbutton | Activated |  | BCV131PP02 |  | 2.6\0.2:12 | BR4-2150-E-00073 | A |  | S | [6 empty] | F2 | 25 | 26
BCV131 | DX06 | DIO1 | 132 | 2 | 6 | 0 | 2 | 13 |  |  | DI | 4 | BCV131PP02LCS01 | STP01 | BCV131 Drive Station SUMP 1 PUMP | Stop Pushbutton | Activated |  | BCV131PP02 |  | 2.6\0.2:13 | BR4-2150-E-00073 | A |  | S | [6 empty] | F2 | 27 | 28
BCV131 | DX06 | DIO1 | 132 | 2 | 6 | 0 | 2 | 14 |  |  | DI | 4 | BCV131PP02LCS01 | IS01 | BCV131 Drive Station SUMP 1 PUMP | Field Isolator | Closed |  | BCV131PP02 |  | 2.6\0.2:14 | BR4-2150-E-00073 | A |  | S | [6 empty] | F2 | 29 | 30
BCV131 | DX06 | DIO1 | 132 | 2 | 6 | 0 | 2 | 15 |  |  | DI | 5 | [8 empty] | 2.6\0.2:15 |  |  |  | S | [6 empty] | F2 | 31 | 32
BCV131 | DX06 | DIO1 | 132 | 2 | 6 | 0 | 2 | 16 |  |  | DI | 4 | BCV131BGB01LCS01 | STT02 | CONVEYOR DRIVE 2 REDUCER LUBRICATION PUMP | Start Pushbutton - GB Pump | Activated |  | BCV131BPP02 |  | 2.6\0.2:16 | BR4-2150-E-00059 | A | Tag changed to STT02 to avoid duplicate. | S | [6 empty] | F3 | 1 | 2
BCV131 | DX06 | DIO1 | 132 | 2 | 6 | 0 | 2 | 17 |  |  | DI | 4 | BCV131BGB01LCS01 | STP02 | CONVEYOR DRIVE 2 REDUCER LUBRICATION PUMP | Stop Pushbutton - GB Pump | Activated |  | BCV131BPP02 |  | 2.6\0.2:17 | BR4-2150-E-00059 | A | Tag changed to STP02 to avoid duplicate. | S | [6 empty] | F3 | 3 | 4
BCV131 | DX06 | DIO1 | 132 | 2 | 6 | 0 | 2 | 18 |  |  | DI | [9 empty] | 2.6\0.2:18 |  |  |  | S | [6 empty] | F3 | 5 | 6
BCV131 | DX06 | DIO1 | 132 | 2 | 6 | 0 | 2 | 19 |  |  | DI | [9 empty] | 2.6\0.2:19 |  |  |  | S | [6 empty] | F3 | 7 | 8
BCV131 | DX06 | DIO1 | 132 | 2 | 6 | 0 | 2 | 20 |  |  | DI | [9 empty] | 2.6\0.2:20 |  |  |  | S | [6 empty] | F3 | 9 | 10
BCV131 | DX06 | DIO1 | 132 | 2 | 6 | 0 | 2 | 21 |  |  | DI | [9 empty] | 2.6\0.2:21 |  |  |  | S | [6 empty] | F3 | 11 | 12
BCV131 | DX06 | DIO1 | 132 | 2 | 6 | 0 | 2 | 22 |  |  | DI | [9 empty] | 2.6\0.2:22 |  |  |  | S | [6 empty] | F3 | 13 | 14
BCV131 | DX06 | DIO1 | 132 | 2 | 6 | 0 | 2 | 23 |  |  | DI | [9 empty] | 2.6\0.2:23 |  |  |  | S | [6 empty] | F3 | 15 | 16
BCV131 | DX06 | DIO1 | 132 | 2 | 6 | 0 | 2 | 24 |  |  | DI | [9 empty] | 2.6\0.2:24 |  |  |  | S | [6 empty] | F3 | 17 | 18
BCV131 | DX06 | DIO1 | 132 | 2 | 6 | 0 | 2 | 25 |  |  | DI | [9 empty] | 2.6\0.2:25 |  |  |  | S | [6 empty] | F3 | 19 | 20
BCV131 | DX06 | DIO1 | 132 | 2 | 6 | 0 | 2 | 26 |  |  | DI | [9 empty] | 2.6\0.2:26 |  |  |  | S | [6 empty] | F3 | 21 | 22
BCV131 | DX06 | DIO1 | 132 | 2 | 6 | 0 | 2 | 27 |  |  | DI | [9 empty] | 2.6\0.2:27 |  |  |  | S | [6 empty] | F3 | 23 | 24
BCV131 | DX06 | DIO1 | 132 | 2 | 6 | 0 | 2 | 28 |  |  | DI | [9 empty] | 2.6\0.2:28 |  |  |  | S | [6 empty] | F3 | 25 | 26
BCV131 | DX06 | DIO1 | 132 | 2 | 6 | 0 | 2 | 29 |  |  | DI | [9 empty] | 2.6\0.2:29 |  |  |  | S | [6 empty] | F3 | 27 | 28
BCV131 | DX06 | DIO1 | 132 | 2 | 6 | 0 | 2 | 30 |  |  | DI | [9 empty] | 2.6\0.2:30 |  |  |  | S | [6 empty] | F3 | 29 | 30
BCV131 | DX06 | DIO1 | 132 | 2 | 6 | 0 | 2 | 31 |  |  | DI | [9 empty] | 2.6\0.2:31 |  |  |  | S | [6 empty] | F3 | 31 | 32
BCV131 | DX06 | DIO1 | 132 | 2 | 6 | 0 | 3 | 0 | BMXFTB2010 | BMXDDO1602 | DO | 4 | BCV131PP02SV01 | SV01 | BCV131 Drive Station SUMP 1 PUMP | Agitator Solenoid Valve | Open |  | BCV131PP02 |  | 2.6\0.3:0 | BR4-2150-E-00142 | 0 |  | S | [6 empty] | F5 | 1 | 2
BCV131 | DX06 | DIO1 | 132 | 2 | 6 | 0 | 3 | 1 |  |  | DO | [9 empty] | 2.6\0.3:1 |  |  |  | S | [6 empty] | F5 | 3 | 4
BCV131 | DX06 | DIO1 | 132 | 2 | 6 | 0 | 3 | 2 |  |  | DO | [9 empty] | 2.6\0.3:2 |  |  |  | S | [6 empty] | F5 | 5 | 6
BCV131 | DX06 | DIO1 | 132 | 2 | 6 | 0 | 3 | 3 |  |  | DO | 5 | BSR132DB02 | SR01 |  | BSR132DB02 Light Contactor | Activated | K353 | BSR132DB02 |  | 2.6\0.3:3 | BR4-2150-E-00114 |  |  | S | [6 empty] | F5 | 7 | 8
BCV131 | DX06 | DIO1 | 132 | 2 | 6 | 0 | 3 | 4 |  |  | DO | [9 empty] | 2.6\0.3:4 |  |  |  | S | [6 empty] | F5 | 9 | 10
BCV131 | DX06 | DIO1 | 132 | 2 | 6 | 0 | 3 | 5 |  |  | DO | [9 empty] | 2.6\0.3:5 |  |  |  | S | [6 empty] | F5 | 11 | 12
BCV131 | DX06 | DIO1 | 132 | 2 | 6 | 0 | 3 | 6 |  |  | DO | [9 empty] | 2.6\0.3:6 |  |  |  | S | [6 empty] | F5 | 13 | 14
BCV131 | DX06 | DIO1 | 132 | 2 | 6 | 0 | 3 | 7 |  |  | DO | [9 empty] | 2.6\0.3:7 |  |  |  | S | [6 empty] | F5 | 15 | 16
BCV131 | DX06 | DIO1 | 132 | 2 | 6 | 0 | 3 | 8 |  |  | DO | [9 empty] | 2.6\0.3:8 |  |  |  | S | [6 empty] | F5 | 17 | 18
BCV131 | DX06 | DIO1 | 132 | 2 | 6 | 0 | 3 | 9 |  |  | DO | [9 empty] | 2.6\0.3:9 |  |  |  | S | [6 empty] | F5 | 19 | 20
BCV131 | DX06 | DIO1 | 132 | 2 | 6 | 0 | 3 | 10 |  |  | DO | [9 empty] | 2.6\0.3:10 |  |  |  | S | [6 empty] | F5 | 21 | 22
BCV131 | DX06 | DIO1 | 132 | 2 | 6 | 0 | 3 | 11 |  |  | DO | [9 empty] | 2.6\0.3:11 |  |  |  | S | [6 empty] | F5 | 23 | 24
BCV131 | DX06 | DIO1 | 132 | 2 | 6 | 0 | 3 | 12 |  |  | DO | [9 empty] | 2.6\0.3:12 |  |  |  | S | [6 empty] | F5 | 25 | 26
BCV131 | DX06 | DIO1 | 132 | 2 | 6 | 0 | 3 | 13 |  |  | DO | [9 empty] | 2.6\0.3:13 |  |  |  | S | [6 empty] | F5 | 27 | 28
BCV131 | DX06 | DIO1 | 132 | 2 | 6 | 0 | 3 | 14 |  |  | DO | [9 empty] | 2.6\0.3:14 |  |  |  | S | [6 empty] | F5 | 29 | 30
BCV131 | DX06 | DIO1 | 132 | 2 | 6 | 0 | 3 | 15 |  |  | DO | [9 empty] | 2.6\0.3:15 |  |  |  | S | [6 empty] | F5 | 31 | 32
BCV131 | DX06 | DIO1 | 132 | 2 | 6 | 0 | 4 | 0 | BMXFTW301S | BMEAHI0812 | AI | 4 | BCV131SM01LIT01 | LIT01 | BCV131 Drive Station SUMP 1 | Level Indicating Transmitter - Level |  | % | BCV131SM01 | REAL | 2.6\0.4:0 | BR4-2150-E-00142 | 0 |  | S |  | 0 | 100 | 0 | 100 | #.# EU | F5 | 33 | 34
BCV131 | DX06 | DIO1 | 132 | 2 | 6 | 0 | 4 | 1 |  |  | AI | 5 | BCV131APP02FT01 | FT01 | BCV131 DRIVE A GEARBOX LUBRICATION | Oil Flow Transmitter |  | L/min | BCV131APP02 | REAL | 2.6\0.4:1 | BR4-2150-E-00259 | 0 | 0-100 used as per brownfileds scaling used on BCV210. | S |  | 0 | 25 | 0 | 25 | #.# EU | F5 | 35 | 36
BCV131 | DX06 | DIO1 | 132 | 2 | 6 | 0 | 4 | 2 |  |  | AI | 5 | BCV131BPP02FT01 | FT01 | BCV131 DRIVE B GEARBOX LUBRICATION | Oil Flow Transmitter |  | L/min | BCV131BPP02 | REAL | 2.6\0.4:2 | BR4-2150-E-00259 | 0 | 0-100 used as per brownfileds scaling used on BCV210. | S |  | 0 | 25 | 0 | 25 | #.# EU | F5 | 37 | 38
BCV131 | DX06 | DIO1 | 132 | 2 | 6 | 0 | 4 | 3 |  |  | AI | [9 empty] | 2.6\0.4:3 |  |  |  | S | [6 empty] | F5 | 39 | 40
BCV131 | DX06 | DIO1 | 132 | 2 | 6 | 0 | 4 | 4 |  |  | AI | [9 empty] | 2.6\0.4:4 |  |  |  | S | [6 empty] | F5 | 41 | 42
BCV131 | DX06 | DIO1 | 132 | 2 | 6 | 0 | 4 | 5 |  |  | AI | [9 empty] | 2.6\0.4:5 |  |  |  | S | [6 empty] | F5 | 43 | 44
BCV131 | DX06 | DIO1 | 132 | 2 | 6 | 0 | 4 | 6 |  |  | AI | [9 empty] | 2.6\0.4:6 |  |  |  | S | [6 empty] | F5 | 45 | 46
BCV131 | DX06 | DIO1 | 132 | 2 | 6 | 0 | 4 | 7 |  |  | AI | [9 empty] | 2.6\0.4:7 |  |  |  | S | [6 empty] | F5 | 47 | 48
BCV131 | DX06 | DIO1 | 132 | 2 | 6 | 0 | 5 | 0 | BMXFCW301S | BMXART0814 | RTDI | 4 | BCV131ARTD01 | RTD01 | CONVEYOR DRIVE ASSEMBLY 1 | Motor 1 Red Winding 1 Temperature |  | C | BCV131A | REAL | 2.6\0.5:0 | BR4-2150-E-00143 | 0 |  | S |  | 0 | 200 | 0 | 200 | # EU | F6 | 1 | 2 | 3
BCV131 | DX06 | DIO1 | 132 | 2 | 6 | 0 | 5 | 1 | BMXFCW301S |  | RTDI | 4 | BCV131ARTD02 | RTD02 | CONVEYOR DRIVE ASSEMBLY 1 | Motor 1 White Winding 1 Temperature |  | C | BCV131A | REAL | 2.6\0.5:1 | BR4-2150-E-00143 | 0 |  | S |  | 0 | 200 | 0 | 200 | # EU | F6 | 4 | 5 | 6
BCV131 | DX06 | DIO1 | 132 | 2 | 6 | 0 | 5 | 2 |  |  | RTDI | 4 | BCV131ARTD03 | RTD03 | CONVEYOR DRIVE ASSEMBLY 1 | Motor 1 Blue Winding 1 Temperature |  | C | BCV131A | REAL | 2.6\0.5:2 | BR4-2150-E-00143 | 0 |  | S |  | 0 | 200 | 0 | 200 | # EU | F6 | 7 | 8 | 9
BCV131 | DX06 | DIO1 | 132 | 2 | 6 | 0 | 5 | 3 |  |  | RTDI | 4 | BCV131ARTD04 | RTD04 | CONVEYOR DRIVE ASSEMBLY 1 | Motor 1 Red Winding 2 Temperature |  | C | BCV131A | REAL | 2.6\0.5:3 | BR4-2150-E-00143 | 0 |  | S |  | 0 | 200 | 0 | 200 | # EU | F6 | 10 | 11 | 12
BCV131 | DX06 | DIO1 | 132 | 2 | 6 | 0 | 5 | 4 |  |  | RTDI | 4 | BCV131ARTD05 | RTD05 | CONVEYOR DRIVE ASSEMBLY 1 | Motor 1 White Winding 2 Temperature |  | C | BCV131A | REAL | 2.6\0.5:4 | BR4-2150-E-00143 | 0 |  | S |  | 0 | 200 | 0 | 200 | # EU | F6 | 13 | 14 | 15
BCV131 | DX06 | DIO1 | 132 | 2 | 6 | 0 | 5 | 5 |  |  | RTDI | 4 | BCV131ARTD06 | RTD06 | CONVEYOR DRIVE ASSEMBLY 1 | Motor 1 Blue Winding 2 Temperature |  | C | BCV131A | REAL | 2.6\0.5:5 | BR4-2150-E-00143 | 0 |  | S |  | 0 | 200 | 0 | 200 | # EU | F6 | 16 | 17 | 18
BCV131 | DX06 | DIO1 | 132 | 2 | 6 | 0 | 5 | 6 |  |  | RTDI | 4 | BCV131ARTD07 | RTD07 | CONVEYOR DRIVE ASSEMBLY 1 | Motor 1 Non Drive End Bearing Temperature |  | C | BCV131A | REAL | 2.6\0.5:6 | BR4-2150-E-00143 | 0 |  | S |  | 0 | 200 | 0 | 200 | # EU | F6 | 19 | 20 | 21
BCV131 | DX06 | DIO1 | 132 | 2 | 6 | 0 | 5 | 7 |  |  | RTDI | 4 | BCV131ARTD08 | RTD08 | CONVEYOR DRIVE ASSEMBLY 1 | Motor 1 Drive End Bearing Temperature |  | C | BCV131A | REAL | 2.6\0.5:7 | BR4-2150-E-00143 | 0 |  | S |  | 0 | 200 | 0 | 200 | # EU | F6 | 22 | 23 | 24
BCV131 | DX06 | DIO1 | 132 | 2 | 6 | 0 | 6 | 0 | BMXFCW301S | BMXART0814 | RTDI | 4 | BCV131ARTD09 | RTD09 | CONVEYOR DRIVE ASSEMBLY 1 | Motor 1 Air Inlet Ambient Temperature |  | C | BCV131A | REAL | 2.6\0.6:0 | BR4-2150-E-00143 | 0 |  | S |  | 0 | 200 | 0 | 200 | # EU | F6 | 25 | 26 | 27
BCV131 | DX06 | DIO1 | 132 | 2 | 6 | 0 | 6 | 1 | BMXFCW301S |  | RTDI | 4 | BCV131AGB01RTD01 | RTD01 | CONVEYOR DRIVE ASSEMBLY 1 | Gearbox 1 Drive End Bearing Temperature |  | C | BCV131AGB01 | REAL | 2.6\0.6:1 | BR4-2150-E-00143 | 0 |  | S |  | 0 | 200 | 0 | 200 | # EU | F6 | 28 | 29 | 30
BCV131 | DX06 | DIO1 | 132 | 2 | 6 | 0 | 6 | 2 |  |  | RTDI | 4 | BCV131AGB01RTD02 | RTD02 | CONVEYOR DRIVE ASSEMBLY 1 | Gearbox 1 Oil Temperature |  | C | BCV131AGB01 | REAL | 2.6\0.6:2 | BR4-2150-E-00143 | 0 |  | S |  | 0 | 200 | 0 | 200 | # EU | F6 | 31 | 32 | 33
BCV131 | DX06 | DIO1 | 132 | 2 | 6 | 0 | 6 | 3 |  |  | RTDI | [9 empty] | 2.6\0.6:3 |  |  |  | S | [6 empty] | F6 | 34 | 35 | 36
BCV131 | DX06 | DIO1 | 132 | 2 | 6 | 0 | 6 | 4 |  |  | RTDI | [9 empty] | 2.6\0.6:4 |  |  |  | S | [6 empty] | F6 | 37 | 38 | 39
BCV131 | DX06 | DIO1 | 132 | 2 | 6 | 0 | 6 | 5 |  |  | RTDI | [9 empty] | 2.6\0.6:5 |  |  |  | S | [6 empty] | F6 | 40 | 41 | 42
BCV131 | DX06 | DIO1 | 132 | 2 | 6 | 0 | 6 | 6 |  |  | RTDI | [9 empty] | 2.6\0.6:6 |  |  |  | S | [6 empty] | F6 | 43 | 44 | 45
BCV131 | DX06 | DIO1 | 132 | 2 | 6 | 0 | 6 | 7 |  |  | RTDI | [9 empty] | 2.6\0.6:7 |  |  |  | S | [6 empty] | F6 | 46 | 47 | 48
BCV131 | DX06 | DIO1 | 132 | 2 | 6 | 0 | 7 | 0 | BMXFCW301S | BMXART0814 | RTDI | 4 | BCV131BRTD01 | RTD01 | CONVEYOR DRIVE ASSEMBLY 2 | Motor 2 Red Winding 1 Temperature |  | C | BCV131B | REAL | 2.6\0.7:0 | BR4-2150-E-00144 | 0 |  | S |  | 0 | 200 | 0 | 200 | # EU | F4 | 1 | 2 | 3
BCV131 | DX06 | DIO1 | 132 | 2 | 6 | 0 | 7 | 1 | BMXFCW301S |  | RTDI | 4 | BCV131BRTD02 | RTD02 | CONVEYOR DRIVE ASSEMBLY 2 | Motor 2 White Winding 1 Temperature |  | C | BCV131B | REAL | 2.6\0.7:1 | BR4-2150-E-00144 | 0 |  | S |  | 0 | 200 | 0 | 200 | # EU | F4 | 4 | 5 | 6
BCV131 | DX06 | DIO1 | 132 | 2 | 6 | 0 | 7 | 2 |  |  | RTDI | 4 | BCV131BRTD03 | RTD03 | CONVEYOR DRIVE ASSEMBLY 2 | Motor 2 Blue Winding 1 Temperature |  | C | BCV131B | REAL | 2.6\0.7:2 | BR4-2150-E-00144 | 0 |  | S |  | 0 | 200 | 0 | 200 | # EU | F4 | 7 | 8 | 9
BCV131 | DX06 | DIO1 | 132 | 2 | 6 | 0 | 7 | 3 |  |  | RTDI | 4 | BCV131BRTD04 | RTD04 | CONVEYOR DRIVE ASSEMBLY 2 | Motor 2 Red Winding 2 Temperature |  | C | BCV131B | REAL | 2.6\0.7:3 | BR4-2150-E-00144 | 0 |  | S |  | 0 | 200 | 0 | 200 | # EU | F4 | 10 | 11 | 12
BCV131 | DX06 | DIO1 | 132 | 2 | 6 | 0 | 7 | 4 |  |  | RTDI | 4 | BCV131BRTD05 | RTD05 | CONVEYOR DRIVE ASSEMBLY 2 | Motor 2 White Winding 2 Temperature |  | C | BCV131B | REAL | 2.6\0.7:4 | BR4-2150-E-00144 | 0 |  | S |  | 0 | 200 | 0 | 200 | # EU | F4 | 13 | 14 | 15
BCV131 | DX06 | DIO1 | 132 | 2 | 6 | 0 | 7 | 5 |  |  | RTDI | 4 | BCV131BRTD06 | RTD06 | CONVEYOR DRIVE ASSEMBLY 2 | Motor 2 Blue Winding 2 Temperature |  | C | BCV131B | REAL | 2.6\0.7:5 | BR4-2150-E-00144 | 0 |  | S |  | 0 | 200 | 0 | 200 | # EU | F4 | 16 | 17 | 18
BCV131 | DX06 | DIO1 | 132 | 2 | 6 | 0 | 7 | 6 |  |  | RTDI | 4 | BCV131BRTD07 | RTD07 | CONVEYOR DRIVE ASSEMBLY 2 | Motor 2 Non Drive End Bearing Temperature |  | C | BCV131B | REAL | 2.6\0.7:6 | BR4-2150-E-00144 | 0 |  | S |  | 0 | 200 | 0 | 200 | # EU | F4 | 19 | 20 | 21
BCV131 | DX06 | DIO1 | 132 | 2 | 6 | 0 | 7 | 7 |  |  | RTDI | 4 | BCV131BRTD08 | RTD08 | CONVEYOR DRIVE ASSEMBLY 2 | Motor 2 Drive End Bearing Temperature |  | C | BCV131B | REAL | 2.6\0.7:7 | BR4-2150-E-00144 | 0 |  | S |  | 0 | 200 | 0 | 200 | # EU | F4 | 22 | 23 | 24
BCV131 | DX06 | DIO1 | 132 | 2 | 6 | 0 | 8 | 0 | BMXFCW301S | BMXART0814 | RTDI | 4 | BCV131BRTD09 | RTD09 | CONVEYOR DRIVE ASSEMBLY 2 | Motor 2 Air Inlet Ambient Temperature |  | C | BCV131B | REAL | 2.6\0.8:0 | BR4-2150-E-00144 | 0 |  | S |  | 0 | 200 | 0 | 200 | # EU | F4 | 25 | 26 | 27
BCV131 | DX06 | DIO1 | 132 | 2 | 6 | 0 | 8 | 1 | BMXFCW301S |  | RTDI | 4 | BCV131BGB01RTD01 | RTD01 | CONVEYOR DRIVE ASSEMBLY 2 | Gearbox 2 Drive End Bearing Temperature |  | C | BCV131BGB01 | REAL | 2.6\0.8:1 | BR4-2150-E-00144 | 0 |  | S |  | 0 | 200 | 0 | 200 | # EU | F4 | 28 | 29 | 30
BCV131 | DX06 | DIO1 | 132 | 2 | 6 | 0 | 8 | 2 |  |  | RTDI | 4 | BCV131BGB01RTD02 | RTD02 | CONVEYOR DRIVE ASSEMBLY 2 | Gearbox 2 Oil Temperature |  | C | BCV131BGB01 | REAL | 2.6\0.8:2 | BR4-2150-E-00144 | 0 |  | S |  | 0 | 200 | 0 | 200 | # EU | F4 | 31 | 32 | 33
BCV131 | DX06 | DIO1 | 132 | 2 | 6 | 0 | 8 | 3 |  |  | RTDI | [9 empty] | 2.6\0.8:3 |  |  |  | S | [6 empty] | F4 | 34 | 35 | 36
BCV131 | DX06 | DIO1 | 132 | 2 | 6 | 0 | 8 | 4 |  |  | RTDI | [9 empty] | 2.6\0.8:4 |  |  |  | S | [6 empty] | F4 | 37 | 38 | 39
BCV131 | DX06 | DIO1 | 132 | 2 | 6 | 0 | 8 | 5 |  |  | RTDI | [9 empty] | 2.6\0.8:5 |  |  |  | S | [6 empty] | F4 | 40 | 41 | 42
BCV131 | DX06 | DIO1 | 132 | 2 | 6 | 0 | 8 | 6 |  |  | RTDI | [9 empty] | 2.6\0.8:6 |  |  |  | S | [6 empty] | F4 | 43 | 44 | 45
BCV131 | DX06 | DIO1 | 132 | 2 | 6 | 0 | 8 | 7 |  |  | RTDI | [9 empty] | 2.6\0.8:7 |  |  |  | S | [6 empty] | F4 | 46 | 47 | 48
BCV131 | DX06 | DIO1 | 132 | 2 | 6 | 0 | 9 | 0 | BMXFTB2010 | BMXEHC0800 | HSCI | 3 | BCV131SS02 | SS02 | OVERLAND CONVEYOR | Underspeed Pulse | Healthy |  | BCV131 |  | 2.6\0.9:0 | BR4-2150-E-00142 | 0 |  | S | [6 empty] | F2 | 33 | 34
BCV131 | DX06 | DIO1 | 132 | 2 | 6 | 0 | 9 | 1 |  |  | HSCI | 3 | BCV131ZQ02 | ZQ02 | OVERLAND CONVEYOR | Distance Pulse |  |  | BCV131 |  | 2.6\0.9:1 | BR4-2150-E-00142 | 0 |  | S | [6 empty] | F2 | 35 | 36
BCV131 | DX06 | DIO1 | 132 | 2 | 6 | 0 | 9 | 2 |  |  | HSCI | [9 empty] | 2.6\0.9:2 |  |  |  | S | [6 empty] | F2 | 37 | 38
BCV131 | DX06 | DIO1 | 132 | 2 | 6 | 0 | 9 | 3 |  |  | HSCI | [9 empty] | 2.6\0.9:3 |  |  |  | S | [6 empty] | F2 | 39 | 40
BCV131 | DX06 | DIO1 | 132 | 2 | 6 | 0 | 9 | 4 |  |  | HSCI | [9 empty] | 2.6\0.9:4 |  |  |  | S | [6 empty] | F2 | 41 | 42
BCV131 | DX06 | DIO1 | 132 | 2 | 6 | 0 | 9 | 5 |  |  | HSCI | [9 empty] | 2.6\0.9:5 |  |  |  | S | [6 empty] | F2 | 43 | 44
BCV131 | DX06 | DIO1 | 132 | 2 | 6 | 0 | 9 | 6 |  |  | HSCI | [9 empty] | 2.6\0.9:6 |  |  |  | S | [6 empty] | F2 | 45 | 46
BCV131 | DX06 | DIO1 | 132 | 2 | 6 | 0 | 9 | 7 |  |  | HSCI | [9 empty] | 2.6\0.9:7 |  |  |  | S | [6 empty] | F2 | 47 | 48
BCV131 | DX06 | DIO1 | 132 | 2 | 6 | 0 | 10 |  |  | BMXXEM010 | [10 empty] | 2.6\0.10:
BCV131 | DX06 | DIO1 | 132 | 2 | 6 | 0 | 10 | [13 empty] | 2.6\0.10:
BCV131 | DX06 | DIO1 | 132 | 2 | 6 | 0 | 10 | [13 empty] | 2.6\0.10:
BCV131 | DX06 | DIO1 | 132 | 2 | 6 | 0 | 10 | [13 empty] | 2.6\0.10:
BCV131 | DX06 | DIO1 | 132 | 2 | 6 | 0 | 11 |  |  | BMXXEM010 | [10 empty] | 2.6\0.11:
BCV131 | DX06 | DIO1 | 132 | 2 | 6 | 0 | 11 | [13 empty] | 2.6\0.11:
BCV131 | DX06 | DIO1 | 132 | 2 | 6 | 0 | 11 | [13 empty] | 2.6\0.11:
BCV131 | DX06 | DIO1 | 132 | 2 | 6 | 0 | 11 | [13 empty] | 2.6\0.11:
[12 empty] | 5 | BCV131PP02LCS01 | LOS01 |  | BCV131PP02 Field LOS To Swrm DX Panel/Bucket |  | SUB LINK | BCV131PP02 |  |  | BR4-2150-E-00073 | [9 empty] | F7 | 1 | 2 | 3 | 4
[12 empty] | 5 | BCV131AGB01LCS01 | LOS01 |  | BCV131AGB01 Field LOS To Swrm DX Panel/Bucket |  | SUB LINK | BCV131AGB01 |  |  | BR4-2150-E-00097 | [9 empty] | F7 | 5 | 6 | 7 | 8
[12 empty] | 5 | BCV131AFN02LCS01 | LOS01 |  | BCV131AFN02/03 Field LOS To Swrm DX Panel Relay |  | SUB LINK | BCV131AFN02 |  |  | BR4-2150-E-00092 | [9 empty] | F7 | 9 | 10 | 11 | 12
[12 empty] | 5 | BCV131BGB01LCS01 | LOS01 |  | BCV131BGB01 Field LOS To Swrm DX Panel/Bucket |  | SUB LINK | BCV131BGB01 |  |  | BR4-2150-E-00097 | [9 empty] | F7 | 13 | 14 | 15 | 16
[12 empty] | 5 | BCV131BFN02LCS01 | LOS01 |  | BCV131BFN02/03 Field LOS To Swrm DX Panel Relay |  | SUB LINK | BCV131BFN02 |  |  | BR4-2150-E-00092 | [9 empty] | F7 | 17 | 18 | 19 | 20
[32 empty] | F7 | 21 | 22 | 23 | 24
[32 empty] | F7 | 25 | 26 | 27 | 28
[32 empty] | F7 | 29 | 30 | 31 | 32
[32 empty] | F7 | 33 | 34 | 35 | 36
[32 empty] | F7 | 37 | 38 | 39 | 40
[32 empty] | F7 | 41 | 42 | 43 | 44
[32 empty] | F7 | 45 | 46 | 47 | 48
BCV131AX02 - BCV131 - Drive Station C
BCV131 | AX02 | SIO1 | SLC02 | 2 | 1 | 0 | 0 | CPU |  | 1059305 | Type 5
BCV131 | AX02 | SIO1 | SLC02 | 2 | 1 | 0 | 1 | 1 | I1 | 1044125 | SDI | 3 | BCV131PWS01 | PWS01A |  | Pullwire Switch 1 ChA | Healthy |  | BCV131 |  | 2.1\0.1:1 | BR4-2150-E-00167 | 0
BCV131 | AX02 | SIO1 | SLC02 | 2 | 1 | 0 | 1 | 2 | I2 | 1047162 | SDI | 3 | BCV131PWS01 | PWS01B |  | Pullwire Switch 1 ChB | Healthy |  | BCV131 |  | 2.1\0.1:2 | BR4-2150-E-00167 | 0
BCV131 | AX02 | SIO1 | SLC02 | 2 | 1 | 0 | 1 | 3 | I3 |  | SDI | 3 | BCV131PWS02 | PWS02A |  | Pullwire Switch 2 ChA | Healthy |  | BCV131 |  | 2.1\0.1:3 | BR4-2150-E-00167 | 0
BCV131 | AX02 | SIO1 | SLC02 | 2 | 1 | 0 | 1 | 4 | I4 |  | SDI | 3 | BCV131PWS02 | PWS02B |  | Pullwire Switch 2 ChB | Healthy |  | BCV131 |  | 2.1\0.1:4 | BR4-2150-E-00167 | 0
BCV131 | AX02 | SIO1 | SLC02 | 2 | 1 | 0 | 1 | 5 | I5 |  | SDI | 3 | BCV131PWS03 | PWS03A |  | Pullwire Switch 3 ChA | Healthy |  | BCV131 |  | 2.1\0.1:5 | BR4-2150-E-00167 | 0
BCV131 | AX02 | SIO1 | SLC02 | 2 | 1 | 0 | 1 | 6 | I6 |  | SDI | 3 | BCV131PWS03 | PWS03B |  | Pullwire Switch 3 ChB | Healthy |  | BCV131 |  | 2.1\0.1:6 | BR4-2150-E-00167 | 0
BCV131 | AX02 | SIO1 | SLC02 | 2 | 1 | 0 | 1 | 7 | I7 |  | SDI | 3 | BCV131PWS04 | PWS04A |  | Pullwire Switch 4 ChA | Healthy |  | BCV131 |  | 2.1\0.1:7 | BR4-2150-E-00167 | 0
BCV131 | AX02 | SIO1 | SLC02 | 2 | 1 | 0 | 1 | 8 | I8 |  | SDI | 3 | BCV131PWS04 | PWS04B |  | Pullwire Switch 4 ChB | Healthy |  | BCV131 |  | 2.1\0.1:8 | BR4-2150-E-00167 | 0
BCV131 | AX02 | SIO1 | SLC02 | 2 | 1 | 0 | 1 | 1 | Q1 |  | SDO | 3 | BCV131YA03 | YL03 |  | Start Up Warning (Beacon) | Active |  | BCV131 |  | 2.1\0.1:1 | BR4-2150-E-00167 | 0
BCV131 | AX02 | SIO1 | SLC02 | 2 | 1 | 0 | 1 | 2 | Q2 |  | SDO | 3 | BCV131YA03 | YA03 |  | Start Up Warning (Siren) | Active |  | BCV131 |  | 2.1\0.1:2 | BR4-2150-E-00167 | 0
BCV131 | AX02 | SIO1 | SLC02 | 2 | 1 | 0 | 1 | 3 | Q3 |  | SDO | 3 | BCV131YA04 | YA04 |  | Start Up Warning (Siren) | Active |  | BCV131 |  | 2.1\0.1:3 | BR4-2150-E-00167 | 0
BCV131 | AX02 | SIO1 | SLC02 | 2 | 1 | 0 | 1 | 4 | Q4 |  | SDO | 3 | [8 empty] | 2.1\0.1:4 | BR4-2150-E-00167 | 0
BCV131 | AX02 | SIO1 | SLC02 | 2 | 1 | 0 | 2 | 1 | I1 | 1044125 | SDI | 3 | BCV131LCS03 | LOS03A |  | Lock Off Stop 3 ChA | Healthy |  | BCV131 |  | 2.1\0.2:1 | BR4-2150-E-00167 | 0
BCV131 | AX02 | SIO1 | SLC02 | 2 | 1 | 0 | 2 | 2 | I2 |  | SDI | 3 | BCV131LCS03 | LOS03B |  | Lock Off Stop 3 ChB | Healthy |  | BCV131 |  | 2.1\0.2:2 | BR4-2150-E-00167 | 0
BCV131 | AX02 | SIO1 | SLC02 | 2 | 1 | 0 | 2 | 3 | I3 |  | SDI | 3 | [8 empty] | 2.1\0.2:3 | BR4-2150-E-00167 | 0
BCV131 | AX02 | SIO1 | SLC02 | 2 | 1 | 0 | 2 | 4 | I4 |  | SDI | 3 | [8 empty] | 2.1\0.2:4 | BR4-2150-E-00167 | 0
BCV131 | AX02 | SIO1 | SLC02 | 2 | 1 | 0 | 2 | 5 | I5 |  | SDI | 3 | [8 empty] | 2.1\0.2:5 | BR4-2150-E-00167 | 0
BCV131 | AX02 | SIO1 | SLC02 | 2 | 1 | 0 | 2 | 6 | I6 |  | SDI | 3 | [8 empty] | 2.1\0.2:6 | BR4-2150-E-00167 | 0
BCV131 | AX02 | SIO1 | SLC02 | 2 | 1 | 0 | 2 | 7 | I7 |  | SDI | 3 | [8 empty] | 2.1\0.2:7 | BR4-2150-E-00167 | 0
BCV131 | AX02 | SIO1 | SLC02 | 2 | 1 | 0 | 2 | 8 | I8 |  | SDI | 3 | [8 empty] | 2.1\0.2:8 | BR4-2150-E-00167 | 0
BCV131 | AX02 | SIO1 | SLC02 | 2 | 1 | 0 | 2 | 1 | Q1 |  | SDO | 3 | [8 empty] | 2.1\0.2:1 | BR4-2150-E-00167 | 0
BCV131 | AX02 | SIO1 | SLC02 | 2 | 1 | 0 | 2 | 2 | Q2 |  | SDO | 3 | [8 empty] | 2.1\0.2:2 | BR4-2150-E-00167 | 0
BCV131 | AX02 | SIO1 | SLC02 | 2 | 1 | 0 | 2 | 3 | Q3 |  | SDO | 3 | [8 empty] | 2.1\0.2:3 | BR4-2150-E-00167 | 0
BCV131 | AX02 | SIO1 | SLC02 | 2 | 1 | 0 | 2 | 4 | Q4 |  | SDO | 3 | [8 empty] | 2.1\0.2:4 | BR4-2150-E-00167 | 0
BCV131DX07 - BCV131 - Head End Drive Station C
EIO node #7 | DX07 | DIO1 | 132 | 2 | 7 | 0
CV702 | DX07 | DIO1 | 132 | 2 | 7 | 0 |  | Chassis |  | BMEXBP1200
CV702 | DX07 | DIO1 | 132 | 2 | 7 | 0 |  | Power |  | BMXCPS4022 |  | total |  | spare |  | % spare
CV702 | DX07 | DIO1 | 132 | 2 | 7 | 0 | 0 | Comms |  | BMECRA31210 | I/O1 | 104 |  | 83 |  | 79.81%
BCV131 | DX07 | DIO1 | 132 | 2 | 7 | 0 | 1 | 0 | BMXFCW303 | BMXDDI3202K | DI | 4 |  | CB01 |  | 240VAC Circuit Breaker - Spare | Closed | Q106 | BCV131DX07 |  | 2.7\0.1:0 | BR4-2150-E-00147 | 0 |  | D | [6 empty] | F1 |  | 1
BCV131 | DX07 | DIO1 | 132 | 2 | 7 | 0 | 1 | 1 |  |  | DI | 4 |  | VDC01 |  | 24VDC DIO1 Output Control Supply | Healthy | Q143 | BCV131DX07 |  | 2.7\0.1:1 | BR4-2150-E-00147 | 0 |  | D | [6 empty] | F1 |  | 2
BCV131 | DX07 | DIO1 | 132 | 2 | 7 | 0 | 1 | 2 |  |  | DI | 4 |  | VDC02 |  | 24VDC GW1 Control Supply | Healthy | Q157 | BCV131DX07 |  | 2.7\0.1:2 | BR4-2150-E-00147 | 0 |  | D | [6 empty] | F1 |  | 3
BCV131 | DX07 | DIO1 | 132 | 2 | 7 | 0 | 1 | 3 |  |  | DI | 4 |  | VDC03 |  | 24VDC Instrument Supply | Healthy | Q164 | BCV131DX07 |  | 2.7\0.1:3 | BR4-2150-E-00147 | 0 |  | D | [6 empty] | F1 |  | 4
BCV131 | DX07 | DIO1 | 132 | 2 | 7 | 0 | 1 | 4 |  |  | DI | 4 |  | VDC04 |  | 24VDC Transmitter Supply | Healthy | Q168 | BCV131DX07 |  | 2.7\0.1:4 | BR4-2150-E-00147 | 0 |  | D | [6 empty] | F1 |  | 5
BCV131 | DX07 | DIO1 | 132 | 2 | 7 | 0 | 1 | 5 |  |  | DI | 4 |  | VDC05 |  | 24VDC BCV131DX07 Control Supply | Healthy | Q172 | BCV131DX07 |  | 2.7\0.1:5 | BR4-2150-E-00147 | 0 |  | D | [6 empty] | F1 |  | 6
BCV131 | DX07 | DIO1 | 132 | 2 | 7 | 0 | 1 | 6 |  |  | DI | 4 |  | VDC06 |  | 24VDC BCV131C Control Supply | Healthy | Q176 | BCV131DX07 |  | 2.7\0.1:6 | BR4-2150-E-00147 | 0 |  | D | [6 empty] | F1 |  | 7
BCV131 | DX07 | DIO1 | 132 | 2 | 7 | 0 | 1 | 7 |  |  | DI | 4 |  | VDC07 |  | 24VDC Spare Control Supply | Healthy | Q180 | BCV131DX07 |  | 2.7\0.1:7 | BR4-2150-E-00147 | 0 |  | D | [6 empty] | F1 |  | 8
BCV131 | DX07 | DIO1 | 132 | 2 | 7 | 0 | 1 | 8 |  |  | DI | 4 |  | VDC08 |  | 24VDC Spare Control Supply | Healthy | Q184 | BCV131DX07 |  | 2.7\0.1:8 | BR4-2150-E-00147 | 0 |  | D | [6 empty] | F1 |  | 9
BCV131 | DX07 | DIO1 | 132 | 2 | 7 | 0 | 1 | 9 |  |  | DI | 4 |  | VDC09 |  | 24VDC Spare Control Supply | Healthy | Q188 | BCV131DX07 |  | 2.7\0.1:9 | BR4-2150-E-00147 | 0 |  | D | [6 empty] | F1 |  | 10
BCV131 | DX07 | DIO1 | 132 | 2 | 7 | 0 | 1 | 10 |  |  | DI | 4 |  | VDC10 |  | 24VDC Spare Control Supply | Healthy | Q192 | BCV131DX07 |  | 2.7\0.1:10 | BR4-2150-E-00147 | 0 |  | D | [6 empty] | F1 |  | 11
BCV131 | DX07 | DIO1 | 132 | 2 | 7 | 0 | 1 | 11 |  |  | DI | 4 |  | VDC11 |  | 24VDC Spare Control Supply | Healthy | Q196 | BCV131DX07 |  | 2.7\0.1:11 | BR4-2150-E-00147 | 0 |  | D | [6 empty] | F1 |  | 12
BCV131 | DX07 | DIO1 | 132 | 2 | 7 | 0 | 1 | 12 |  |  | DI | [9 empty] | 2.7\0.1:12 |  |  |  | S | [6 empty] | F1 |  | 13
BCV131 | DX07 | DIO1 | 132 | 2 | 7 | 0 | 1 | 13 |  |  | DI | [9 empty] | 2.7\0.1:13 |  |  |  | S | [6 empty] | F1 |  | 14
BCV131 | DX07 | DIO1 | 132 | 2 | 7 | 0 | 1 | 14 |  |  | DI | [9 empty] | 2.7\0.1:14 |  |  |  | S | [6 empty] | F1 |  | 15
BCV131 | DX07 | DIO1 | 132 | 2 | 7 | 0 | 1 | 15 |  |  | DI | [9 empty] | 2.7\0.1:15 |  |  |  | S | [6 empty] | F1 |  | 16
BCV131 | DX07 | DIO1 | 132 | 2 | 7 | 0 | 1 | 16 |  |  | DI | 4 | BCV131LCS03 | STT01 | CONVEYOR DRIVE ASSEMBLY 3 | Start Pushbutton | Activated |  | BCV131C |  | 2.7\0.1:16 | BR4-2150-E-00148 | 0 |  | S | [6 empty] | F1 | 17 | 18
BCV131 | DX07 | DIO1 | 132 | 2 | 7 | 0 | 1 | 17 |  |  | DI | 4 | BCV131LCS03 | STP01 | CONVEYOR DRIVE ASSEMBLY 3 | Stop Pushbutton | Activated |  | BCV131C |  | 2.7\0.1:17 | BR4-2150-E-00148 | 0 |  | S | [6 empty] | F1 | 19 | 20
BCV131 | DX07 | DIO1 | 132 | 2 | 7 | 0 | 1 | 18 |  |  | DI | 4 | BCV131CGB01LCS01 | STT01 | CONVEYOR DRIVE 3 REDUCER COOLING FAN BCV131CFN01 | Start Pushbutton - GB Fan | Activated |  | BCV131CFN01 |  | 2.7\0.1:18 | BR4-2150-E-00098 | A |  | S | [6 empty] | F1 | 21 | 22
BCV131 | DX07 | DIO1 | 132 | 2 | 7 | 0 | 1 | 19 |  |  | DI | 4 | BCV131CGB01LCS01 | STP01 | CONVEYOR DRIVE 3 REDUCER COOLING FAN BCV131CFN01 | Stop Pushbutton - GB Fan | Activated |  | BCV131CFN01 |  | 2.7\0.1:19 | BR4-2150-E-00098 | A |  | S | [6 empty] | F1 | 23 | 24
BCV131 | DX07 | DIO1 | 132 | 2 | 7 | 0 | 1 | 20 |  |  | DI | 4 | BCV131CFN02LCS01 | STT01 | CONVEYOR DRIVE 3 MOTOR LUBRICATION PUMP BCV131CPP01 | Start Pushbutton - Motor Fan | Activated |  | BCV131CFN02 |  | 2.7\0.1:20 | BR4-2150-E-00094 | A |  | S | [6 empty] | F1 | 25 | 26
BCV131 | DX07 | DIO1 | 132 | 2 | 7 | 0 | 1 | 21 |  |  | DI | 4 | BCV131CFN02LCS01 | STP01 | CONVEYOR DRIVE 3 MOTOR LUBRICATION PUMP BCV131CPP01 | Stop Pushbutton - Motor Fan | Activated |  | BCV131CFN02 |  | 2.7\0.1:21 | BR4-2150-E-00094 | A |  | S | [6 empty] | F1 | 27 | 28
BCV131 | DX07 | DIO1 | 132 | 2 | 7 | 0 | 1 | 22 |  |  | DI | 5 | [8 empty] | 2.7\0.1:22 | BR4-2150-E-00095 | A |  | S | [6 empty] | F1 | 29 | 30
BCV131 | DX07 | DIO1 | 132 | 2 | 7 | 0 | 1 | 23 |  |  | DI | 5 | [8 empty] | 2.7\0.1:23 | BR4-2150-E-00095 | A |  | S | [6 empty] | F1 | 31 | 32
BCV131 | DX07 | DIO1 | 132 | 2 | 7 | 0 | 1 | 24 |  |  | DI | 4 | BCV131BDS05 | BDS05 | OVERLAND CONVEYOR | Belt Drift Switch 5 | Healthy |  | BCV131 |  | 2.7\0.1:24 | BR4-2150-E-00148 | 0 |  | S | [6 empty] | F1 | 33 | 34
BCV131 | DX07 | DIO1 | 132 | 2 | 7 | 0 | 1 | 25 |  |  | DI | 4 | BCV131BDS06 | BDS06 | OVERLAND CONVEYOR | Belt Drift Switch 6 | Healthy |  | BCV131 |  | 2.7\0.1:25 | BR4-2150-E-00148 | 0 |  | S | [6 empty] | F1 | 35 | 36
BCV131 | DX07 | DIO1 | 132 | 2 | 7 | 0 | 1 | 26 |  |  | DI | 5 | BCV131ZS01 | ZS01 | BCV131 LIMIT SWITCH OUT | Take Up Trolley Outer Limit | Healthy | K218 | BCV131 |  | 2.7\0.1:26 | BR4-2150-E-00148 | 0 |  | S | [6 empty] | F1 | 37 | 38
BCV131 | DX07 | DIO1 | 132 | 2 | 7 | 0 | 1 | 27 |  |  | DI | 5 | BCV131ZS02 | ZS02 | BCV131 LIMIT SWITCH IN | Take Up Trolley Inner Limit | Healthy | K220 | BCV131 |  | 2.7\0.1:27 | BR4-2150-E-00148 | 0 |  | S | [6 empty] | F1 | 39 | 40
BCV131 | DX07 | DIO1 | 132 | 2 | 7 | 0 | 1 | 28 |  |  | DI | 4 | BCV131CGB01LCS01 | STT02 | CONVEYOR DRIVE 1 REDUCER LUBRICATION PUMP | Start Pushbutton - GB Pump | Activated |  | BCV131CPP02 |  | 2.7\0.1:28 | BR4-2150-E-00060 | A | Tag changed to STT02 to avoid duplicate | S | [6 empty] | F1 | 41 | 42
BCV131 | DX07 | DIO1 | 132 | 2 | 7 | 0 | 1 | 29 |  |  | DI | 4 | BCV131CGB01LCS01 | STP02 | CONVEYOR DRIVE 1 REDUCER LUBRICATION PUMP | Stop Pushbutton - GB Pump | Activated |  | BCV131CPP02 |  | 2.7\0.1:29 | BR4-2150-E-00060 | A | Tag changed to STP02 to avoid duplicate | S | [6 empty] | F1 | 43 | 44
BCV131 | DX07 | DIO1 | 132 | 2 | 7 | 0 | 1 | 30 |  |  | DI | [9 empty] | 2.7\0.1:30 |  |  |  | S | [6 empty] | F1 | 45 | 46
BCV131 | DX07 | DIO1 | 132 | 2 | 7 | 0 | 1 | 31 |  |  | DI | [9 empty] | 2.7\0.1:31 |  |  |  | S | [6 empty] | F1 | 47 | 48
BCV131 | DX07 | DIO1 | 132 | 2 | 7 | 0 | 2 | 0 | BMXFCW303 | BMXDDI3202K | DI | 4 | BCV131PP03LCS01 | STT01 | BCV131 Drive Station SUMP 2 PUMP | Local Start Pushbutton | Activated |  | BCV131PP03 |  | 2.7\0.2:0 | BR4-2150-E-00075 | A |  | S | [6 empty] | F2 | 1 | 2
BCV131 | DX07 | DIO1 | 132 | 2 | 7 | 0 | 2 | 1 |  |  | DI | 4 | BCV131PP03LCS01 | STP01 | BCV131 Drive Station SUMP 2 PUMP | Local Stop Pushbutton | Activated |  | BCV131PP03 |  | 2.7\0.2:1 | BR4-2150-E-00075 | A |  | S | [6 empty] | F2 | 3 | 4
BCV131 | DX07 | DIO1 | 132 | 2 | 7 | 0 | 2 | 2 |  |  | DI | 4 | BCV131PP03LCS01 | IS01 | BCV131 Drive Station SUMP 2 PUMP | Field Isolator | Closed |  | BCV131PP03 |  | 2.7\0.2:2 | BR4-2150-E-00075 | A |  | S | [6 empty] | F2 | 5 | 6
BCV131 | DX07 | DIO1 | 132 | 2 | 7 | 0 | 2 | 3 |  |  | DI | [9 empty] | 2.7\0.2:3 |  |  |  | S | [6 empty] | F2 | 7 | 8
BCV131 | DX07 | DIO1 | 132 | 2 | 7 | 0 | 2 | 4 |  |  | DI | [9 empty] | 2.7\0.2:4 |  |  |  | S | [6 empty] | F2 | 9 | 10
BCV131 | DX07 | DIO1 | 132 | 2 | 7 | 0 | 2 | 5 |  |  | DI | [9 empty] | 2.7\0.2:5 |  |  |  | S | [6 empty] | F2 | 11 | 12
BCV131 | DX07 | DIO1 | 132 | 2 | 7 | 0 | 2 | 6 |  |  | DI | [9 empty] | 2.7\0.2:6 |  |  |  | S | [6 empty] | F2 | 13 | 14
BCV131 | DX07 | DIO1 | 132 | 2 | 7 | 0 | 2 | 7 |  |  | DI | [9 empty] | 2.7\0.2:7 |  |  |  | S | [6 empty] | F2 | 15 | 16
BCV131 | DX07 | DIO1 | 132 | 2 | 7 | 0 | 2 | 8 |  |  | DI | [9 empty] | 2.7\0.2:8 |  |  |  | S | [6 empty] | F2 | 17 | 18
BCV131 | DX07 | DIO1 | 132 | 2 | 7 | 0 | 2 | 9 |  |  | DI | [9 empty] | 2.7\0.2:9 |  |  |  | S | [6 empty] | F2 | 19 | 20
BCV131 | DX07 | DIO1 | 132 | 2 | 7 | 0 | 2 | 10 |  |  | DI | [9 empty] | 2.7\0.2:10 |  |  |  | S | [6 empty] | F2 | 21 | 22
BCV131 | DX07 | DIO1 | 132 | 2 | 7 | 0 | 2 | 11 |  |  | DI | [9 empty] | 2.7\0.2:11 |  |  |  | S | [6 empty] | F2 | 23 | 24
BCV131 | DX07 | DIO1 | 132 | 2 | 7 | 0 | 2 | 12 |  |  | DI | [9 empty] | 2.7\0.2:12 |  |  |  | S | [6 empty] | F2 | 25 | 26
BCV131 | DX07 | DIO1 | 132 | 2 | 7 | 0 | 2 | 13 |  |  | DI | [9 empty] | 2.7\0.2:13 |  |  |  | S | [6 empty] | F2 | 27 | 28
BCV131 | DX07 | DIO1 | 132 | 2 | 7 | 0 | 2 | 14 |  |  | DI | [9 empty] | 2.7\0.2:14 |  |  |  | S | [6 empty] | F2 | 29 | 30
BCV131 | DX07 | DIO1 | 132 | 2 | 7 | 0 | 2 | 15 |  |  | DI | [9 empty] | 2.7\0.2:15 |  |  |  | S | [6 empty] | F2 | 31 | 32
BCV131 | DX07 | DIO1 | 132 | 2 | 7 | 0 | 2 | 16 |  |  | DI | [9 empty] | 2.7\0.2:16 |  |  |  | S | [6 empty] | F3 | 1 | 2
BCV131 | DX07 | DIO1 | 132 | 2 | 7 | 0 | 2 | 17 |  |  | DI | [9 empty] | 2.7\0.2:17 |  |  |  | S | [6 empty] | F3 | 3 | 4
BCV131 | DX07 | DIO1 | 132 | 2 | 7 | 0 | 2 | 18 |  |  | DI | [9 empty] | 2.7\0.2:18 |  |  |  | S | [6 empty] | F3 | 5 | 6
BCV131 | DX07 | DIO1 | 132 | 2 | 7 | 0 | 2 | 19 |  |  | DI | [9 empty] | 2.7\0.2:19 |  |  |  | S | [6 empty] | F3 | 7 | 8
BCV131 | DX07 | DIO1 | 132 | 2 | 7 | 0 | 2 | 20 |  |  | DI | [9 empty] | 2.7\0.2:20 |  |  |  | S | [6 empty] | F3 | 9 | 10
BCV131 | DX07 | DIO1 | 132 | 2 | 7 | 0 | 2 | 21 |  |  | DI | [9 empty] | 2.7\0.2:21 |  |  |  | S | [6 empty] | F3 | 11 | 12
BCV131 | DX07 | DIO1 | 132 | 2 | 7 | 0 | 2 | 22 |  |  | DI | [9 empty] | 2.7\0.2:22 |  |  |  | S | [6 empty] | F3 | 13 | 14
BCV131 | DX07 | DIO1 | 132 | 2 | 7 | 0 | 2 | 23 |  |  | DI | [9 empty] | 2.7\0.2:23 |  |  |  | S | [6 empty] | F3 | 15 | 16
BCV131 | DX07 | DIO1 | 132 | 2 | 7 | 0 | 2 | 24 |  |  | DI | [9 empty] | 2.7\0.2:24 |  |  |  | S | [6 empty] | F3 | 17 | 18
BCV131 | DX07 | DIO1 | 132 | 2 | 7 | 0 | 2 | 25 |  |  | DI | [9 empty] | 2.7\0.2:25 |  |  |  | S | [6 empty] | F3 | 19 | 20
BCV131 | DX07 | DIO1 | 132 | 2 | 7 | 0 | 2 | 26 |  |  | DI | [9 empty] | 2.7\0.2:26 |  |  |  | S | [6 empty] | F3 | 21 | 22
BCV131 | DX07 | DIO1 | 132 | 2 | 7 | 0 | 2 | 27 |  |  | DI | [9 empty] | 2.7\0.2:27 |  |  |  | S | [6 empty] | F3 | 23 | 24
BCV131 | DX07 | DIO1 | 132 | 2 | 7 | 0 | 2 | 28 |  |  | DI | [9 empty] | 2.7\0.2:28 |  |  |  | S | [6 empty] | F3 | 25 | 26
BCV131 | DX07 | DIO1 | 132 | 2 | 7 | 0 | 2 | 29 |  |  | DI | [9 empty] | 2.7\0.2:29 |  |  |  | S | [6 empty] | F3 | 27 | 28
BCV131 | DX07 | DIO1 | 132 | 2 | 7 | 0 | 2 | 30 |  |  | DI | [9 empty] | 2.7\0.2:30 |  |  |  | S | [6 empty] | F3 | 29 | 30
BCV131 | DX07 | DIO1 | 132 | 2 | 7 | 0 | 2 | 31 |  |  | DI | [9 empty] | 2.7\0.2:31 |  |  |  | S | [6 empty] | F3 | 31 | 32
BCV131 | DX07 | DIO1 | 132 | 2 | 7 | 0 | 3 | 0 | BMXFTB2010 | BMXDDO1602 | DO | 5 | BCV131PP03SV01 | SV01 | BCV131 Drive Station SUMP 2 PUMP | Agitator Solenoid Valve | Open |  | BCV131PP03 |  | 2.7\0.3:0 | BR4-2150-E-00148 | 0 |  | S | [6 empty] | F5 | 1 | 2
BCV131 | DX07 | DIO1 | 132 | 2 | 7 | 0 | 3 | 1 |  |  | DO | [9 empty] | 2.7\0.3:1 |  |  |  | S | [6 empty] | F5 | 3 | 4
BCV131 | DX07 | DIO1 | 132 | 2 | 7 | 0 | 3 | 2 |  |  | DO | [9 empty] | 2.7\0.3:2 |  |  |  | S | [6 empty] | F5 | 5 | 6
BCV131 | DX07 | DIO1 | 132 | 2 | 7 | 0 | 3 | 3 |  |  | DO | [9 empty] | 2.7\0.3:3 |  |  |  | S | [6 empty] | F5 | 7 | 8
BCV131 | DX07 | DIO1 | 132 | 2 | 7 | 0 | 3 | 4 |  |  | DO | [9 empty] | 2.7\0.3:4 |  |  |  | S | [6 empty] | F5 | 9 | 10
BCV131 | DX07 | DIO1 | 132 | 2 | 7 | 0 | 3 | 5 |  |  | DO | [9 empty] | 2.7\0.3:5 |  |  |  | S | [6 empty] | F5 | 11 | 12
BCV131 | DX07 | DIO1 | 132 | 2 | 7 | 0 | 3 | 6 |  |  | DO | [9 empty] | 2.7\0.3:6 |  |  |  | S | [6 empty] | F5 | 13 | 14
BCV131 | DX07 | DIO1 | 132 | 2 | 7 | 0 | 3 | 7 |  |  | DO | [9 empty] | 2.7\0.3:7 |  |  |  | S | [6 empty] | F5 | 15 | 16
BCV131 | DX07 | DIO1 | 132 | 2 | 7 | 0 | 3 | 8 |  |  | DO | [9 empty] | 2.7\0.3:8 |  |  |  | S | [6 empty] | F5 | 17 | 18
BCV131 | DX07 | DIO1 | 132 | 2 | 7 | 0 | 3 | 9 |  |  | DO | [9 empty] | 2.7\0.3:9 |  |  |  | S | [6 empty] | F5 | 19 | 20
BCV131 | DX07 | DIO1 | 132 | 2 | 7 | 0 | 3 | 10 |  |  | DO | [9 empty] | 2.7\0.3:10 |  |  |  | S | [6 empty] | F5 | 21 | 22
BCV131 | DX07 | DIO1 | 132 | 2 | 7 | 0 | 3 | 11 |  |  | DO | [9 empty] | 2.7\0.3:11 |  |  |  | S | [6 empty] | F5 | 23 | 24
BCV131 | DX07 | DIO1 | 132 | 2 | 7 | 0 | 3 | 12 |  |  | DO | [9 empty] | 2.7\0.3:12 |  |  |  | S | [6 empty] | F5 | 25 | 26
BCV131 | DX07 | DIO1 | 132 | 2 | 7 | 0 | 3 | 13 |  |  | DO | [9 empty] | 2.7\0.3:13 |  |  |  | S | [6 empty] | F5 | 27 | 28
BCV131 | DX07 | DIO1 | 132 | 2 | 7 | 0 | 3 | 14 |  |  | DO | [9 empty] | 2.7\0.3:14 |  |  |  | S | [6 empty] | F5 | 29 | 30
BCV131 | DX07 | DIO1 | 132 | 2 | 7 | 0 | 3 | 15 |  |  | DO | [9 empty] | 2.7\0.3:15 |  |  |  | S | [6 empty] | F5 | 31 | 32
BCV131 | DX07 | DIO1 | 132 | 2 | 7 | 0 | 4 | 0 | BMXFTW301S | BMEAHI0812 | AI | 4 | BCV131SM02LIT02 | LIT02 | CONVEYOR DRIVE STATION SUMP 2 | Water Level |  | % | BCV131SM02 | REAL | 2.7\0.4:0 | BR4-2150-E-00148 | 0 |  | S |  | 0 | 100 | 0 | 100 | #.# EU | F5 | 33 | 34
BCV131 | DX07 | DIO1 | 132 | 2 | 7 | 0 | 4 | 1 |  |  | AI | 5 | BCV131CPP02FT01 | FT01 | BCV131 DRIVE C GEARBOX LUBRICATION | OIL FLOW TRANSMITTER |  | L/min | BCV131CPP02 | REAL | 2.7\0.4:1 | BR4-2150-E-00263 |  | To be added to BR4-2150-E-00263 next rev. 0-100 used as per brownfileds scaling used on BCV210. | S |  | 0 | 25 | 0 | 25 | #.# EU | F5 | 35 | 36
BCV131 | DX07 | DIO1 | 132 | 2 | 7 | 0 | 4 | 2 |  |  | AI | [9 empty] | 2.7\0.4:2 | [10 empty] | F5 | 37 | 38 |  |  | Earth
BCV131 | DX07 | DIO1 | 132 | 2 | 7 | 0 | 4 | 3 |  |  | AI | [9 empty] | 2.7\0.4:3 | [10 empty] | F5 | 39 | 40 |  |  | Earth
BCV131 | DX07 | DIO1 | 132 | 2 | 7 | 0 | 4 | 4 |  |  | AI | [9 empty] | 2.7\0.4:4 | [10 empty] | F5 | 41 | 42
BCV131 | DX07 | DIO1 | 132 | 2 | 7 | 0 | 4 | 5 |  |  | AI | [9 empty] | 2.7\0.4:5 | [10 empty] | F5 | 43 | 44
BCV131 | DX07 | DIO1 | 132 | 2 | 7 | 0 | 4 | 6 |  |  | AI | [9 empty] | 2.7\0.4:6 | [10 empty] | F5 | 45 | 46
BCV131 | DX07 | DIO1 | 132 | 2 | 7 | 0 | 4 | 7 |  |  | AI | [9 empty] | 2.7\0.4:7 | [10 empty] | F5 | 47 | 48
BCV131 | DX07 | DIO1 | 132 | 2 | 7 | 0 | 5 | 0 | BMXFCW301S | BMXART0814 | RTDI | 3 | BCV131CRTD01 | RTD01 | CONVEYOR DRIVE ASSEMBLY 3 | Motor 3 Red Winding 1 Temperature |  | C | BCV131C | REAL | 2.7\0.5:0 | BR4-2150-E-00149 | 0 |  | S |  | 0 | 200 | 0 | 200 | # EU | F6 | 1 | 2 | 3
BCV131 | DX07 | DIO1 | 132 | 2 | 7 | 0 | 5 | 1 | BMXFCW301S |  | RTDI | 3 | BCV131CRTD02 | RTD02 | CONVEYOR DRIVE ASSEMBLY 3 | Motor 3 White Winding 1 Temperature |  | C | BCV131C | REAL | 2.7\0.5:1 | BR4-2150-E-00149 | 0 |  | S |  | 0 | 200 | 0 | 200 | # EU | F6 | 4 | 5 | 6
BCV131 | DX07 | DIO1 | 132 | 2 | 7 | 0 | 5 | 2 |  |  | RTDI | 3 | BCV131CRTD03 | RTD03 | CONVEYOR DRIVE ASSEMBLY 3 | Motor 3 Blue Winding 1 Temperature |  | C | BCV131C | REAL | 2.7\0.5:2 | BR4-2150-E-00149 | 0 |  | S |  | 0 | 200 | 0 | 200 | # EU | F6 | 7 | 8 | 9
BCV131 | DX07 | DIO1 | 132 | 2 | 7 | 0 | 5 | 3 |  |  | RTDI | 3 | BCV131CRTD04 | RTD04 | CONVEYOR DRIVE ASSEMBLY 3 | Motor 3 Red Winding 2 Temperature |  | C | BCV131C | REAL | 2.7\0.5:3 | BR4-2150-E-00149 | 0 |  | S |  | 0 | 200 | 0 | 200 | # EU | F6 | 10 | 11 | 12
BCV131 | DX07 | DIO1 | 132 | 2 | 7 | 0 | 5 | 4 |  |  | RTDI | 3 | BCV131CRTD05 | RTD05 | CONVEYOR DRIVE ASSEMBLY 3 | Motor 3 White Winding 2 Temperature |  | C | BCV131C | REAL | 2.7\0.5:4 | BR4-2150-E-00149 | 0 |  | S |  | 0 | 200 | 0 | 200 | # EU | F6 | 13 | 14 | 15
BCV131 | DX07 | DIO1 | 132 | 2 | 7 | 0 | 5 | 5 |  |  | RTDI | 3 | BCV131CRTD06 | RTD06 | CONVEYOR DRIVE ASSEMBLY 3 | Motor 3 Blue Winding 2 Temperature |  | C | BCV131C | REAL | 2.7\0.5:5 | BR4-2150-E-00149 | 0 |  | S |  | 0 | 200 | 0 | 200 | # EU | F6 | 16 | 17 | 18
BCV131 | DX07 | DIO1 | 132 | 2 | 7 | 0 | 5 | 6 |  |  | RTDI | 3 | BCV131CRTD07 | RTD07 | CONVEYOR DRIVE ASSEMBLY 3 | Motor 3 Non Drive End Bearing Temperature |  | C | BCV131C | REAL | 2.7\0.5:6 | BR4-2150-E-00149 | 0 |  | S |  | 0 | 200 | 0 | 200 | # EU | F6 | 19 | 20 | 21
BCV131 | DX07 | DIO1 | 132 | 2 | 7 | 0 | 5 | 7 |  |  | RTDI | 3 | BCV131CRTD08 | RTD08 | CONVEYOR DRIVE ASSEMBLY 3 | Motor 3 Drive End Bearing Temperature |  | C | BCV131C | REAL | 2.7\0.5:7 | BR4-2150-E-00149 | 0 |  | S |  | 0 | 200 | 0 | 200 | # EU | F6 | 22 | 23 | 24
BCV131 | DX07 | DIO1 | 132 | 2 | 7 | 0 | 6 | 0 | BMXFCW301S | BMXART0814 | RTDI | 3 | BCV131CRTD09 | RTD09 | CONVEYOR DRIVE ASSEMBLY 3 | Motor 3 Air Inlet Ambient Temperature |  | C | BCV131C | REAL | 2.7\0.6:0 | BR4-2150-E-00149 | 0 |  | S |  | 0 | 200 | 0 | 200 | # EU | F6 | 25 | 26 | 27
BCV131 | DX07 | DIO1 | 132 | 2 | 7 | 0 | 6 | 1 | BMXFCW301S |  | RTDI | 3 | BCV131CGB01RTD01 | RTD01 | CONVEYOR DRIVE ASSEMBLY 3 | Gearbox 3 Drive End Bearing Temperature |  | C | BCV131CGB01RTD01 | REAL | 2.7\0.6:1 | BR4-2150-E-00149 | 0 |  | S |  | 0 | 200 | 0 | 200 | # EU | F6 | 28 | 29 | 30
BCV131 | DX07 | DIO1 | 132 | 2 | 7 | 0 | 6 | 2 |  |  | RTDI | 3 | BCV131CGB01RTD02 | RTD02 | CONVEYOR DRIVE ASSEMBLY 3 | Gearbox 3 Oil Temperature |  | C | BCV131CGB01RTD02 | REAL | 2.7\0.6:2 | BR4-2150-E-00149 | 0 |  | S |  | 0 | 200 | 0 | 200 | # EU | F6 | 31 | 32 | 33
BCV131 | DX07 | DIO1 | 132 | 2 | 7 | 0 | 6 | 3 |  |  | RTDI | [9 empty] | 2.7\0.6:3 | [10 empty] | F6 | 34 | 35 | 36
BCV131 | DX07 | DIO1 | 132 | 2 | 7 | 0 | 6 | 4 |  |  | RTDI | [9 empty] | 2.7\0.6:4 | [10 empty] | F6 | 37 | 38 | 39
BCV131 | DX07 | DIO1 | 132 | 2 | 7 | 0 | 6 | 5 |  |  | RTDI | [9 empty] | 2.7\0.6:5 | [10 empty] | F6 | 40 | 41 | 42
BCV131 | DX07 | DIO1 | 132 | 2 | 7 | 0 | 6 | 6 |  |  | RTDI | [9 empty] | 2.7\0.6:6 | [10 empty] | F6 | 43 | 44 | 45
BCV131 | DX07 | DIO1 | 132 | 2 | 7 | 0 | 6 | 7 |  |  | RTDI | [9 empty] | 2.7\0.6:7 | [10 empty] | F6 | 46 | 47 | 48
BCV131 | DX07 | DIO1 | 132 | 2 | 7 | 0 | 7 |  |  | BMXXEM010 |  | 0 | [8 empty] | 2.7\0.7:
BCV131 | DX07 | DIO1 | 132 | 2 | 7 | 0 | 7 |  |  |  |  | 0 | [8 empty] | 2.7\0.7:
BCV131 | DX07 | DIO1 | 132 | 2 | 7 | 0 | 7 |  |  |  |  | 0 | [8 empty] | 2.7\0.7:
BCV131 | DX07 | DIO1 | 132 | 2 | 7 | 0 | 7 |  |  |  |  | 0 | [8 empty] | 2.7\0.7:
BCV131 | DX07 | DIO1 | 132 | 2 | 7 | 0 | 8 |  |  | BMXXEM010 |  | 0 | [8 empty] | 2.7\0.8:
BCV131 | DX07 | DIO1 | 132 | 2 | 7 | 0 | 8 |  |  |  |  | 0 | [8 empty] | 2.7\0.8:
BCV131 | DX07 | DIO1 | 132 | 2 | 7 | 0 | 8 |  |  |  |  | 0 | [8 empty] | 2.7\0.8:
BCV131 | DX07 | DIO1 | 132 | 2 | 7 | 0 | 8 |  |  |  |  | 0 | [8 empty] | 2.7\0.8:
BCV131 | DX07 | DIO1 | 132 | 2 | 7 | 0 | 9 |  |  | BMXXEM010 |  | 0 | [8 empty] | 2.7\0.9:
BCV131 | DX07 | DIO1 | 132 | 2 | 7 | 0 | 9 |  |  |  |  | 0 | [8 empty] | 2.7\0.9:
BCV131 | DX07 | DIO1 | 132 | 2 | 7 | 0 | 9 |  |  |  |  | 0 | [8 empty] | 2.7\0.9:
BCV131 | DX07 | DIO1 | 132 | 2 | 7 | 0 | 9 |  |  |  |  | 0 | [8 empty] | 2.7\0.9: | [15 empty] | Earth
BCV131 | DX07 | DIO1 | 132 | 2 | 7 | 0 | 10 |  |  | BMXXEM010 |  | 0 | [8 empty] | 2.7\0.10:
BCV131 | DX07 | DIO1 | 132 | 2 | 7 | 0 | 10 |  |  |  |  | 0 | [8 empty] | 2.7\0.10:
BCV131 | DX07 | DIO1 | 132 | 2 | 7 | 0 | 10 |  |  |  |  | 0 | [8 empty] | 2.7\0.10:
BCV131 | DX07 | DIO1 | 132 | 2 | 7 | 0 | 10 |  |  |  |  | 0 | [8 empty] | 2.7\0.10:
BCV131 | DX07 | DIO1 | 132 | 2 | 7 | 0 | 11 |  |  | BMXXEM010 |  | 0 | [8 empty] | 2.7\0.11:
BCV131 | DX07 | DIO1 | 132 | 2 | 7 | 0 | 11 |  |  |  |  | 0 | [8 empty] | 2.7\0.11:
BCV131 | DX07 | DIO1 | 132 | 2 | 7 | 0 | 11 |  |  |  |  | 0 | [8 empty] | 2.7\0.11:
BCV131 | DX07 | DIO1 | 132 | 2 | 7 | 0 | 11 |  |  |  |  | 0 | [8 empty] | 2.7\0.11: | [15 empty] | Earth
[12 empty] | 5 | BCV131PP03LCS01 | LOS01 |  | BCV131PP03 Field LOS To Swrm DX Panel/Bucket |  | SUB LINK | BCV131PP03 |  |  | BR4-2150-E-00075 | [9 empty] | F7 | 1 | 2 | 3 | 4
[12 empty] | 5 | BCV131CGB01LCS01 | LOS01 |  | BCV131CGB01 Field LOS To Swrm DX Panel/Bucket |  | SUB LINK | BCV131CGB01 |  |  | BR4-2150-E-00098 | [9 empty] | F7 | 5 | 6 | 7 | 8
[12 empty] | 5 | BCV131CFN02LCS01 | LOS01 |  | BCV131CFN02/03 Field LOS To Swrm DX Panel Relay |  | SUB LINK | BCV131CFN02 |  |  | BR4-2150-E-00094 | [9 empty] | F7 | 9 | 10 | 11 | 12
[32 empty] | F7 | 13 | 14 | 15 | 16
[32 empty] | F7 | 17 | 18 | 19 | 20
[32 empty] | F7 | 21 | 22 | 23 | 24
[32 empty] | F7 | 25 | 26 | 27 | 28
[32 empty] | F7 | 29 | 30 | 31 | 32
[32 empty] | F7 | 33 | 34 | 35 | 36
[32 empty] | F7 | 37 | 38 | 39 | 40
[32 empty] | F7 | 41 | 42 | 43 | 44
[32 empty] | F7 | 45 | 46 | 47 | 48
BCV131AX01 - BCV131 - Drive Station A&B
BCV131 | AX01 | SIO1 | SLC01 | 1 | 1 | 0 | 0 | CPU |  | 1059305 | Type 6
BCV131 | AX01 | SIO1 | SLC01 | 1 | 1 | 0 | 1 | 1 | I1 | 1044125 | SDI | 3 | BCV131PWS05 | PWS05A |  | Pullwire Switch 5 ChA | Healthy |  | BCV131 |  | 1.1\0.1:1 | BR4-2150-E-00165 | 0
BCV131 | AX01 | SIO1 | SLC01 | 1 | 1 | 0 | 1 | 2 | I2 | 1047162 | SDI | 3 | BCV131PWS05 | PWS05B |  | Pullwire Switch 5 ChB | Healthy |  | BCV131 |  | 1.1\0.1:2 | BR4-2150-E-00165 | 0
BCV131 | AX01 | SIO1 | SLC01 | 1 | 1 | 0 | 1 | 3 | I3 |  | SDI | 3 | BCV131PWS06 | PWS06A |  | Pullwire Switch 6 ChA | Healthy |  | BCV131 |  | 1.1\0.1:3 | BR4-2150-E-00165 | 0
BCV131 | AX01 | SIO1 | SLC01 | 1 | 1 | 0 | 1 | 4 | I4 |  | SDI | 3 | BCV131PWS06 | PWS06B |  | Pullwire Switch 6 ChB | Healthy |  | BCV131 |  | 1.1\0.1:4 | BR4-2150-E-00165 | 0
BCV131 | AX01 | SIO1 | SLC01 | 1 | 1 | 0 | 1 | 5 | I5 |  | SDI | 3 | BCV131PWS07 | PWS07A |  | Pullwire Switch 7 ChA | Healthy |  | BCV131 |  | 1.1\0.1:5 | BR4-2150-E-00165 | 0
BCV131 | AX01 | SIO1 | SLC01 | 1 | 1 | 0 | 1 | 6 | I6 |  | SDI | 3 | BCV131PWS07 | PWS07B |  | Pullwire Switch 7 ChB | Healthy |  | BCV131 |  | 1.1\0.1:6 | BR4-2150-E-00165 | 0
BCV131 | AX01 | SIO1 | SLC01 | 1 | 1 | 0 | 1 | 7 | I7 |  | SDI | 3 | BCV131PWS08 | PWS08A |  | Pullwire Switch 8 ChA | Healthy |  | BCV131 |  | 1.1\0.1:7 | BR4-2150-E-00165 | 0
BCV131 | AX01 | SIO1 | SLC01 | 1 | 1 | 0 | 1 | 8 | I8 |  | SDI | 3 | BCV131PWS08 | PWS08B |  | Pullwire Switch 8 ChB | Healthy |  | BCV131 |  | 1.1\0.1:8 | BR4-2150-E-00165 | 0
BCV131 | AX01 | SIO1 | SLC01 | 1 | 1 | 0 | 1 | 1 | Q1 |  | SDO | 3 | BCV131YA01 | YL01 |  | Start Up Warning (Beacon) | Active |  | BCV131 |  | 1.1\0.1:1 | BR4-2150-E-00165 | 0
BCV131 | AX01 | SIO1 | SLC01 | 1 | 1 | 0 | 1 | 2 | Q2 |  | SDO | 3 | BCV131YA01 | YA01 |  | Start Up Warning (Siren) | Active |  | BCV131 |  | 1.1\0.1:2 | BR4-2150-E-00165 | 0
BCV131 | AX01 | SIO1 | SLC01 | 1 | 1 | 0 | 1 | 3 | Q3 |  | SDO | 3 | BCV131YA02 | YA02 |  | Start Up Warning (Siren) | Active |  | BCV131 |  | 1.1\0.1:3 | BR4-2150-E-00165 | 0
BCV131 | AX01 | SIO1 | SLC01 | 1 | 1 | 0 | 1 | 4 | Q4 |  | SDO | 3 | [8 empty] | 1.1\0.1:4 | BR4-2150-E-00165 | 0
BCV131 | AX01 | SIO1 | SLC01 | 1 | 1 | 0 | 2 | 1 | I1 | 1044125 | SDI | 3 | BCV131LCS01 | LOS01A |  | Lock Off Stop 1 ChA | Healthy |  | BCV131 |  | 1.1\0.2:1 | BR4-2150-E-00165 | 0
BCV131 | AX01 | SIO1 | SLC01 | 1 | 1 | 0 | 2 | 2 | I2 |  | SDI | 3 | BCV131LCS01 | LOS01B |  | Lock Off Stop 1 ChB | Healthy |  | BCV131 |  | 1.1\0.2:2 | BR4-2150-E-00165 | 0
BCV131 | AX01 | SIO1 | SLC01 | 1 | 1 | 0 | 2 | 3 | I3 |  | SDI | 3 | BCV131LCS02 | LOS02A |  | Lock Off Stop 2 ChA | Healthy |  | BCV131 |  | 1.1\0.2:3 | BR4-2150-E-00165 | 0
BCV131 | AX01 | SIO1 | SLC01 | 1 | 1 | 0 | 2 | 4 | I4 |  | SDI | 3 | BCV131LCS02 | LOS02B |  | Lock Off Stop 2 ChB | Healthy |  | BCV131 |  | 1.1\0.2:4 | BR4-2150-E-00165 | 0
BCV131 | AX01 | SIO1 | SLC01 | 1 | 1 | 0 | 2 | 5 | I5 |  | SDI | 3 | [8 empty] | 1.1\0.2:5 | BR4-2150-E-00165 | 0
BCV131 | AX01 | SIO1 | SLC01 | 1 | 1 | 0 | 2 | 6 | I6 |  | SDI | 3 | [8 empty] | 1.1\0.2:6 | BR4-2150-E-00165 | 0
BCV131 | AX01 | SIO1 | SLC01 | 1 | 1 | 0 | 2 | 7 | I7 |  | SDI | 3 | [8 empty] | 1.1\0.2:7 | BR4-2150-E-00165 | 0
BCV131 | AX01 | SIO1 | SLC01 | 1 | 1 | 0 | 2 | 8 | I8 |  | SDI | 3 | [8 empty] | 1.1\0.2:8 | BR4-2150-E-00165 | 0
BCV131 | AX01 | SIO1 | SLC01 | 1 | 1 | 0 | 2 | 1 | Q1 |  | SDO | 3 | [8 empty] | 1.1\0.2:1 | BR4-2150-E-00165 | 0
BCV131 | AX01 | SIO1 | SLC01 | 1 | 1 | 0 | 2 | 2 | Q2 |  | SDO | 3 | [8 empty] | 1.1\0.2:2 | BR4-2150-E-00165 | 0
BCV131 | AX01 | SIO1 | SLC01 | 1 | 1 | 0 | 2 | 3 | Q3 |  | SDO | 3 | [8 empty] | 1.1\0.2:3 | BR4-2150-E-00165 | 0
BCV131 | AX01 | SIO1 | SLC01 | 1 | 1 | 0 | 2 | 4 | Q4 |  | SDO | 3 | [8 empty] | 1.1\0.2:4 | BR4-2150-E-00165 | 0
BCV131DX08 - BCV131 - Ore Conditioning
EIO node #8 | DX08 | DIO1 | 132 | 2 | 8 | 0 | [7 empty] | LLM1144
BCV131 | DX08 | DIO1 | 132 | 2 | 8 | 0 |  | Chassis |  | BMEXBP1200
BCV131 | DX08 | DIO1 | 132 | 2 | 8 | 0 |  | Power |  | BMXCPS4022 |  | total |  | spare |  | % spare
BCV131 | DX08 | DIO1 | 132 | 2 | 8 | 0 | 0 | Comms |  | BMECRA31210 | I/O1 | 56 |  | 71 |  | 126.8%
BCV131 | DX08 | DIO1 | 132 | 2 | 8 | 0 | 1 | 0 | BMXFCW303 | BMXDDI3202K | DI | 4 |  | CB01 |  | 240VAC Circuit Breaker - Spare | Closed | Q106 | BCV131DX08 |  | 2.8\0.1:0 | BR4-2150-E-00152 | 0 |  | D | [6 empty] | F1 |  | 1
BCV131 | DX08 | DIO1 | 132 | 2 | 8 | 0 | 1 | 1 |  |  | DI | 4 |  | VDC01 |  | 24VDC DIO1 Output Control Supply | Healthy | Q143 | BCV131DX08 |  | 2.8\0.1:1 | BR4-2150-E-00152 | 0 |  | D | [6 empty] | F1 |  | 2
BCV131 | DX08 | DIO1 | 132 | 2 | 8 | 0 | 1 | 2 |  |  | DI | 4 |  | VDC02 |  | 24VDC GW1 Control Supply | Healthy | Q157 | BCV131DX08 |  | 2.8\0.1:2 | BR4-2150-E-00152 | 0 |  | D | [6 empty] | F1 |  | 3
BCV131 | DX08 | DIO1 | 132 | 2 | 8 | 0 | 1 | 3 |  |  | DI | 4 |  | VDC03 |  | 24VDC Instrument Supply | Healthy | Q164 | BCV131DX08 |  | 2.8\0.1:3 | BR4-2150-E-00152 | 0 |  | D | [6 empty] | F1 |  | 4
BCV131 | DX08 | DIO1 | 132 | 2 | 8 | 0 | 1 | 4 |  |  | DI | 4 |  | VDC04 |  | 24VDC Transmitter Supply | Healthy | Q168 | BCV131DX08 |  | 2.8\0.1:4 | BR4-2150-E-00152 | 0 |  | D | [6 empty] | F1 |  | 5
BCV131 | DX08 | DIO1 | 132 | 2 | 8 | 0 | 1 | 5 |  |  | DI | 4 |  | VDC05 |  | 24VDC BCV131DX08 Control Supply | Healthy | Q172 | BCV131DX08 |  | 2.8\0.1:5 | BR4-2150-E-00152 | 0 |  | D | [6 empty] | F1 |  | 6
BCV131 | DX08 | DIO1 | 132 | 2 | 8 | 0 | 1 | 6 |  |  | DI | 4 |  | VDC06 |  | 24VDC FT01 Control Supply | Healthy | Q176 | BCV131DX08 |  | 2.8\0.1:6 | BR4-2150-E-00152 | 0 |  | D | [6 empty] | F1 |  | 7
BCV131 | DX08 | DIO1 | 132 | 2 | 8 | 0 | 1 | 7 |  |  | DI | 4 |  | VDC07 |  | 24VDC Spare Control Supply | Healthy | Q180 | BCV131DX08 |  | 2.8\0.1:7 | BR4-2150-E-00152 | 0 |  | D | [6 empty] | F1 |  | 8
BCV131 | DX08 | DIO1 | 132 | 2 | 8 | 0 | 1 | 8 |  |  | DI | 4 |  | VDC08 |  | 24VDC Spare Control Supply | Healthy | Q184 | BCV131DX08 |  | 2.8\0.1:8 | BR4-2150-E-00152 | 0 |  | D | [6 empty] | F1 |  | 9
BCV131 | DX08 | DIO1 | 132 | 2 | 8 | 0 | 1 | 9 |  |  | DI | 4 |  | VDC09 |  | 24VDC Spare Control Supply | Healthy | Q188 | BCV131DX08 |  | 2.8\0.1:9 | BR4-2150-E-00152 | 0 |  | D | [6 empty] | F1 |  | 10
BCV131 | DX08 | DIO1 | 132 | 2 | 8 | 0 | 1 | 10 |  |  | DI | 4 |  | VDC10 |  | 24VDC Spare Control Supply | Healthy | Q192 | BCV131DX08 |  | 2.8\0.1:10 | BR4-2150-E-00152 | 0 |  | D | [6 empty] | F1 |  | 11
BCV131 | DX08 | DIO1 | 132 | 2 | 8 | 0 | 1 | 11 |  |  | DI | 4 |  | VDC11 |  | 24VDC Spare Control Supply | Healthy | Q196 | BCV131DX08 |  | 2.8\0.1:11 | BR4-2150-E-00152 | 0 |  | D | [6 empty] | F1 |  | 12
BCV131 | DX08 | DIO1 | 132 | 2 | 8 | 0 | 1 | 12 |  |  | DI | [9 empty] | 2.8\0.1:12 |  |  |  | S | [6 empty] | F1 |  | 13
BCV131 | DX08 | DIO1 | 132 | 2 | 8 | 0 | 1 | 13 |  |  | DI | [9 empty] | 2.8\0.1:13 |  |  |  | S | [6 empty] | F1 |  | 14
BCV131 | DX08 | DIO1 | 132 | 2 | 8 | 0 | 1 | 14 |  |  | DI | [9 empty] | 2.8\0.1:14 |  |  |  | S | [6 empty] | F1 |  | 15
BCV131 | DX08 | DIO1 | 132 | 2 | 8 | 0 | 1 | 15 |  |  | DI | [9 empty] | 2.8\0.1:15 |  |  |  | S | [6 empty] | F1 |  | 16
BCV131 | DX08 | DIO1 | 132 | 2 | 8 | 0 | 1 | 16 |  |  | DI | 5 | BCV131FIT10 | FQ10 | BCV131 ORE CONDITIONING SPRAY BAR | Flow Pulse | Active |  | BCV131 |  | 2.8\0.1:16 | BR4-2150-E-00153 | 0 |  | S | [6 empty] | F1 | 17 | 18
BCV131 | DX08 | DIO1 | 132 | 2 | 8 | 0 | 1 | 17 |  |  | DI | [9 empty] | 2.8\0.1:17 |  |  |  | S | [6 empty] | F1 | 19 | 20
BCV131 | DX08 | DIO1 | 132 | 2 | 8 | 0 | 1 | 18 |  |  | DI | [9 empty] | 2.8\0.1:18 |  |  |  | S | [6 empty] | F1 | 21 | 22
BCV131 | DX08 | DIO1 | 132 | 2 | 8 | 0 | 1 | 19 |  |  | DI | [9 empty] | 2.8\0.1:19 |  |  |  | S | [6 empty] | F1 | 23 | 24
BCV131 | DX08 | DIO1 | 132 | 2 | 8 | 0 | 1 | 20 |  |  | DI | [9 empty] | 2.8\0.1:20 |  |  |  | S | [6 empty] | F1 | 25 | 26
BCV131 | DX08 | DIO1 | 132 | 2 | 8 | 0 | 1 | 21 |  |  | DI | [9 empty] | 2.8\0.1:21 |  |  |  | S | [6 empty] | F1 | 27 | 28
BCV131 | DX08 | DIO1 | 132 | 2 | 8 | 0 | 1 | 22 |  |  | DI | [9 empty] | 2.8\0.1:22 |  |  |  | S | [6 empty] | F1 | 29 | 30
BCV131 | DX08 | DIO1 | 132 | 2 | 8 | 0 | 1 | 23 |  |  | DI | [9 empty] | 2.8\0.1:23 |  |  |  | S | [6 empty] | F1 | 31 | 32
BCV131 | DX08 | DIO1 | 132 | 2 | 8 | 0 | 1 | 24 |  |  | DI | [9 empty] | 2.8\0.1:24 |  |  |  | S | [6 empty] | F1 | 33 | 34
BCV131 | DX08 | DIO1 | 132 | 2 | 8 | 0 | 1 | 25 |  |  | DI | [9 empty] | 2.8\0.1:25 |  |  |  | S | [6 empty] | F1 | 35 | 36
BCV131 | DX08 | DIO1 | 132 | 2 | 8 | 0 | 1 | 26 |  |  | DI | [9 empty] | 2.8\0.1:26 |  |  |  | S | [6 empty] | F1 | 37 | 38
BCV131 | DX08 | DIO1 | 132 | 2 | 8 | 0 | 1 | 27 |  |  | DI | [9 empty] | 2.8\0.1:27 |  |  |  | S | [6 empty] | F1 | 39 | 40
BCV131 | DX08 | DIO1 | 132 | 2 | 8 | 0 | 1 | 28 |  |  | DI | [9 empty] | 2.8\0.1:28 |  |  |  | S | [6 empty] | F1 | 41 | 42
BCV131 | DX08 | DIO1 | 132 | 2 | 8 | 0 | 1 | 29 |  |  | DI | [9 empty] | 2.8\0.1:29 |  |  |  | S | [6 empty] | F1 | 43 | 44
BCV131 | DX08 | DIO1 | 132 | 2 | 8 | 0 | 1 | 30 |  |  | DI | [9 empty] | 2.8\0.1:30 |  |  |  | S | [6 empty] | F1 | 45 | 46
BCV131 | DX08 | DIO1 | 132 | 2 | 8 | 0 | 1 | 31 |  |  | DI | [9 empty] | 2.8\0.1:31 |  |  |  | S | [6 empty] | F1 | 47 | 48
BCV131 | DX08 | DIO1 | 132 | 2 | 8 | 0 | 2 | 0 | BMXFTB2010 | BMXDDO1602 | DO | 3 | BCV131SV02 | SV02 | BCV131 ORE CONDITIONING SPRAY BAR (2 NOZZLES) | Solenoid Valve 2 | Open |  | BCV131 |  | 2.8\0.2:0 | BR4-2150-E-00153 | 0 |  | S | [6 empty] | F5 | 1 | 2
BCV131 | DX08 | DIO1 | 132 | 2 | 8 | 0 | 2 | 1 |  |  | DO | 3 | BCV131SV03 | SV03 | BCV131 ORE CONDITIONING SPRAY BAR (1 NOZZLE) | Solenoid Valve 3 | Open |  | BCV131 |  | 2.8\0.2:1 | BR4-2150-E-00153 | 0 |  | S | [6 empty] | F5 | 3 | 4
BCV131 | DX08 | DIO1 | 132 | 2 | 8 | 0 | 2 | 2 |  |  | DO | 3 | BCV131SV04 | SV04 | BCV131 ORE CONDITIONING SPRAY BAR (4 NOZZLES) | Solenoid Valve 4 | Open |  | BCV131 |  | 2.8\0.2:2 | BR4-2150-E-00153 | 0 |  | S | [6 empty] | F5 | 5 | 6
BCV131 | DX08 | DIO1 | 132 | 2 | 8 | 0 | 2 | 3 |  |  | DO | [9 empty] | 2.8\0.2:3 |  |  |  | S | [6 empty] | F5 | 7 | 8
BCV131 | DX08 | DIO1 | 132 | 2 | 8 | 0 | 2 | 4 |  |  | DO | [9 empty] | 2.8\0.2:4 |  |  |  | S | [6 empty] | F5 | 9 | 10
BCV131 | DX08 | DIO1 | 132 | 2 | 8 | 0 | 2 | 5 |  |  | DO | [9 empty] | 2.8\0.2:5 |  |  |  | S | [6 empty] | F5 | 11 | 12
BCV131 | DX08 | DIO1 | 132 | 2 | 8 | 0 | 2 | 6 |  |  | DO | [9 empty] | 2.8\0.2:6 |  |  |  | S | [6 empty] | F5 | 13 | 14
BCV131 | DX08 | DIO1 | 132 | 2 | 8 | 0 | 2 | 7 |  |  | DO | [9 empty] | 2.8\0.2:7 |  |  |  | S | [6 empty] | F5 | 15 | 16
BCV131 | DX08 | DIO1 | 132 | 2 | 8 | 0 | 2 | 8 |  |  | DO | [9 empty] | 2.8\0.2:8 |  |  |  | S | [6 empty] | F5 | 17 | 18
BCV131 | DX08 | DIO1 | 132 | 2 | 8 | 0 | 2 | 9 |  |  | DO | [9 empty] | 2.8\0.2:9 |  |  |  | S | [6 empty] | F5 | 19 | 20
BCV131 | DX08 | DIO1 | 132 | 2 | 8 | 0 | 2 | 10 |  |  | DO | [9 empty] | 2.8\0.2:10 |  |  |  | S | [6 empty] | F5 | 21 | 22
BCV131 | DX08 | DIO1 | 132 | 2 | 8 | 0 | 2 | 11 |  |  | DO | [9 empty] | 2.8\0.2:11 |  |  |  | S | [6 empty] | F5 | 23 | 24
BCV131 | DX08 | DIO1 | 132 | 2 | 8 | 0 | 2 | 12 |  |  | DO | [9 empty] | 2.8\0.2:12 |  |  |  | S | [6 empty] | F5 | 25 | 26
BCV131 | DX08 | DIO1 | 132 | 2 | 8 | 0 | 2 | 13 |  |  | DO | [9 empty] | 2.8\0.2:13 |  |  |  | S | [6 empty] | F5 | 27 | 28
BCV131 | DX08 | DIO1 | 132 | 2 | 8 | 0 | 2 | 14 |  |  | DO | [9 empty] | 2.8\0.2:14 |  |  |  | S | [6 empty] | F5 | 29 | 30
BCV131 | DX08 | DIO1 | 132 | 2 | 8 | 0 | 2 | 15 |  |  | DO | [9 empty] | 2.8\0.2:15 |  |  |  | S | [6 empty] | F5 | 31 | 32
BCV131 | DX08 | DIO1 | 132 | 2 | 8 | 0 | 3 | 0 | BMXFTW301S | BMEAHI0812 | AI | 3 | BCV131FIT10 | FT10 | BCV131 ORE CONDITIONING SPRAY BAR | Flow Indicating Transmitter |  | L/s | BCV131 | REAL | 2.8\0.3:0 | BR4-2150-E-00153 | 0 |  | S |  | 0 | 18 | 0 | 18 | #.# EU | F5 | 33 | 34
BCV131 | DX08 | DIO1 | 132 | 2 | 8 | 0 | 3 | 1 |  |  | AI | [9 empty] | 2.8\0.3:1 |  |  |  | S | [6 empty] | F5 | 35 | 36
BCV131 | DX08 | DIO1 | 132 | 2 | 8 | 0 | 3 | 2 |  |  | AI | [9 empty] | 2.8\0.3:2 |  |  |  | S | [6 empty] | F5 | 37 | 38 |  |  | Earth
BCV131 | DX08 | DIO1 | 132 | 2 | 8 | 0 | 3 | 3 |  |  | AI | [9 empty] | 2.8\0.3:3 |  |  |  | S | [6 empty] | F5 | 39 | 40 |  |  | Earth
BCV131 | DX08 | DIO1 | 132 | 2 | 8 | 0 | 3 | 4 |  |  | AI | [9 empty] | 2.8\0.3:4 |  |  |  | S | [6 empty] | F5 | 41 | 42
BCV131 | DX08 | DIO1 | 132 | 2 | 8 | 0 | 3 | 5 |  |  | AI | [9 empty] | 2.8\0.3:5 |  |  |  | S | [6 empty] | F5 | 43 | 44
BCV131 | DX08 | DIO1 | 132 | 2 | 8 | 0 | 3 | 6 |  |  | AI | [9 empty] | 2.8\0.3:6 |  |  |  | S | [6 empty] | F5 | 45 | 46
BCV131 | DX08 | DIO1 | 132 | 2 | 8 | 0 | 3 | 7 |  |  | AI | [9 empty] | 2.8\0.3:7 |  |  |  | S | [6 empty] | F5 | 47 | 48
BCV131 | DX08 | DIO1 | 132 | 2 | 8 | 0 | 4 |  |  | BMXXEM010 |  | 0 | [8 empty] | 2.8\0.4:
BCV131 | DX08 | DIO1 | 132 | 2 | 8 | 0 | 4 |  |  |  |  | 0 | [8 empty] | 2.8\0.4:
BCV131 | DX08 | DIO1 | 132 | 2 | 8 | 0 | 4 |  |  |  |  | 0 | [8 empty] | 2.8\0.4:
BCV131 | DX08 | DIO1 | 132 | 2 | 8 | 0 | 4 |  |  |  |  | 0 | [8 empty] | 2.8\0.4:
BCV131 | DX08 | DIO1 | 132 | 2 | 8 | 0 | 5 |  |  | BMXXEM010 |  | 0 | [8 empty] | 2.8\0.5:
BCV131 | DX08 | DIO1 | 132 | 2 | 8 | 0 | 5 |  |  |  |  | 0 | [8 empty] | 2.8\0.5:
BCV131 | DX08 | DIO1 | 132 | 2 | 8 | 0 | 5 |  |  |  |  | 0 | [8 empty] | 2.8\0.5:
BCV131 | DX08 | DIO1 | 132 | 2 | 8 | 0 | 5 |  |  |  |  | 0 | [8 empty] | 2.8\0.5: | [15 empty] | Earth
BCV131 | DX08 | DIO1 | 132 | 2 | 8 | 0 | 6 |  |  | BMXXEM010 |  | 0 | [8 empty] | 2.8\0.6:
BCV131 | DX08 | DIO1 | 132 | 2 | 8 | 0 | 6 |  |  |  |  | 0 | [8 empty] | 2.8\0.6:
BCV131 | DX08 | DIO1 | 132 | 2 | 8 | 0 | 6 |  |  |  |  | 0 | [8 empty] | 2.8\0.6:
BCV131 | DX08 | DIO1 | 132 | 2 | 8 | 0 | 6 |  |  |  |  | 0 | [8 empty] | 2.8\0.6:
BCV131 | DX08 | DIO1 | 132 | 2 | 8 | 0 | 7 |  |  | BMXXEM010 |  | 0 | [8 empty] | 2.8\0.7:
BCV131 | DX08 | DIO1 | 132 | 2 | 8 | 0 | 7 |  |  |  |  | 0 | [8 empty] | 2.8\0.7:
BCV131 | DX08 | DIO1 | 132 | 2 | 8 | 0 | 7 |  |  |  |  | 0 | [8 empty] | 2.8\0.7:
BCV131 | DX08 | DIO1 | 132 | 2 | 8 | 0 | 7 |  |  |  |  | 0 | [8 empty] | 2.8\0.7: | [15 empty] | Earth
BCV131 | DX08 | DIO1 | 132 | 2 | 8 | 0 | 8 |  |  | BMXXEM010 |  | 0 | [8 empty] | 2.8\0.8:
BCV131 | DX08 | DIO1 | 132 | 2 | 8 | 0 | 8 |  |  |  |  | 0 | [8 empty] | 2.8\0.8:
BCV131 | DX08 | DIO1 | 132 | 2 | 8 | 0 | 8 |  |  |  |  | 0 | [8 empty] | 2.8\0.8:
BCV131 | DX08 | DIO1 | 132 | 2 | 8 | 0 | 8 |  |  |  |  | 0 | [8 empty] | 2.8\0.8:
BCV131 | DX08 | DIO1 | 132 | 2 | 8 | 0 | 9 |  |  | BMXXEM010 |  | 0 | [8 empty] | 2.8\0.9:
BCV131 | DX08 | DIO1 | 132 | 2 | 8 | 0 | 9 |  |  |  |  | 0 | [8 empty] | 2.8\0.9:
BCV131 | DX08 | DIO1 | 132 | 2 | 8 | 0 | 9 |  |  |  |  | 0 | [8 empty] | 2.8\0.9:
BCV131 | DX08 | DIO1 | 132 | 2 | 8 | 0 | 9 |  |  |  |  | 0 | [8 empty] | 2.8\0.9: | [15 empty] | Earth
BCV131 | DX08 | DIO1 | 132 | 2 | 8 | 0 | 10 |  |  | BMXXEM010 |  | 0 | [8 empty] | 2.8\0.10:
BCV131 | DX08 | DIO1 | 132 | 2 | 8 | 0 | 10 |  |  |  |  | 0 | [8 empty] | 2.8\0.10:
BCV131 | DX08 | DIO1 | 132 | 2 | 8 | 0 | 10 |  |  |  |  | 0 | [8 empty] | 2.8\0.10:
BCV131 | DX08 | DIO1 | 132 | 2 | 8 | 0 | 10 |  |  |  |  | 0 | [8 empty] | 2.8\0.10:
BCV131 | DX08 | DIO1 | 132 | 2 | 8 | 0 | 11 |  |  | BMXXEM010 |  | 0 | [8 empty] | 2.8\0.11:
BCV131 | DX08 | DIO1 | 132 | 2 | 8 | 0 | 11 |  |  |  |  | 0 | [8 empty] | 2.8\0.11:
BCV131 | DX08 | DIO1 | 132 | 2 | 8 | 0 | 11 |  |  |  |  | 0 | [8 empty] | 2.8\0.11:
BCV131 | DX08 | DIO1 | 132 | 2 | 8 | 0 | 11 |  |  |  |  | 0 | [8 empty] | 2.8\0.11: | [15 empty] | Earth
Earth
[32 empty] | F7 | 1 | 2 | 3 | 4
[32 empty] | F7 | 5 | 6 | 7 | 8
[32 empty] | F7 | 9 | 10 | 11 | 12
[32 empty] | F7 | 13 | 14 | 15 | 16
[32 empty] | F7 | 17 | 18 | 19 | 20
[32 empty] | F7 | 21 | 22 | 23 | 24
[32 empty] | F7 | 25 | 26 | 27 | 28
[32 empty] | F7 | 29 | 30 | 31 | 32
[32 empty] | F7 | 33 | 34 | 35 | 36
[32 empty] | F7 | 37 | 38 | 39 | 40
[32 empty] | F7 | 41 | 42 | 43 | 44
[32 empty] | F7 | 45 | 46 | 47 | 48
BCV131AX03 - BCV131 - 7463m
BCV131 | AX03 | SIO1 | SLC01 | 1 | 2 | 0 | 0 | CPU |  | 1059305 | Type 4 | 3 | [9 empty] | BR4-2150-E-00169 | 0
BCV131 | AX03 | SIO1 | SLC01 | 1 | 2 | 0 | 1 | 1 | I1 | 1044125 | SDI | 3 | BCV131PWS09 | PWS09A |  | Pullwire Switch 09 ChA | Healthy |  | BCV131 |  | 1.2\0.1:1 | BR4-2150-E-00169 | 0
BCV131 | AX03 | SIO1 | SLC01 | 1 | 2 | 0 | 1 | 2 | I2 | 1047162 | SDI | 3 | BCV131PWS09 | PWS09B |  | Pullwire Switch 09 ChB | Healthy |  | BCV131 |  | 1.2\0.1:2 | BR4-2150-E-00169 | 0
BCV131 | AX03 | SIO1 | SLC01 | 1 | 2 | 0 | 1 | 3 | I3 |  | SDI | 3 | BCV131PWS10 | PWS10A |  | Pullwire Switch 10 ChA | Healthy |  | BCV131 |  | 1.2\0.1:3 | BR4-2150-E-00169 | 0
BCV131 | AX03 | SIO1 | SLC01 | 1 | 2 | 0 | 1 | 4 | I4 |  | SDI | 3 | BCV131PWS10 | PWS10B |  | Pullwire Switch 10 ChB | Healthy |  | BCV131 |  | 1.2\0.1:4 | BR4-2150-E-00169 | 0
BCV131 | AX03 | SIO1 | SLC01 | 1 | 2 | 0 | 1 | 5 | I5 |  | SDI | 3 | [8 empty] | 1.2\0.1:5 | BR4-2150-E-00169 | 0
BCV131 | AX03 | SIO1 | SLC01 | 1 | 2 | 0 | 1 | 6 | I6 |  | SDI | 3 | [8 empty] | 1.2\0.1:6 | BR4-2150-E-00169 | 0
BCV131 | AX03 | SIO1 | SLC01 | 1 | 2 | 0 | 1 | 7 | I7 |  | SDI | 3 | [8 empty] | 1.2\0.1:7 | BR4-2150-E-00169 | 0
BCV131 | AX03 | SIO1 | SLC01 | 1 | 2 | 0 | 1 | 8 | I8 |  | SDI | 3 | [8 empty] | 1.2\0.1:8 | BR4-2150-E-00169 | 0
BCV131 | AX03 | SIO1 | SLC01 | 1 | 2 | 0 | 1 | 1 | Q1 | XTIO-Q | SDO | 3 | BCV131YA05 | YL05 |  | Start Up Warning (Beacon) | Active |  | BCV131 |  | 1.2\0.1:1 | BR4-2150-E-00169 | 0
BCV131 | AX03 | SIO1 | SLC01 | 1 | 2 | 0 | 1 | 2 | Q2 |  | SDO | 3 | BCV131YA05 | YA05 |  | Start Up Warning (Siren) | Active |  | BCV131 |  | 1.2\0.1:2 | BR4-2150-E-00169 | 0
BCV131 | AX03 | SIO1 | SLC01 | 1 | 2 | 0 | 1 | 3 | Q3 |  | SDO | 3 | BCV131YA06 | YA06 |  | Start Up Warning (Siren) | Active |  | BCV131 |  | 1.2\0.1:3 | BR4-2150-E-00169 | 0
BCV131 | AX03 | SIO1 | SLC01 | 1 | 2 | 0 | 1 | 4 | Q4 |  | SDO | 3 | [8 empty] | 1.2\0.1:4 | BR4-2150-E-00169 | 0
BCV131AX04 - BCV131 - 7220m
BCV131 | AX04 | SIO1 | SLC02 | 2 | 2 | 0 | 0 | CPU |  | 1059305 | Type 4 | 3 | [9 empty] | BR4-2150-E-00170 | 0
BCV131 | AX04 | SIO1 | SLC02 | 2 | 2 | 0 | 1 | 1 | I1 | 1044125 | SDI | 3 | BCV131PWS11 | PWS11A |  | Pullwire Switch 11 ChA | Healthy |  | BCV131 |  | 2.2\0.1:1 | BR4-2150-E-00170 | 0
BCV131 | AX04 | SIO1 | SLC02 | 2 | 2 | 0 | 1 | 2 | I2 | 1047162 | SDI | 3 | BCV131PWS11 | PWS11B |  | Pullwire Switch 11 ChB | Healthy |  | BCV131 |  | 2.2\0.1:2 | BR4-2150-E-00170 | 0
BCV131 | AX04 | SIO1 | SLC02 | 2 | 2 | 0 | 1 | 3 | I3 |  | SDI | 3 | BCV131PWS12 | PWS12A |  | Pullwire Switch 12 ChA | Healthy |  | BCV131 |  | 2.2\0.1:3 | BR4-2150-E-00170 | 0
BCV131 | AX04 | SIO1 | SLC02 | 2 | 2 | 0 | 1 | 4 | I4 |  | SDI | 3 | BCV131PWS12 | PWS12B |  | Pullwire Switch 12 ChB | Healthy |  | BCV131 |  | 2.2\0.1:4 | BR4-2150-E-00170 | 0
BCV131 | AX04 | SIO1 | SLC02 | 2 | 2 | 0 | 1 | 5 | I5 |  | SDI | 3 | [8 empty] | 2.2\0.1:5 | BR4-2150-E-00170 | 0
BCV131 | AX04 | SIO1 | SLC02 | 2 | 2 | 0 | 1 | 6 | I6 |  | SDI | 3 | [8 empty] | 2.2\0.1:6 | BR4-2150-E-00170 | 0
BCV131 | AX04 | SIO1 | SLC02 | 2 | 2 | 0 | 1 | 7 | I7 |  | SDI | 3 | [8 empty] | 2.2\0.1:7 | BR4-2150-E-00170 | 0
BCV131 | AX04 | SIO1 | SLC02 | 2 | 2 | 0 | 1 | 8 | I8 |  | SDI | 3 | [8 empty] | 2.2\0.1:8 | BR4-2150-E-00170 | 0
BCV131 | AX04 | SIO1 | SLC02 | 2 | 2 | 0 | 1 | 1 | Q1 | XTIO-Q | SDO | 3 | BCV131YA07 | YL07 |  | Start Up Warning (Beacon) | Active |  | BCV131 |  | 2.2\0.1:1 | BR4-2150-E-00170 | 0
BCV131 | AX04 | SIO1 | SLC02 | 2 | 2 | 0 | 1 | 2 | Q2 |  | SDO | 3 | BCV131YA07 | YA07 |  | Start Up Warning (Siren) | Active |  | BCV131 |  | 2.2\0.1:2 | BR4-2150-E-00170 | 0
BCV131 | AX04 | SIO1 | SLC02 | 2 | 2 | 0 | 1 | 3 | Q3 |  | SDO | 3 | BCV131YA08 | YA08 |  | Start Up Warning (Siren) | Active |  | BCV131 |  | 2.2\0.1:3 | BR4-2150-E-00170 | 0
BCV131 | AX04 | SIO1 | SLC02 | 2 | 2 | 0 | 1 | 4 | Q4 |  | SDO | 3 | [8 empty] | 2.2\0.1:4 | BR4-2150-E-00170 | 0
BCV131AX05 - BCV131 - 6977m
BCV131 | AX05 | SIO1 | SLC01 | 1 | 3 | 0 | 0 | CPU |  | 1059305 | Type 4 | 3 | [9 empty] | BR4-2150-E-00171 | 0
BCV131 | AX05 | SIO1 | SLC01 | 1 | 3 | 0 | 1 | 1 | I1 | 1044125 | SDI | 3 | BCV131PWS13 | PWS13A |  | Pullwire Switch 13 ChA | Healthy |  | BCV131 |  | 1.3\0.1:1 | BR4-2150-E-00171 | 0
BCV131 | AX05 | SIO1 | SLC01 | 1 | 3 | 0 | 1 | 2 | I2 | 1047162 | SDI | 3 | BCV131PWS13 | PWS13B |  | Pullwire Switch 13 ChB | Healthy |  | BCV131 |  | 1.3\0.1:2 | BR4-2150-E-00171 | 0
BCV131 | AX05 | SIO1 | SLC01 | 1 | 3 | 0 | 1 | 3 | I3 |  | SDI | 3 | BCV131PWS14 | PWS14A |  | Pullwire Switch 14 ChA | Healthy |  | BCV131 |  | 1.3\0.1:3 | BR4-2150-E-00171 | 0
BCV131 | AX05 | SIO1 | SLC01 | 1 | 3 | 0 | 1 | 4 | I4 |  | SDI | 3 | BCV131PWS14 | PWS14B |  | Pullwire Switch 14 ChB | Healthy |  | BCV131 |  | 1.3\0.1:4 | BR4-2150-E-00171 | 0
BCV131 | AX05 | SIO1 | SLC01 | 1 | 3 | 0 | 1 | 5 | I5 |  | SDI | 3 | [8 empty] | 1.3\0.1:5 | BR4-2150-E-00171 | 0
BCV131 | AX05 | SIO1 | SLC01 | 1 | 3 | 0 | 1 | 6 | I6 |  | SDI | 3 | [8 empty] | 1.3\0.1:6 | BR4-2150-E-00171 | 0
BCV131 | AX05 | SIO1 | SLC01 | 1 | 3 | 0 | 1 | 7 | I7 |  | SDI | 3 | [8 empty] | 1.3\0.1:7 | BR4-2150-E-00171 | 0
BCV131 | AX05 | SIO1 | SLC01 | 1 | 3 | 0 | 1 | 8 | I8 |  | SDI | 3 | [8 empty] | 1.3\0.1:8 | BR4-2150-E-00171 | 0
BCV131 | AX05 | SIO1 | SLC01 | 1 | 3 | 0 | 1 | 1 | Q1 | XTIO-Q | SDO | 3 | BCV131YA09 | YL09 |  | Start Up Warning (Beacon) | Active |  | BCV131 |  | 1.3\0.1:1 | BR4-2150-E-00171 | 0
BCV131 | AX05 | SIO1 | SLC01 | 1 | 3 | 0 | 1 | 2 | Q2 |  | SDO | 3 | BCV131YA09 | YA09 |  | Start Up Warning (Siren) | Active |  | BCV131 |  | 1.3\0.1:2 | BR4-2150-E-00171 | 0
BCV131 | AX05 | SIO1 | SLC01 | 1 | 3 | 0 | 1 | 3 | Q3 |  | SDO | 3 | BCV131YA10 | YA10 |  | Start Up Warning (Siren) | Active |  | BCV131 |  | 1.3\0.1:3 | BR4-2150-E-00171 | 0
BCV131 | AX05 | SIO1 | SLC01 | 1 | 3 | 0 | 1 | 4 | Q4 |  | SDO | 3 | [8 empty] | 1.3\0.1:4 | BR4-2150-E-00171 | 0
BCV131AX06 - BCV131 - 6734m
BCV131 | AX06 | SIO1 | SLC02 | 2 | 3 | 0 | 0 | CPU |  | 1059305 | Type 4 | 3 | [9 empty] | BR4-2150-E-00172 | 0
BCV131 | AX06 | SIO1 | SLC02 | 2 | 3 | 0 | 1 | 1 | I1 | 1044125 | SDI | 3 | BCV131PWS15 | PWS15A |  | Pullwire Switch 15 ChA | Healthy |  | BCV131 |  | 2.3\0.1:1 | BR4-2150-E-00172 | 0
BCV131 | AX06 | SIO1 | SLC02 | 2 | 3 | 0 | 1 | 2 | I2 | 1047162 | SDI | 3 | BCV131PWS15 | PWS15B |  | Pullwire Switch 15 ChB | Healthy |  | BCV131 |  | 2.3\0.1:2 | BR4-2150-E-00172 | 0
BCV131 | AX06 | SIO1 | SLC02 | 2 | 3 | 0 | 1 | 3 | I3 |  | SDI | 3 | BCV131PWS16 | PWS16A |  | Pullwire Switch 16 ChA | Healthy |  | BCV131 |  | 2.3\0.1:3 | BR4-2150-E-00172 | 0
BCV131 | AX06 | SIO1 | SLC02 | 2 | 3 | 0 | 1 | 4 | I4 |  | SDI | 3 | BCV131PWS16 | PWS16B |  | Pullwire Switch 16 ChB | Healthy |  | BCV131 |  | 2.3\0.1:4 | BR4-2150-E-00172 | 0
BCV131 | AX06 | SIO1 | SLC02 | 2 | 3 | 0 | 1 | 5 | I5 |  | SDI | 3 | [8 empty] | 2.3\0.1:5 | BR4-2150-E-00172 | 0
BCV131 | AX06 | SIO1 | SLC02 | 2 | 3 | 0 | 1 | 6 | I6 |  | SDI | 3 | [8 empty] | 2.3\0.1:6 | BR4-2150-E-00172 | 0
BCV131 | AX06 | SIO1 | SLC02 | 2 | 3 | 0 | 1 | 7 | I7 |  | SDI | 3 | [8 empty] | 2.3\0.1:7 | BR4-2150-E-00172 | 0
BCV131 | AX06 | SIO1 | SLC02 | 2 | 3 | 0 | 1 | 8 | I8 |  | SDI | 3 | [8 empty] | 2.3\0.1:8 | BR4-2150-E-00172 | 0
BCV131 | AX06 | SIO1 | SLC02 | 2 | 3 | 0 | 1 | 1 | Q1 | XTIO-Q | SDO | 3 | BCV131YA11 | YL11 |  | Start Up Warning (Beacon) | Active |  | BCV131 |  | 2.3\0.1:1 | BR4-2150-E-00172 | 0
BCV131 | AX06 | SIO1 | SLC02 | 2 | 3 | 0 | 1 | 2 | Q2 |  | SDO | 3 | BCV131YA11 | YA11 |  | Start Up Warning (Siren) | Active |  | BCV131 |  | 2.3\0.1:2 | BR4-2150-E-00172 | 0
BCV131 | AX06 | SIO1 | SLC02 | 2 | 3 | 0 | 1 | 3 | Q3 |  | SDO | 3 | BCV131YA12 | YA12 |  | Start Up Warning (Siren) | Active |  | BCV131 |  | 2.3\0.1:3 | BR4-2150-E-00172 | 0
BCV131 | AX06 | SIO1 | SLC02 | 2 | 3 | 0 | 1 | 4 | Q4 |  | SDO | 3 | [8 empty] | 2.3\0.1:4 | BR4-2150-E-00172 | 0
BCV131AX07 - BCV131 - 6523m
BCV131 | AX07 | SIO1 | SLC01 | 1 | 4 | 0 | 0 | CPU |  | 1059305 | Type 4 | 3 | [9 empty] | BR4-2150-E-00173 | 0
BCV131 | AX07 | SIO1 | SLC01 | 1 | 4 | 0 | 1 | 1 | I1 | 1044125 | SDI | 3 | BCV131PWS17 | PWS17A |  | Pullwire Switch 17 ChA | Healthy |  | BCV131 |  | 1.4\0.1:1 | BR4-2150-E-00173 | 0
BCV131 | AX07 | SIO1 | SLC01 | 1 | 4 | 0 | 1 | 2 | I2 | 1047162 | SDI | 3 | BCV131PWS17 | PWS17B |  | Pullwire Switch 17 ChB | Healthy |  | BCV131 |  | 1.4\0.1:2 | BR4-2150-E-00173 | 0
BCV131 | AX07 | SIO1 | SLC01 | 1 | 4 | 0 | 1 | 3 | I3 |  | SDI | 3 | BCV131PWS18 | PWS18A |  | Pullwire Switch 18 ChA | Healthy |  | BCV131 |  | 1.4\0.1:3 | BR4-2150-E-00173 | 0
BCV131 | AX07 | SIO1 | SLC01 | 1 | 4 | 0 | 1 | 4 | I4 |  | SDI | 3 | BCV131PWS18 | PWS18B |  | Pullwire Switch 18 ChB | Healthy |  | BCV131 |  | 1.4\0.1:4 | BR4-2150-E-00173 | 0
BCV131 | AX07 | SIO1 | SLC01 | 1 | 4 | 0 | 1 | 5 | I5 |  | SDI | 3 | [8 empty] | 1.4\0.1:5 | BR4-2150-E-00173 | 0
BCV131 | AX07 | SIO1 | SLC01 | 1 | 4 | 0 | 1 | 6 | I6 |  | SDI | 3 | [8 empty] | 1.4\0.1:6 | BR4-2150-E-00173 | 0
BCV131 | AX07 | SIO1 | SLC01 | 1 | 4 | 0 | 1 | 7 | I7 |  | SDI | 3 | [8 empty] | 1.4\0.1:7 | BR4-2150-E-00173 | 0
BCV131 | AX07 | SIO1 | SLC01 | 1 | 4 | 0 | 1 | 8 | I8 |  | SDI | 3 | [8 empty] | 1.4\0.1:8 | BR4-2150-E-00173 | 0
BCV131 | AX07 | SIO1 | SLC01 | 1 | 4 | 0 | 1 | 1 | Q1 | XTIO-Q | SDO | 3 | BCV131YA13 | YL13 |  | Start Up Warning (Beacon) | Active |  | BCV131 |  | 1.4\0.1:1 | BR4-2150-E-00173 | 0
BCV131 | AX07 | SIO1 | SLC01 | 1 | 4 | 0 | 1 | 2 | Q2 |  | SDO | 3 | BCV131YA13 | YA13 |  | Start Up Warning (Siren) | Active |  | BCV131 |  | 1.4\0.1:2 | BR4-2150-E-00173 | 0
BCV131 | AX07 | SIO1 | SLC01 | 1 | 4 | 0 | 1 | 3 | Q3 |  | SDO | 3 | BCV131YA14 | YA14 |  | Start Up Warning (Siren) | Active |  | BCV131 |  | 1.4\0.1:3 | BR4-2150-E-00173 | 0
BCV131 | AX07 | SIO1 | SLC01 | 1 | 4 | 0 | 1 | 4 | Q4 |  | SDO | 3 | [8 empty] | 1.4\0.1:4 | BR4-2150-E-00173 | 0
BCV131AX08 - BCV131 - 6333m
BCV131 | AX08 | SIO1 | SLC02 | 2 | 4 | 0 | 0 | CPU |  | 1059305 | Type 4 | 3 | [9 empty] | BR4-2150-E-00174 | 0
BCV131 | AX08 | SIO1 | SLC02 | 2 | 4 | 0 | 1 | 1 | I1 | 1044125 | SDI | 3 | BCV131PWS19 | PWS19A |  | Pullwire Switch 19 ChA | Healthy |  | BCV131 |  | 2.4\0.1:1 | BR4-2150-E-00174 | 0
BCV131 | AX08 | SIO1 | SLC02 | 2 | 4 | 0 | 1 | 2 | I2 | 1047162 | SDI | 3 | BCV131PWS19 | PWS19B |  | Pullwire Switch 19 ChB | Healthy |  | BCV131 |  | 2.4\0.1:2 | BR4-2150-E-00174 | 0
BCV131 | AX08 | SIO1 | SLC02 | 2 | 4 | 0 | 1 | 3 | I3 |  | SDI | 3 | BCV131PWS20 | PWS20A |  | Pullwire Switch 20 ChA | Healthy |  | BCV131 |  | 2.4\0.1:3 | BR4-2150-E-00174 | 0
BCV131 | AX08 | SIO1 | SLC02 | 2 | 4 | 0 | 1 | 4 | I4 |  | SDI | 3 | BCV131PWS20 | PWS20B |  | Pullwire Switch 20 ChB | Healthy |  | BCV131 |  | 2.4\0.1:4 | BR4-2150-E-00174 | 0
BCV131 | AX08 | SIO1 | SLC02 | 2 | 4 | 0 | 1 | 5 | I5 |  | SDI | 3 | [8 empty] | 2.4\0.1:5 | BR4-2150-E-00174 | 0
BCV131 | AX08 | SIO1 | SLC02 | 2 | 4 | 0 | 1 | 6 | I6 |  | SDI | 3 | [8 empty] | 2.4\0.1:6 | BR4-2150-E-00174 | 0
BCV131 | AX08 | SIO1 | SLC02 | 2 | 4 | 0 | 1 | 7 | I7 |  | SDI | 3 | [8 empty] | 2.4\0.1:7 | BR4-2150-E-00174 | 0
BCV131 | AX08 | SIO1 | SLC02 | 2 | 4 | 0 | 1 | 8 | I8 |  | SDI | 3 | [8 empty] | 2.4\0.1:8 | BR4-2150-E-00174 | 0
BCV131 | AX08 | SIO1 | SLC02 | 2 | 4 | 0 | 1 | 1 | Q1 | XTIO-Q | SDO | 3 | BCV131YA15 | YL15 |  | Start Up Warning (Beacon) | Active |  | BCV131 |  | 2.4\0.1:1 | BR4-2150-E-00174 | 0
BCV131 | AX08 | SIO1 | SLC02 | 2 | 4 | 0 | 1 | 2 | Q2 |  | SDO | 3 | BCV131YA15 | YA15 |  | Start Up Warning (Siren) | Active |  | BCV131 |  | 2.4\0.1:2 | BR4-2150-E-00174 | 0
BCV131 | AX08 | SIO1 | SLC02 | 2 | 4 | 0 | 1 | 3 | Q3 |  | SDO | 3 | BCV131YA16 | YA16 |  | Start Up Warning (Siren) | Active |  | BCV131 |  | 2.4\0.1:3 | BR4-2150-E-00174 | 0
BCV131 | AX08 | SIO1 | SLC02 | 2 | 4 | 0 | 1 | 4 | Q4 |  | SDO | 3 | [8 empty] | 2.4\0.1:4 | BR4-2150-E-00174 | 0
BCV131AX09 - BCV131 - 6143m
BCV131 | AX09 | SIO1 | SLC01 | 1 | 5 | 0 | 0 | CPU |  | 1059305 | Type 4 | 3 | [9 empty] | BR4-2150-E-00175 | 0
BCV131 | AX09 | SIO1 | SLC01 | 1 | 5 | 0 | 1 | 1 | I1 | 1044125 | SDI | 3 | BCV131PWS21 | PWS21A |  | Pullwire Switch 21 ChA | Healthy |  | BCV131 |  | 1.5\0.1:1 | BR4-2150-E-00175 | 0
BCV131 | AX09 | SIO1 | SLC01 | 1 | 5 | 0 | 1 | 2 | I2 | 1047162 | SDI | 3 | BCV131PWS21 | PWS21B |  | Pullwire Switch 21 ChB | Healthy |  | BCV131 |  | 1.5\0.1:2 | BR4-2150-E-00175 | 0
BCV131 | AX09 | SIO1 | SLC01 | 1 | 5 | 0 | 1 | 3 | I3 |  | SDI | 3 | BCV131PWS22 | PWS22A |  | Pullwire Switch 22 ChA | Healthy |  | BCV131 |  | 1.5\0.1:3 | BR4-2150-E-00175 | 0
BCV131 | AX09 | SIO1 | SLC01 | 1 | 5 | 0 | 1 | 4 | I4 |  | SDI | 3 | BCV131PWS22 | PWS22B |  | Pullwire Switch 22 ChB | Healthy |  | BCV131 |  | 1.5\0.1:4 | BR4-2150-E-00175 | 0
BCV131 | AX09 | SIO1 | SLC01 | 1 | 5 | 0 | 1 | 5 | I5 |  | SDI | 3 | [8 empty] | 1.5\0.1:5 | BR4-2150-E-00175 | 0
BCV131 | AX09 | SIO1 | SLC01 | 1 | 5 | 0 | 1 | 6 | I6 |  | SDI | 3 | [8 empty] | 1.5\0.1:6 | BR4-2150-E-00175 | 0
BCV131 | AX09 | SIO1 | SLC01 | 1 | 5 | 0 | 1 | 7 | I7 |  | SDI | 3 | [8 empty] | 1.5\0.1:7 | BR4-2150-E-00175 | 0
BCV131 | AX09 | SIO1 | SLC01 | 1 | 5 | 0 | 1 | 8 | I8 |  | SDI | 3 | [8 empty] | 1.5\0.1:8 | BR4-2150-E-00175 | 0
BCV131 | AX09 | SIO1 | SLC01 | 1 | 5 | 0 | 1 | 1 | Q1 | XTIO-Q | SDO | 3 | BCV131YA17 | YL17 |  | Start Up Warning (Beacon) | Active |  | BCV131 |  | 1.5\0.1:1 | BR4-2150-E-00175 | 0
BCV131 | AX09 | SIO1 | SLC01 | 1 | 5 | 0 | 1 | 2 | Q2 |  | SDO | 3 | BCV131YA17 | YA17 |  | Start Up Warning (Siren) | Active |  | BCV131 |  | 1.5\0.1:2 | BR4-2150-E-00175 | 0
BCV131 | AX09 | SIO1 | SLC01 | 1 | 5 | 0 | 1 | 3 | Q3 |  | SDO | 3 | BCV131YA18 | YA18 |  | Start Up Warning (Siren) | Active |  | BCV131 |  | 1.5\0.1:3 | BR4-2150-E-00175 | 0
BCV131 | AX09 | SIO1 | SLC01 | 1 | 5 | 0 | 1 | 4 | Q4 |  | SDO | 3 | [8 empty] | 1.5\0.1:4 | BR4-2150-E-00175 | 0
BCV131AX10 - BCV131 - 5953m
BCV131 | AX10 | SIO1 | SLC02 | 2 | 5 | 0 | 0 | CPU |  | 1059305 | Type 4 | 3 | [9 empty] | BR4-2150-E-00176 | 0
BCV131 | AX10 | SIO1 | SLC02 | 2 | 5 | 0 | 1 | 1 | I1 | 1044125 | SDI | 3 | BCV131PWS23 | PWS23A |  | Pullwire Switch 23 ChA | Healthy |  | BCV131 |  | 2.5\0.1:1 | BR4-2150-E-00176 | 0
BCV131 | AX10 | SIO1 | SLC02 | 2 | 5 | 0 | 1 | 2 | I2 | 1047162 | SDI | 3 | BCV131PWS23 | PWS23B |  | Pullwire Switch 23 ChB | Healthy |  | BCV131 |  | 2.5\0.1:2 | BR4-2150-E-00176 | 0
BCV131 | AX10 | SIO1 | SLC02 | 2 | 5 | 0 | 1 | 3 | I3 |  | SDI | 3 | BCV131PWS24 | PWS24A |  | Pullwire Switch 24 ChA | Healthy |  | BCV131 |  | 2.5\0.1:3 | BR4-2150-E-00176 | 0
BCV131 | AX10 | SIO1 | SLC02 | 2 | 5 | 0 | 1 | 4 | I4 |  | SDI | 3 | BCV131PWS24 | PWS24B |  | Pullwire Switch 24 ChB | Healthy |  | BCV131 |  | 2.5\0.1:4 | BR4-2150-E-00176 | 0
BCV131 | AX10 | SIO1 | SLC02 | 2 | 5 | 0 | 1 | 5 | I5 |  | SDI | 3 | [8 empty] | 2.5\0.1:5 | BR4-2150-E-00176 | 0
BCV131 | AX10 | SIO1 | SLC02 | 2 | 5 | 0 | 1 | 6 | I6 |  | SDI | 3 | [8 empty] | 2.5\0.1:6 | BR4-2150-E-00176 | 0
BCV131 | AX10 | SIO1 | SLC02 | 2 | 5 | 0 | 1 | 7 | I7 |  | SDI | 3 | [8 empty] | 2.5\0.1:7 | BR4-2150-E-00176 | 0
BCV131 | AX10 | SIO1 | SLC02 | 2 | 5 | 0 | 1 | 8 | I8 |  | SDI | 3 | [8 empty] | 2.5\0.1:8 | BR4-2150-E-00176 | 0
BCV131 | AX10 | SIO1 | SLC02 | 2 | 5 | 0 | 1 | 1 | Q1 | XTIO-Q | SDO | 3 | BCV131YA19 | YL19 |  | Start Up Warning (Beacon) | Active |  | BCV131 |  | 2.5\0.1:1 | BR4-2150-E-00176 | 0
BCV131 | AX10 | SIO1 | SLC02 | 2 | 5 | 0 | 1 | 2 | Q2 |  | SDO | 3 | BCV131YA19 | YA19 |  | Start Up Warning (Siren) | Active |  | BCV131 |  | 2.5\0.1:2 | BR4-2150-E-00176 | 0
BCV131 | AX10 | SIO1 | SLC02 | 2 | 5 | 0 | 1 | 3 | Q3 |  | SDO | 3 | BCV131YA20 | YA20 |  | Start Up Warning (Siren) | Active |  | BCV131 |  | 2.5\0.1:3 | BR4-2150-E-00176 | 0
BCV131 | AX10 | SIO1 | SLC02 | 2 | 5 | 0 | 1 | 4 | Q4 |  | SDO | 3 | [8 empty] | 2.5\0.1:4 | BR4-2150-E-00176 | 0
BCV131AX11 - BCV131 - 5710m
BCV131 | AX11 | SIO1 | SLC01 | 1 | 6 | 0 | 0 | CPU |  | 1059305 | Type 4 | 3 | [9 empty] | BR4-2150-E-00177 | 0
BCV131 | AX11 | SIO1 | SLC01 | 1 | 6 | 0 | 1 | 1 | I1 | 1044125 | SDI | 3 | BCV131PWS25 | PWS25A |  | Pullwire Switch 25 ChA | Healthy |  | BCV131 |  | 1.6\0.1:1 | BR4-2150-E-00177 | 0
BCV131 | AX11 | SIO1 | SLC01 | 1 | 6 | 0 | 1 | 2 | I2 | 1047162 | SDI | 3 | BCV131PWS25 | PWS25B |  | Pullwire Switch 25 ChB | Healthy |  | BCV131 |  | 1.6\0.1:2 | BR4-2150-E-00177 | 0
BCV131 | AX11 | SIO1 | SLC01 | 1 | 6 | 0 | 1 | 3 | I3 |  | SDI | 3 | BCV131PWS26 | PWS26A |  | Pullwire Switch 26 ChA | Healthy |  | BCV131 |  | 1.6\0.1:3 | BR4-2150-E-00177 | 0
BCV131 | AX11 | SIO1 | SLC01 | 1 | 6 | 0 | 1 | 4 | I4 |  | SDI | 3 | BCV131PWS26 | PWS26B |  | Pullwire Switch 26 ChB | Healthy |  | BCV131 |  | 1.6\0.1:4 | BR4-2150-E-00177 | 0
BCV131 | AX11 | SIO1 | SLC01 | 1 | 6 | 0 | 1 | 5 | I5 |  | SDI | 3 | [8 empty] | 1.6\0.1:5 | BR4-2150-E-00177 | 0
BCV131 | AX11 | SIO1 | SLC01 | 1 | 6 | 0 | 1 | 6 | I6 |  | SDI | 3 | [8 empty] | 1.6\0.1:6 | BR4-2150-E-00177 | 0
BCV131 | AX11 | SIO1 | SLC01 | 1 | 6 | 0 | 1 | 7 | I7 |  | SDI | 3 | [8 empty] | 1.6\0.1:7 | BR4-2150-E-00177 | 0
BCV131 | AX11 | SIO1 | SLC01 | 1 | 6 | 0 | 1 | 8 | I8 |  | SDI | 3 | [8 empty] | 1.6\0.1:8 | BR4-2150-E-00177 | 0
BCV131 | AX11 | SIO1 | SLC01 | 1 | 6 | 0 | 1 | 1 | Q1 | XTIO-Q | SDO | 3 | BCV131YA21 | YL21 |  | Start Up Warning (Beacon) | Active |  | BCV131 |  | 1.6\0.1:1 | BR4-2150-E-00177 | 0
BCV131 | AX11 | SIO1 | SLC01 | 1 | 6 | 0 | 1 | 2 | Q2 |  | SDO | 3 | BCV131YA21 | YA21 |  | Start Up Warning (Siren) | Active |  | BCV131 |  | 1.6\0.1:2 | BR4-2150-E-00177 | 0
BCV131 | AX11 | SIO1 | SLC01 | 1 | 6 | 0 | 1 | 3 | Q3 |  | SDO | 3 | BCV131YA22 | YA22 |  | Start Up Warning (Siren) | Active |  | BCV131 |  | 1.6\0.1:3 | BR4-2150-E-00177 | 0
BCV131 | AX11 | SIO1 | SLC01 | 1 | 6 | 0 | 1 | 4 | Q4 |  | SDO | 3 | [8 empty] | 1.6\0.1:4 | BR4-2150-E-00177 | 0
BCV131AX12 - BCV131 - 5467m
BCV131 | AX12 | SIO1 | SLC02 | 2 | 6 | 0 | 0 | CPU |  | 1059305 | Type 4 | 3 | [9 empty] | BR4-2150-E-00178 | 0
BCV131 | AX12 | SIO1 | SLC02 | 2 | 6 | 0 | 1 | 1 | I1 | 1044125 | SDI | 3 | BCV131PWS27 | PWS27A |  | Pullwire Switch 27 ChA | Healthy |  | BCV131 |  | 2.6\0.1:1 | BR4-2150-E-00178 | 0
BCV131 | AX12 | SIO1 | SLC02 | 2 | 6 | 0 | 1 | 2 | I2 | 1047162 | SDI | 3 | BCV131PWS27 | PWS27B |  | Pullwire Switch 27 ChB | Healthy |  | BCV131 |  | 2.6\0.1:2 | BR4-2150-E-00178 | 0
BCV131 | AX12 | SIO1 | SLC02 | 2 | 6 | 0 | 1 | 3 | I3 |  | SDI | 3 | BCV131PWS28 | PWS28A |  | Pullwire Switch 28 ChA | Healthy |  | BCV131 |  | 2.6\0.1:3 | BR4-2150-E-00178 | 0
BCV131 | AX12 | SIO1 | SLC02 | 2 | 6 | 0 | 1 | 4 | I4 |  | SDI | 3 | BCV131PWS28 | PWS28B |  | Pullwire Switch 28 ChB | Healthy |  | BCV131 |  | 2.6\0.1:4 | BR4-2150-E-00178 | 0
BCV131 | AX12 | SIO1 | SLC02 | 2 | 6 | 0 | 1 | 5 | I5 |  | SDI | 3 | [8 empty] | 2.6\0.1:5 | BR4-2150-E-00178 | 0
BCV131 | AX12 | SIO1 | SLC02 | 2 | 6 | 0 | 1 | 6 | I6 |  | SDI | 3 | [8 empty] | 2.6\0.1:6 | BR4-2150-E-00178 | 0
BCV131 | AX12 | SIO1 | SLC02 | 2 | 6 | 0 | 1 | 7 | I7 |  | SDI | 3 | [8 empty] | 2.6\0.1:7 | BR4-2150-E-00178 | 0
BCV131 | AX12 | SIO1 | SLC02 | 2 | 6 | 0 | 1 | 8 | I8 |  | SDI | 3 | [8 empty] | 2.6\0.1:8 | BR4-2150-E-00178 | 0
BCV131 | AX12 | SIO1 | SLC02 | 2 | 6 | 0 | 1 | 1 | Q1 | XTIO-Q | SDO | 3 | BCV131YA23 | YL23 |  | Start Up Warning (Beacon) | Active |  | BCV131 |  | 2.6\0.1:1 | BR4-2150-E-00178 | 0
BCV131 | AX12 | SIO1 | SLC02 | 2 | 6 | 0 | 1 | 2 | Q2 |  | SDO | 3 | BCV131YA23 | YA23 |  | Start Up Warning (Siren) | Active |  | BCV131 |  | 2.6\0.1:2 | BR4-2150-E-00178 | 0
BCV131 | AX12 | SIO1 | SLC02 | 2 | 6 | 0 | 1 | 3 | Q3 |  | SDO | 3 | BCV131YA24 | YA24 |  | Start Up Warning (Siren) | Active |  | BCV131 |  | 2.6\0.1:3 | BR4-2150-E-00178 | 0
BCV131 | AX12 | SIO1 | SLC02 | 2 | 6 | 0 | 1 | 4 | Q4 |  | SDO | 3 | [8 empty] | 2.6\0.1:4 | BR4-2150-E-00178 | 0
BCV131AX13 - BCV131 - 5224m
BCV131 | AX13 | SIO1 | SLC01 | 1 | 7 | 0 | 0 | CPU |  | 1059305 | Type 4 | 3 | [9 empty] | BR4-2150-E-00179 | 0
BCV131 | AX13 | SIO1 | SLC01 | 1 | 7 | 0 | 1 | 1 | I1 | 1044125 | SDI | 3 | BCV131PWS29 | PWS29A |  | Pullwire Switch 29 ChA | Healthy |  | BCV131 |  | 1.7\0.1:1 | BR4-2150-E-00179 | 0
BCV131 | AX13 | SIO1 | SLC01 | 1 | 7 | 0 | 1 | 2 | I2 | 1047162 | SDI | 3 | BCV131PWS29 | PWS29B |  | Pullwire Switch 29 ChB | Healthy |  | BCV131 |  | 1.7\0.1:2 | BR4-2150-E-00179 | 0
BCV131 | AX13 | SIO1 | SLC01 | 1 | 7 | 0 | 1 | 3 | I3 |  | SDI | 3 | BCV131PWS30 | PWS30A |  | Pullwire Switch 30 ChA | Healthy |  | BCV131 |  | 1.7\0.1:3 | BR4-2150-E-00179 | 0
BCV131 | AX13 | SIO1 | SLC01 | 1 | 7 | 0 | 1 | 4 | I4 |  | SDI | 3 | BCV131PWS30 | PWS30B |  | Pullwire Switch 30 ChB | Healthy |  | BCV131 |  | 1.7\0.1:4 | BR4-2150-E-00179 | 0
BCV131 | AX13 | SIO1 | SLC01 | 1 | 7 | 0 | 1 | 5 | I5 |  | SDI | 3 | [8 empty] | 1.7\0.1:5 | BR4-2150-E-00179 | 0
BCV131 | AX13 | SIO1 | SLC01 | 1 | 7 | 0 | 1 | 6 | I6 |  | SDI | 3 | [8 empty] | 1.7\0.1:6 | BR4-2150-E-00179 | 0
BCV131 | AX13 | SIO1 | SLC01 | 1 | 7 | 0 | 1 | 7 | I7 |  | SDI | 3 | [8 empty] | 1.7\0.1:7 | BR4-2150-E-00179 | 0
BCV131 | AX13 | SIO1 | SLC01 | 1 | 7 | 0 | 1 | 8 | I8 |  | SDI | 3 | [8 empty] | 1.7\0.1:8 | BR4-2150-E-00179 | 0
BCV131 | AX13 | SIO1 | SLC01 | 1 | 7 | 0 | 1 | 1 | Q1 | XTIO-Q | SDO | 3 | BCV131YA25 | YL25 |  | Start Up Warning (Beacon) | Active |  | BCV131 |  | 1.7\0.1:1 | BR4-2150-E-00179 | 0
BCV131 | AX13 | SIO1 | SLC01 | 1 | 7 | 0 | 1 | 2 | Q2 |  | SDO | 3 | BCV131YA25 | YA25 |  | Start Up Warning (Siren) | Active |  | BCV131 |  | 1.7\0.1:2 | BR4-2150-E-00179 | 0
BCV131 | AX13 | SIO1 | SLC01 | 1 | 7 | 0 | 1 | 3 | Q3 |  | SDO | 3 | BCV131YA26 | YA26 |  | Start Up Warning (Siren) | Active |  | BCV131 |  | 1.7\0.1:3 | BR4-2150-E-00179 | 0
BCV131 | AX13 | SIO1 | SLC01 | 1 | 7 | 0 | 1 | 4 | Q4 |  | SDO | 3 | [8 empty] | 1.7\0.1:4 | BR4-2150-E-00179 | 0
BCV131AX14 - BCV131 - 4981m
BCV131 | AX14 | SIO1 | SLC02 | 2 | 7 | 0 | 0 | CPU |  | 1059305 | Type 4 | 3 | [9 empty] | BR4-2150-E-00180 | 0
BCV131 | AX14 | SIO1 | SLC02 | 2 | 7 | 0 | 1 | 1 | I1 | 1044125 | SDI | 3 | BCV131PWS31 | PWS31A |  | Pullwire Switch 31 ChA | Healthy |  | BCV131 |  | 2.7\0.1:1 | BR4-2150-E-00180 | 0
BCV131 | AX14 | SIO1 | SLC02 | 2 | 7 | 0 | 1 | 2 | I2 | 1047162 | SDI | 3 | BCV131PWS31 | PWS31B |  | Pullwire Switch 31 ChB | Healthy |  | BCV131 |  | 2.7\0.1:2 | BR4-2150-E-00180 | 0
BCV131 | AX14 | SIO1 | SLC02 | 2 | 7 | 0 | 1 | 3 | I3 |  | SDI | 3 | BCV131PWS32 | PWS32A |  | Pullwire Switch 32 ChA | Healthy |  | BCV131 |  | 2.7\0.1:3 | BR4-2150-E-00180 | 0
BCV131 | AX14 | SIO1 | SLC02 | 2 | 7 | 0 | 1 | 4 | I4 |  | SDI | 3 | BCV131PWS32 | PWS32B |  | Pullwire Switch 32 ChB | Healthy |  | BCV131 |  | 2.7\0.1:4 | BR4-2150-E-00180 | 0
BCV131 | AX14 | SIO1 | SLC02 | 2 | 7 | 0 | 1 | 5 | I5 |  | SDI | 3 | [8 empty] | 2.7\0.1:5 | BR4-2150-E-00180 | 0
BCV131 | AX14 | SIO1 | SLC02 | 2 | 7 | 0 | 1 | 6 | I6 |  | SDI | 3 | [8 empty] | 2.7\0.1:6 | BR4-2150-E-00180 | 0
BCV131 | AX14 | SIO1 | SLC02 | 2 | 7 | 0 | 1 | 7 | I7 |  | SDI | 3 | [8 empty] | 2.7\0.1:7 | BR4-2150-E-00180 | 0
BCV131 | AX14 | SIO1 | SLC02 | 2 | 7 | 0 | 1 | 8 | I8 |  | SDI | 3 | [8 empty] | 2.7\0.1:8 | BR4-2150-E-00180 | 0
BCV131 | AX14 | SIO1 | SLC02 | 2 | 7 | 0 | 1 | 1 | Q1 | XTIO-Q | SDO | 3 | BCV131YA27 | YL27 |  | Start Up Warning (Beacon) | Active |  | BCV131 |  | 2.7\0.1:1 | BR4-2150-E-00180 | 0
BCV131 | AX14 | SIO1 | SLC02 | 2 | 7 | 0 | 1 | 2 | Q2 |  | SDO | 3 | BCV131YA27 | YA27 |  | Start Up Warning (Siren) | Active |  | BCV131 |  | 2.7\0.1:2 | BR4-2150-E-00180 | 0
BCV131 | AX14 | SIO1 | SLC02 | 2 | 7 | 0 | 1 | 3 | Q3 |  | SDO | 3 | BCV131YA28 | YA28 |  | Start Up Warning (Siren) | Active |  | BCV131 |  | 2.7\0.1:3 | BR4-2150-E-00180 | 0
BCV131 | AX14 | SIO1 | SLC02 | 2 | 7 | 0 | 1 | 4 | Q4 |  | SDO | 3 | [8 empty] | 2.7\0.1:4 | BR4-2150-E-00180 | 0
BCV131AX15 - BCV131 - 4738m
BCV131 | AX15 | SIO1 | SLC01 | 1 | 8 | 0 | 0 | CPU |  | 1059305 | Type 4 | 3 | [9 empty] | BR4-2150-E-00181 | 0
BCV131 | AX15 | SIO1 | SLC01 | 1 | 8 | 0 | 1 | 1 | I1 | 1044125 | SDI | 3 | BCV131PWS33 | PWS33A |  | Pullwire Switch 33 ChA | Healthy |  | BCV131 |  | 1.8\0.1:1 | BR4-2150-E-00181 | 0
BCV131 | AX15 | SIO1 | SLC01 | 1 | 8 | 0 | 1 | 2 | I2 | 1047162 | SDI | 3 | BCV131PWS33 | PWS33B |  | Pullwire Switch 33 ChB | Healthy |  | BCV131 |  | 1.8\0.1:2 | BR4-2150-E-00181 | 0
BCV131 | AX15 | SIO1 | SLC01 | 1 | 8 | 0 | 1 | 3 | I3 |  | SDI | 3 | BCV131PWS34 | PWS34A |  | Pullwire Switch 34 ChA | Healthy |  | BCV131 |  | 1.8\0.1:3 | BR4-2150-E-00181 | 0
BCV131 | AX15 | SIO1 | SLC01 | 1 | 8 | 0 | 1 | 4 | I4 |  | SDI | 3 | BCV131PWS34 | PWS34B |  | Pullwire Switch 34 ChB | Healthy |  | BCV131 |  | 1.8\0.1:4 | BR4-2150-E-00181 | 0
BCV131 | AX15 | SIO1 | SLC01 | 1 | 8 | 0 | 1 | 5 | I5 |  | SDI | 3 | [8 empty] | 1.8\0.1:5 | BR4-2150-E-00181 | 0
BCV131 | AX15 | SIO1 | SLC01 | 1 | 8 | 0 | 1 | 6 | I6 |  | SDI | 3 | [8 empty] | 1.8\0.1:6 | BR4-2150-E-00181 | 0
BCV131 | AX15 | SIO1 | SLC01 | 1 | 8 | 0 | 1 | 7 | I7 |  | SDI | 3 | [8 empty] | 1.8\0.1:7 | BR4-2150-E-00181 | 0
BCV131 | AX15 | SIO1 | SLC01 | 1 | 8 | 0 | 1 | 8 | I8 |  | SDI | 3 | [8 empty] | 1.8\0.1:8 | BR4-2150-E-00181 | 0
BCV131 | AX15 | SIO1 | SLC01 | 1 | 8 | 0 | 1 | 1 | Q1 | XTIO-Q | SDO | 3 | BCV131YA29 | YL29 |  | Start Up Warning (Beacon) | Active |  | BCV131 |  | 1.8\0.1:1 | BR4-2150-E-00181 | 0
BCV131 | AX15 | SIO1 | SLC01 | 1 | 8 | 0 | 1 | 2 | Q2 |  | SDO | 3 | BCV131YA29 | YA29 |  | Start Up Warning (Siren) | Active |  | BCV131 |  | 1.8\0.1:2 | BR4-2150-E-00181 | 0
BCV131 | AX15 | SIO1 | SLC01 | 1 | 8 | 0 | 1 | 3 | Q3 |  | SDO | 3 | BCV131YA30 | YA30 |  | Start Up Warning (Siren) | Active |  | BCV131 |  | 1.8\0.1:3 | BR4-2150-E-00181 | 0
BCV131 | AX15 | SIO1 | SLC01 | 1 | 8 | 0 | 1 | 4 | Q4 |  | SDO | 3 | [8 empty] | 1.8\0.1:4 | BR4-2150-E-00181 | 0
BCV131AX16 - BCV131 - 4495m
BCV131 | AX16 | SIO1 | SLC02 | 2 | 8 | 0 | 0 | CPU |  | 1059305 | Type 4 | 3 | [9 empty] | BR4-2150-E-00182 | 0
BCV131 | AX16 | SIO1 | SLC02 | 2 | 8 | 0 | 1 | 1 | I1 | 1044125 | SDI | 3 | BCV131PWS35 | PWS35A |  | Pullwire Switch 35 ChA | Healthy |  | BCV131 |  | 2.8\0.1:1 | BR4-2150-E-00182 | 0
BCV131 | AX16 | SIO1 | SLC02 | 2 | 8 | 0 | 1 | 2 | I2 | 1047162 | SDI | 3 | BCV131PWS35 | PWS35B |  | Pullwire Switch 35 ChB | Healthy |  | BCV131 |  | 2.8\0.1:2 | BR4-2150-E-00182 | 0
BCV131 | AX16 | SIO1 | SLC02 | 2 | 8 | 0 | 1 | 3 | I3 |  | SDI | 3 | BCV131PWS36 | PWS36A |  | Pullwire Switch 36 ChA | Healthy |  | BCV131 |  | 2.8\0.1:3 | BR4-2150-E-00182 | 0
BCV131 | AX16 | SIO1 | SLC02 | 2 | 8 | 0 | 1 | 4 | I4 |  | SDI | 3 | BCV131PWS36 | PWS36B |  | Pullwire Switch 36 ChB | Healthy |  | BCV131 |  | 2.8\0.1:4 | BR4-2150-E-00182 | 0
BCV131 | AX16 | SIO1 | SLC02 | 2 | 8 | 0 | 1 | 5 | I5 |  | SDI | 3 | [8 empty] | 2.8\0.1:5 | BR4-2150-E-00182 | 0
BCV131 | AX16 | SIO1 | SLC02 | 2 | 8 | 0 | 1 | 6 | I6 |  | SDI | 3 | [8 empty] | 2.8\0.1:6 | BR4-2150-E-00182 | 0
BCV131 | AX16 | SIO1 | SLC02 | 2 | 8 | 0 | 1 | 7 | I7 |  | SDI | 3 | [8 empty] | 2.8\0.1:7 | BR4-2150-E-00182 | 0
BCV131 | AX16 | SIO1 | SLC02 | 2 | 8 | 0 | 1 | 8 | I8 |  | SDI | 3 | [8 empty] | 2.8\0.1:8 | BR4-2150-E-00182 | 0
BCV131 | AX16 | SIO1 | SLC02 | 2 | 8 | 0 | 1 | 1 | Q1 | XTIO-Q | SDO | 3 | BCV131YA31 | YL31 |  | Start Up Warning (Beacon) | Active |  | BCV131 |  | 2.8\0.1:1 | BR4-2150-E-00182 | 0
BCV131 | AX16 | SIO1 | SLC02 | 2 | 8 | 0 | 1 | 2 | Q2 |  | SDO | 3 | BCV131YA31 | YA31 |  | Start Up Warning (Siren) | Active |  | BCV131 |  | 2.8\0.1:2 | BR4-2150-E-00182 | 0
BCV131 | AX16 | SIO1 | SLC02 | 2 | 8 | 0 | 1 | 3 | Q3 |  | SDO | 3 | BCV131YA32 | YA32 |  | Start Up Warning (Siren) | Active |  | BCV131 |  | 2.8\0.1:3 | BR4-2150-E-00182 | 0
BCV131 | AX16 | SIO1 | SLC02 | 2 | 8 | 0 | 1 | 4 | Q4 |  | SDO | 3 | [8 empty] | 2.8\0.1:4 | BR4-2150-E-00182 | 0
BCV131AX17 - BCV131 - 4252m
BCV131 | AX17 | SIO1 | SLC01 | 1 | 9 | 0 | 0 | CPU |  | 1059305 | Type 4 | 3 | [9 empty] | BR4-2150-E-00183 | 0
BCV131 | AX17 | SIO1 | SLC01 | 1 | 9 | 0 | 1 | 1 | I1 | 1044125 | SDI | 3 | BCV131PWS37 | PWS37A |  | Pullwire Switch 37 ChA | Healthy |  | BCV131 |  | 1.9\0.1:1 | BR4-2150-E-00183 | 0
BCV131 | AX17 | SIO1 | SLC01 | 1 | 9 | 0 | 1 | 2 | I2 | 1047162 | SDI | 3 | BCV131PWS37 | PWS37B |  | Pullwire Switch 37 ChB | Healthy |  | BCV131 |  | 1.9\0.1:2 | BR4-2150-E-00183 | 0
BCV131 | AX17 | SIO1 | SLC01 | 1 | 9 | 0 | 1 | 3 | I3 |  | SDI | 3 | BCV131PWS38 | PWS38A |  | Pullwire Switch 38 ChA | Healthy |  | BCV131 |  | 1.9\0.1:3 | BR4-2150-E-00183 | 0
BCV131 | AX17 | SIO1 | SLC01 | 1 | 9 | 0 | 1 | 4 | I4 |  | SDI | 3 | BCV131PWS38 | PWS38B |  | Pullwire Switch 38 ChB | Healthy |  | BCV131 |  | 1.9\0.1:4 | BR4-2150-E-00183 | 0
BCV131 | AX17 | SIO1 | SLC01 | 1 | 9 | 0 | 1 | 5 | I5 |  | SDI | 3 | [8 empty] | 1.9\0.1:5 | BR4-2150-E-00183 | 0
BCV131 | AX17 | SIO1 | SLC01 | 1 | 9 | 0 | 1 | 6 | I6 |  | SDI | 3 | [8 empty] | 1.9\0.1:6 | BR4-2150-E-00183 | 0
BCV131 | AX17 | SIO1 | SLC01 | 1 | 9 | 0 | 1 | 7 | I7 |  | SDI | 3 | [8 empty] | 1.9\0.1:7 | BR4-2150-E-00183 | 0
BCV131 | AX17 | SIO1 | SLC01 | 1 | 9 | 0 | 1 | 8 | I8 |  | SDI | 3 | [8 empty] | 1.9\0.1:8 | BR4-2150-E-00183 | 0
BCV131 | AX17 | SIO1 | SLC01 | 1 | 9 | 0 | 1 | 1 | Q1 | XTIO-Q | SDO | 3 | BCV131YA33 | YL33 |  | Start Up Warning (Beacon) | Active |  | BCV131 |  | 1.9\0.1:1 | BR4-2150-E-00183 | 0
BCV131 | AX17 | SIO1 | SLC01 | 1 | 9 | 0 | 1 | 2 | Q2 |  | SDO | 3 | BCV131YA33 | YA33 |  | Start Up Warning (Siren) | Active |  | BCV131 |  | 1.9\0.1:2 | BR4-2150-E-00183 | 0
BCV131 | AX17 | SIO1 | SLC01 | 1 | 9 | 0 | 1 | 3 | Q3 |  | SDO | 3 | BCV131YA34 | YA34 |  | Start Up Warning (Siren) | Active |  | BCV131 |  | 1.9\0.1:3 | BR4-2150-E-00183 | 0
BCV131 | AX17 | SIO1 | SLC01 | 1 | 9 | 0 | 1 | 4 | Q4 |  | SDO | 3 | [8 empty] | 1.9\0.1:4 | BR4-2150-E-00183 | 0
BCV131AX18 - BCV131 - 4009m
BCV131 | AX18 | SIO1 | SLC02 | 2 | 9 | 0 | 0 | CPU |  | 1059305 | Type 4 | 3 | [9 empty] | BR4-2150-E-00184 | 0
BCV131 | AX18 | SIO1 | SLC02 | 2 | 9 | 0 | 1 | 1 | I1 | 1044125 | SDI | 3 | BCV131PWS39 | PWS39A |  | Pullwire Switch 39 ChA | Healthy |  | BCV131 |  | 2.9\0.1:1 | BR4-2150-E-00184 | 0
BCV131 | AX18 | SIO1 | SLC02 | 2 | 9 | 0 | 1 | 2 | I2 | 1047162 | SDI | 3 | BCV131PWS39 | PWS39B |  | Pullwire Switch 39 ChB | Healthy |  | BCV131 |  | 2.9\0.1:2 | BR4-2150-E-00184 | 0
BCV131 | AX18 | SIO1 | SLC02 | 2 | 9 | 0 | 1 | 3 | I3 |  | SDI | 3 | BCV131PWS40 | PWS40A |  | Pullwire Switch 40 ChA | Healthy |  | BCV131 |  | 2.9\0.1:3 | BR4-2150-E-00184 | 0
BCV131 | AX18 | SIO1 | SLC02 | 2 | 9 | 0 | 1 | 4 | I4 |  | SDI | 3 | BCV131PWS40 | PWS40B |  | Pullwire Switch 40 ChB | Healthy |  | BCV131 |  | 2.9\0.1:4 | BR4-2150-E-00184 | 0
BCV131 | AX18 | SIO1 | SLC02 | 2 | 9 | 0 | 1 | 5 | I5 |  | SDI | 3 | [8 empty] | 2.9\0.1:5 | BR4-2150-E-00184 | 0
BCV131 | AX18 | SIO1 | SLC02 | 2 | 9 | 0 | 1 | 6 | I6 |  | SDI | 3 | [8 empty] | 2.9\0.1:6 | BR4-2150-E-00184 | 0
BCV131 | AX18 | SIO1 | SLC02 | 2 | 9 | 0 | 1 | 7 | I7 |  | SDI | 3 | [8 empty] | 2.9\0.1:7 | BR4-2150-E-00184 | 0
BCV131 | AX18 | SIO1 | SLC02 | 2 | 9 | 0 | 1 | 8 | I8 |  | SDI | 3 | [8 empty] | 2.9\0.1:8 | BR4-2150-E-00184 | 0
BCV131 | AX18 | SIO1 | SLC02 | 2 | 9 | 0 | 1 | 1 | Q1 | XTIO-Q | SDO | 3 | BCV131YA35 | YL35 |  | Start Up Warning (Beacon) | Active |  | BCV131 |  | 2.9\0.1:1 | BR4-2150-E-00184 | 0
BCV131 | AX18 | SIO1 | SLC02 | 2 | 9 | 0 | 1 | 2 | Q2 |  | SDO | 3 | BCV131YA35 | YA35 |  | Start Up Warning (Siren) | Active |  | BCV131 |  | 2.9\0.1:2 | BR4-2150-E-00184 | 0
BCV131 | AX18 | SIO1 | SLC02 | 2 | 9 | 0 | 1 | 3 | Q3 |  | SDO | 3 | BCV131YA36 | YA36 |  | Start Up Warning (Siren) | Active |  | BCV131 |  | 2.9\0.1:3 | BR4-2150-E-00184 | 0
BCV131 | AX18 | SIO1 | SLC02 | 2 | 9 | 0 | 1 | 4 | Q4 |  | SDO | 3 | [8 empty] | 2.9\0.1:4 | BR4-2150-E-00184 | 0
BCV131AX19 - BCV131 - 3766m
BCV131 | AX19 | SIO1 | SLC01 | 1 | 10 | 0 | 0 | CPU |  | 1059305 | Type 4 | 3 | [9 empty] | BR4-2150-E-00185 | 0
BCV131 | AX19 | SIO1 | SLC01 | 1 | 10 | 0 | 1 | 1 | I1 | 1044125 | SDI | 3 | BCV131PWS41 | PWS41A |  | Pullwire Switch 41 ChA | Healthy |  | BCV131 |  | 1.10\0.1:1 | BR4-2150-E-00185 | 0
BCV131 | AX19 | SIO1 | SLC01 | 1 | 10 | 0 | 1 | 2 | I2 | 1047162 | SDI | 3 | BCV131PWS41 | PWS41B |  | Pullwire Switch 41 ChB | Healthy |  | BCV131 |  | 1.10\0.1:2 | BR4-2150-E-00185 | 0
BCV131 | AX19 | SIO1 | SLC01 | 1 | 10 | 0 | 1 | 3 | I3 |  | SDI | 3 | BCV131PWS42 | PWS42A |  | Pullwire Switch 42 ChA | Healthy |  | BCV131 |  | 1.10\0.1:3 | BR4-2150-E-00185 | 0
BCV131 | AX19 | SIO1 | SLC01 | 1 | 10 | 0 | 1 | 4 | I4 |  | SDI | 3 | BCV131PWS42 | PWS42B |  | Pullwire Switch 42 ChB | Healthy |  | BCV131 |  | 1.10\0.1:4 | BR4-2150-E-00185 | 0
BCV131 | AX19 | SIO1 | SLC01 | 1 | 10 | 0 | 1 | 5 | I5 |  | SDI | 3 | [8 empty] | 1.10\0.1:5 | BR4-2150-E-00185 | 0
BCV131 | AX19 | SIO1 | SLC01 | 1 | 10 | 0 | 1 | 6 | I6 |  | SDI | 3 | [8 empty] | 1.10\0.1:6 | BR4-2150-E-00185 | 0
BCV131 | AX19 | SIO1 | SLC01 | 1 | 10 | 0 | 1 | 7 | I7 |  | SDI | 3 | [8 empty] | 1.10\0.1:7 | BR4-2150-E-00185 | 0
BCV131 | AX19 | SIO1 | SLC01 | 1 | 10 | 0 | 1 | 8 | I8 |  | SDI | 3 | [8 empty] | 1.10\0.1:8 | BR4-2150-E-00185 | 0
BCV131 | AX19 | SIO1 | SLC01 | 1 | 10 | 0 | 1 | 1 | Q1 | XTIO-Q | SDO | 3 | BCV131YA37 | YL37 |  | Start Up Warning (Beacon) | Active |  | BCV131 |  | 1.10\0.1:1 | BR4-2150-E-00185 | 0
BCV131 | AX19 | SIO1 | SLC01 | 1 | 10 | 0 | 1 | 2 | Q2 |  | SDO | 3 | BCV131YA37 | YA37 |  | Start Up Warning (Siren) | Active |  | BCV131 |  | 1.10\0.1:2 | BR4-2150-E-00185 | 0
BCV131 | AX19 | SIO1 | SLC01 | 1 | 10 | 0 | 1 | 3 | Q3 |  | SDO | 3 | BCV131YA38 | YA38 |  | Start Up Warning (Siren) | Active |  | BCV131 |  | 1.10\0.1:3 | BR4-2150-E-00185 | 0
BCV131 | AX19 | SIO1 | SLC01 | 1 | 10 | 0 | 1 | 4 | Q4 |  | SDO | 3 | [8 empty] | 1.10\0.1:4 | BR4-2150-E-00185 | 0
BCV131AX20 - BCV131 - 3523m
BCV131 | AX20 | SIO1 | SLC02 | 2 | 10 | 0 | 0 | CPU |  | 1059305 | Type 4 | 3 | [9 empty] | BR4-2150-E-00186 | 0
BCV131 | AX20 | SIO1 | SLC02 | 2 | 10 | 0 | 1 | 1 | I1 | 1044125 | SDI | 3 | BCV131PWS43 | PWS43A |  | Pullwire Switch 43 ChA | Healthy |  | BCV131 |  | 2.10\0.1:1 | BR4-2150-E-00186 | 0
BCV131 | AX20 | SIO1 | SLC02 | 2 | 10 | 0 | 1 | 2 | I2 | 1047162 | SDI | 3 | BCV131PWS43 | PWS43B |  | Pullwire Switch 43 ChB | Healthy |  | BCV131 |  | 2.10\0.1:2 | BR4-2150-E-00186 | 0
BCV131 | AX20 | SIO1 | SLC02 | 2 | 10 | 0 | 1 | 3 | I3 |  | SDI | 3 | BCV131PWS44 | PWS44A |  | Pullwire Switch 44 ChA | Healthy |  | BCV131 |  | 2.10\0.1:3 | BR4-2150-E-00186 | 0
BCV131 | AX20 | SIO1 | SLC02 | 2 | 10 | 0 | 1 | 4 | I4 |  | SDI | 3 | BCV131PWS44 | PWS44B |  | Pullwire Switch 44 ChB | Healthy |  | BCV131 |  | 2.10\0.1:4 | BR4-2150-E-00186 | 0
BCV131 | AX20 | SIO1 | SLC02 | 2 | 10 | 0 | 1 | 5 | I5 |  | SDI | 3 | [8 empty] | 2.10\0.1:5 | BR4-2150-E-00186 | 0
BCV131 | AX20 | SIO1 | SLC02 | 2 | 10 | 0 | 1 | 6 | I6 |  | SDI | 3 | [8 empty] | 2.10\0.1:6 | BR4-2150-E-00186 | 0
BCV131 | AX20 | SIO1 | SLC02 | 2 | 10 | 0 | 1 | 7 | I7 |  | SDI | 3 | [8 empty] | 2.10\0.1:7 | BR4-2150-E-00186 | 0
BCV131 | AX20 | SIO1 | SLC02 | 2 | 10 | 0 | 1 | 8 | I8 |  | SDI | 3 | [8 empty] | 2.10\0.1:8 | BR4-2150-E-00186 | 0
BCV131 | AX20 | SIO1 | SLC02 | 2 | 10 | 0 | 1 | 1 | Q1 | XTIO-Q | SDO | 3 | BCV131YA39 | YL39 |  | Start Up Warning (Beacon) | Active |  | BCV131 |  | 2.10\0.1:1 | BR4-2150-E-00186 | 0
BCV131 | AX20 | SIO1 | SLC02 | 2 | 10 | 0 | 1 | 2 | Q2 |  | SDO | 3 | BCV131YA39 | YA39 |  | Start Up Warning (Siren) | Active |  | BCV131 |  | 2.10\0.1:2 | BR4-2150-E-00186 | 0
BCV131 | AX20 | SIO1 | SLC02 | 2 | 10 | 0 | 1 | 3 | Q3 |  | SDO | 3 | BCV131YA40 | YA40 |  | Start Up Warning (Siren) | Active |  | BCV131 |  | 2.10\0.1:3 | BR4-2150-E-00186 | 0
BCV131 | AX20 | SIO1 | SLC02 | 2 | 10 | 0 | 1 | 4 | Q4 |  | SDO | 3 | [8 empty] | 2.10\0.1:4 | BR4-2150-E-00186 | 0
BCV131AX21 - BCV131 - 3280m
BCV131 | AX19 | SIO1 | SLC01 | 1 | 11 | 0 | 0 | CPU |  | 1059305 | Type 4 | 3 | [9 empty] | BR4-2150-E-00187 | 0
BCV131 | AX19 | SIO1 | SLC01 | 1 | 11 | 0 | 1 | 1 | I1 | 1044125 | SDI | 3 | BCV131PWS45 | PWS45A |  | Pullwire Switch 45 ChA | Healthy |  | BCV131 |  | 1.11\0.1:1 | BR4-2150-E-00187 | 0
BCV131 | AX19 | SIO1 | SLC01 | 1 | 11 | 0 | 1 | 2 | I2 | 1047162 | SDI | 3 | BCV131PWS45 | PWS45B |  | Pullwire Switch 45 ChB | Healthy |  | BCV131 |  | 1.11\0.1:2 | BR4-2150-E-00187 | 0
BCV131 | AX19 | SIO1 | SLC01 | 1 | 11 | 0 | 1 | 3 | I3 |  | SDI | 3 | BCV131PWS46 | PWS46A |  | Pullwire Switch 46 ChA | Healthy |  | BCV131 |  | 1.11\0.1:3 | BR4-2150-E-00187 | 0
BCV131 | AX19 | SIO1 | SLC01 | 1 | 11 | 0 | 1 | 4 | I4 |  | SDI | 3 | BCV131PWS46 | PWS46B |  | Pullwire Switch 46 ChB | Healthy |  | BCV131 |  | 1.11\0.1:4 | BR4-2150-E-00187 | 0
BCV131 | AX19 | SIO1 | SLC01 | 1 | 11 | 0 | 1 | 5 | I5 |  | SDI | 3 | [8 empty] | 1.11\0.1:5 | BR4-2150-E-00187 | 0
BCV131 | AX19 | SIO1 | SLC01 | 1 | 11 | 0 | 1 | 6 | I6 |  | SDI | 3 | [8 empty] | 1.11\0.1:6 | BR4-2150-E-00187 | 0
BCV131 | AX19 | SIO1 | SLC01 | 1 | 11 | 0 | 1 | 7 | I7 |  | SDI | 3 | [8 empty] | 1.11\0.1:7 | BR4-2150-E-00187 | 0
BCV131 | AX19 | SIO1 | SLC01 | 1 | 11 | 0 | 1 | 8 | I8 |  | SDI | 3 | [8 empty] | 1.11\0.1:8 | BR4-2150-E-00187 | 0
BCV131 | AX19 | SIO1 | SLC01 | 1 | 11 | 0 | 1 | 1 | Q1 | XTIO-Q | SDO | 3 | BCV131YA41 | YL41 |  | Start Up Warning (Beacon) | Active |  | BCV131 |  | 1.11\0.1:1 | BR4-2150-E-00187 | 0
BCV131 | AX19 | SIO1 | SLC01 | 1 | 11 | 0 | 1 | 2 | Q2 |  | SDO | 3 | BCV131YA41 | YA41 |  | Start Up Warning (Siren) | Active |  | BCV131 |  | 1.11\0.1:2 | BR4-2150-E-00187 | 0
BCV131 | AX19 | SIO1 | SLC01 | 1 | 11 | 0 | 1 | 3 | Q3 |  | SDO | 3 | BCV131YA42 | YA42 |  | Start Up Warning (Siren) | Active |  | BCV131 |  | 1.11\0.1:3 | BR4-2150-E-00187 | 0
BCV131 | AX19 | SIO1 | SLC01 | 1 | 11 | 0 | 1 | 4 | Q4 |  | SDO | 3 | [8 empty] | 1.11\0.1:4 | BR4-2150-E-00187 | 0
BCV131AX22 - BCV131 - 3037m
BCV131 | AX20 | SIO1 | SLC02 | 2 | 11 | 0 | 0 | CPU |  | 1059305 | Type 4 | 3 | [9 empty] | BR4-2150-E-00188 | 0
BCV131 | AX20 | SIO1 | SLC02 | 2 | 11 | 0 | 1 | 1 | I1 | 1044125 | SDI | 3 | BCV131PWS47 | PWS47A |  | Pullwire Switch 47 ChA | Healthy |  | BCV131 |  | 2.11\0.1:1 | BR4-2150-E-00188 | 0
BCV131 | AX20 | SIO1 | SLC02 | 2 | 11 | 0 | 1 | 2 | I2 | 1047162 | SDI | 3 | BCV131PWS47 | PWS47B |  | Pullwire Switch 47 ChB | Healthy |  | BCV131 |  | 2.11\0.1:2 | BR4-2150-E-00188 | 0
BCV131 | AX20 | SIO1 | SLC02 | 2 | 11 | 0 | 1 | 3 | I3 |  | SDI | 3 | BCV131PWS48 | PWS48A |  | Pullwire Switch 48 ChA | Healthy |  | BCV131 |  | 2.11\0.1:3 | BR4-2150-E-00188 | 0
BCV131 | AX20 | SIO1 | SLC02 | 2 | 11 | 0 | 1 | 4 | I4 |  | SDI | 3 | BCV131PWS48 | PWS48B |  | Pullwire Switch 48 ChB | Healthy |  | BCV131 |  | 2.11\0.1:4 | BR4-2150-E-00188 | 0
BCV131 | AX20 | SIO1 | SLC02 | 2 | 11 | 0 | 1 | 5 | I5 |  | SDI | 3 | [8 empty] | 2.11\0.1:5 | BR4-2150-E-00188 | 0
BCV131 | AX20 | SIO1 | SLC02 | 2 | 11 | 0 | 1 | 6 | I6 |  | SDI | 3 | [8 empty] | 2.11\0.1:6 | BR4-2150-E-00188 | 0
BCV131 | AX20 | SIO1 | SLC02 | 2 | 11 | 0 | 1 | 7 | I7 |  | SDI | 3 | [8 empty] | 2.11\0.1:7 | BR4-2150-E-00188 | 0
BCV131 | AX20 | SIO1 | SLC02 | 2 | 11 | 0 | 1 | 8 | I8 |  | SDI | 3 | [8 empty] | 2.11\0.1:8 | BR4-2150-E-00188 | 0
BCV131 | AX20 | SIO1 | SLC02 | 2 | 11 | 0 | 1 | 1 | Q1 | XTIO-Q | SDO | 3 | BCV131YA43 | YL43 |  | Start Up Warning (Beacon) | Active |  | BCV131 |  | 2.11\0.1:1 | BR4-2150-E-00188 | 0
BCV131 | AX20 | SIO1 | SLC02 | 2 | 11 | 0 | 1 | 2 | Q2 |  | SDO | 3 | BCV131YA43 | YA43 |  | Start Up Warning (Siren) | Active |  | BCV131 |  | 2.11\0.1:2 | BR4-2150-E-00188 | 0
BCV131 | AX20 | SIO1 | SLC02 | 2 | 11 | 0 | 1 | 3 | Q3 |  | SDO | 3 | BCV131YA44 | YA44 |  | Start Up Warning (Siren) | Active |  | BCV131 |  | 2.11\0.1:3 | BR4-2150-E-00188 | 0
BCV131 | AX20 | SIO1 | SLC02 | 2 | 11 | 0 | 1 | 4 | Q4 |  | SDO | 3 | [8 empty] | 2.11\0.1:4 | BR4-2150-E-00188 | 0
BCV131AX23 - BCV131 - 2794m
BCV131 | AX23 | SIO1 | SLC01 | 1 | 12 | 0 | 0 | CPU |  | 1059305 | Type 4 | 3 | [9 empty] | BR4-2150-E-00189 | 0
BCV131 | AX23 | SIO1 | SLC01 | 1 | 12 | 0 | 1 | 1 | I1 | 1044125 | SDI | 3 | BCV131PWS49 | PWS49A |  | Pullwire Switch 49 ChA | Healthy |  | BCV131 |  | 1.12\0.1:1 | BR4-2150-E-00189 | 0
BCV131 | AX23 | SIO1 | SLC01 | 1 | 12 | 0 | 1 | 2 | I2 | 1047162 | SDI | 3 | BCV131PWS49 | PWS49B |  | Pullwire Switch 49 ChB | Healthy |  | BCV131 |  | 1.12\0.1:2 | BR4-2150-E-00189 | 0
BCV131 | AX23 | SIO1 | SLC01 | 1 | 12 | 0 | 1 | 3 | I3 |  | SDI | 3 | BCV131PWS50 | PWS50A |  | Pullwire Switch 50 ChA | Healthy |  | BCV131 |  | 1.12\0.1:3 | BR4-2150-E-00189 | 0
BCV131 | AX23 | SIO1 | SLC01 | 1 | 12 | 0 | 1 | 4 | I4 |  | SDI | 3 | BCV131PWS50 | PWS50B |  | Pullwire Switch 50 ChB | Healthy |  | BCV131 |  | 1.12\0.1:4 | BR4-2150-E-00189 | 0
BCV131 | AX23 | SIO1 | SLC01 | 1 | 12 | 0 | 1 | 5 | I5 |  | SDI | 3 | [8 empty] | 1.12\0.1:5 | BR4-2150-E-00189 | 0
BCV131 | AX23 | SIO1 | SLC01 | 1 | 12 | 0 | 1 | 6 | I6 |  | SDI | 3 | [8 empty] | 1.12\0.1:6 | BR4-2150-E-00189 | 0
BCV131 | AX23 | SIO1 | SLC01 | 1 | 12 | 0 | 1 | 7 | I7 |  | SDI | 3 | [8 empty] | 1.12\0.1:7 | BR4-2150-E-00189 | 0
BCV131 | AX23 | SIO1 | SLC01 | 1 | 12 | 0 | 1 | 8 | I8 |  | SDI | 3 | [8 empty] | 1.12\0.1:8 | BR4-2150-E-00189 | 0
BCV131 | AX23 | SIO1 | SLC01 | 1 | 12 | 0 | 1 | 1 | Q1 | XTIO-Q | SDO | 3 | BCV131YA45 | YL45 |  | Start Up Warning (Beacon) | Active |  | BCV131 |  | 1.12\0.1:1 | BR4-2150-E-00189 | 0
BCV131 | AX23 | SIO1 | SLC01 | 1 | 12 | 0 | 1 | 2 | Q2 |  | SDO | 3 | BCV131YA45 | YA45 |  | Start Up Warning (Siren) | Active |  | BCV131 |  | 1.12\0.1:2 | BR4-2150-E-00189 | 0
BCV131 | AX23 | SIO1 | SLC01 | 1 | 12 | 0 | 1 | 3 | Q3 |  | SDO | 3 | BCV131YA46 | YA46 |  | Start Up Warning (Siren) | Active |  | BCV131 |  | 1.12\0.1:3 | BR4-2150-E-00189 | 0
BCV131 | AX23 | SIO1 | SLC01 | 1 | 12 | 0 | 1 | 4 | Q4 |  | SDO | 3 | [8 empty] | 1.12\0.1:4 | BR4-2150-E-00189 | 0
BCV131DX09 - BCV131 - After Horizontal Curve
EIO node #9 | DX09 | DIO1 | 132 | 2 | 9 | 0
BCV131 | DX09 | DIO1 | 132 | 2 | 9 | 0 |  | Chassis |  | BMEXBP0400
BCV131 | DX09 | DIO1 | 132 | 2 | 9 | 0 |  | Power |  | BMXCPS2010 |  | total |  | spare |  | % spare
BCV131 | DX09 | DIO1 | 132 | 2 | 9 | 0 | 0 | Comms |  | BMECRA31210 | I/O1 | 32 |  | 35 |  | 109.4%
BCV131 | DX09 | DIO1 | 132 | 2 | 9 | 0 | 1 | 0 | BMXFCW303 | BMXDDI3202K | DI | 4 | BCV131DX09 | VDC01 |  | 24VDC PLC Inputs Control Supply | Healthy | Q172 | BCV131DX09 |  | 2.9\0.1:0 | BR4-2150-E-00155 | 0 |  | D | [6 empty] | F1 | 1
BCV131 | DX09 | DIO1 | 132 | 2 | 9 | 0 | 1 | 1 |  |  | DI | [9 empty] | 2.9\0.1:1 |  |  |  | S | [6 empty] | F1 | 2
BCV131 | DX09 | DIO1 | 132 | 2 | 9 | 0 | 1 | 2 |  |  | DI | [9 empty] | 2.9\0.1:2 |  |  |  | S | [6 empty] | F1 | 3
BCV131 | DX09 | DIO1 | 132 | 2 | 9 | 0 | 1 | 3 |  |  | DI | [9 empty] | 2.9\0.1:3 |  |  |  | S | [6 empty] | F1 | 4
BCV131 | DX09 | DIO1 | 132 | 2 | 9 | 0 | 1 | 4 |  |  | DI | [9 empty] | 2.9\0.1:4 |  |  |  | S | [6 empty] | F1 | 5
BCV131 | DX09 | DIO1 | 132 | 2 | 9 | 0 | 1 | 5 |  |  | DI | [9 empty] | 2.9\0.1:5 |  |  |  | S | [6 empty] | F1 | 6
BCV131 | DX09 | DIO1 | 132 | 2 | 9 | 0 | 1 | 6 |  |  | DI | [9 empty] | 2.9\0.1:6 |  |  |  | S | [6 empty] | F1 | 7
BCV131 | DX09 | DIO1 | 132 | 2 | 9 | 0 | 1 | 7 |  |  | DI | [9 empty] | 2.9\0.1:7 |  |  |  | S | [6 empty] | F1 | 8
BCV131 | DX09 | DIO1 | 132 | 2 | 9 | 0 | 1 | 8 |  |  | DI | 4 | BCV131BDS07 | BDS07 |  | Belt Drift Switch 7 | Healthy |  | BCV131 |  | 2.9\0.1:8 | BR4-2150-E-00156 | 0 |  | S | [6 empty] | F1 | 9 | 10
BCV131 | DX09 | DIO1 | 132 | 2 | 9 | 0 | 1 | 9 |  |  | DI | 4 | BCV131BDS08 | BDS08 |  | Belt Drift Switch 8 | Healthy |  | BCV131 |  | 2.9\0.1:9 | BR4-2150-E-00156 | 0 |  | S | [6 empty] | F1 | 11 | 12
BCV131 | DX09 | DIO1 | 132 | 2 | 9 | 0 | 1 | 10 |  |  | DI | 4 | BCV131BDS09 | BDS09 |  | Belt Drift Switch 9 | Healthy |  | BCV131 |  | 2.9\0.1:10 | BR4-2150-E-00156 | 0 |  | S | [6 empty] | F1 | 13 | 14
BCV131 | DX09 | DIO1 | 132 | 2 | 9 | 0 | 1 | 11 |  |  | DI | 4 | BCV131BDS10 | BDS10 |  | Belt Drift Switch 10 | Healthy |  | BCV131 |  | 2.9\0.1:11 | BR4-2150-E-00156 | 0 |  | S | [6 empty] | F1 | 15 | 16
BCV131 | DX09 | DIO1 | 132 | 2 | 9 | 0 | 1 | 12 |  |  | DI | [9 empty] | 2.9\0.1:12 |  |  |  | S | [6 empty] | F1 | 17 | 18
BCV131 | DX09 | DIO1 | 132 | 2 | 9 | 0 | 1 | 13 |  |  | DI | [9 empty] | 2.9\0.1:13 |  |  |  | S | [6 empty] | F1 | 19 | 20
BCV131 | DX09 | DIO1 | 132 | 2 | 9 | 0 | 1 | 14 |  |  | DI | [9 empty] | 2.9\0.1:14 |  |  |  | S | [6 empty] | F1 | 21 | 22
BCV131 | DX09 | DIO1 | 132 | 2 | 9 | 0 | 1 | 15 |  |  | DI | [9 empty] | 2.9\0.1:15 |  |  |  | S | [6 empty] | F1 | 23 | 24
BCV131 | DX09 | DIO1 | 132 | 2 | 9 | 0 | 1 | 16 |  |  | DI | [9 empty] | 2.9\0.1:16 |  |  |  | S | [6 empty] | F1 | 25 | 26
BCV131 | DX09 | DIO1 | 132 | 2 | 9 | 0 | 1 | 17 |  |  | DI | [9 empty] | 2.9\0.1:17 |  |  |  | S | [6 empty] | F1 | 27 | 28
BCV131 | DX09 | DIO1 | 132 | 2 | 9 | 0 | 1 | 18 |  |  | DI | [9 empty] | 2.9\0.1:18 |  |  |  | S | [6 empty] | F1 | 29 | 30
BCV131 | DX09 | DIO1 | 132 | 2 | 9 | 0 | 1 | 19 |  |  | DI | [9 empty] | 2.9\0.1:19 |  |  |  | S | [6 empty] | F1 | 31 | 32
BCV131 | DX09 | DIO1 | 132 | 2 | 9 | 0 | 1 | 20 |  |  | DI | [9 empty] | 2.9\0.1:20 |  |  |  | S | [6 empty] | F1 | 33 | 34
BCV131 | DX09 | DIO1 | 132 | 2 | 9 | 0 | 1 | 21 |  |  | DI | [9 empty] | 2.9\0.1:21 |  |  |  | S | [6 empty] | F1 | 35 | 36
BCV131 | DX09 | DIO1 | 132 | 2 | 9 | 0 | 1 | 22 |  |  | DI | [9 empty] | 2.9\0.1:22 |  |  |  | S | [6 empty] | F1 | 37 | 38
BCV131 | DX09 | DIO1 | 132 | 2 | 9 | 0 | 1 | 23 |  |  | DI | [9 empty] | 2.9\0.1:23 |  |  |  | S | [6 empty] | F1 | 39 | 40
BCV131 | DX09 | DIO1 | 132 | 2 | 9 | 0 | 1 | 24 |  |  | DI | [9 empty] | 2.9\0.1:24 |  |  |  | S | [6 empty] | F1 | 41 | 42
BCV131 | DX09 | DIO1 | 132 | 2 | 9 | 0 | 1 | 25 |  |  | DI | [9 empty] | 2.9\0.1:25 |  |  |  | S | [6 empty] | F1 | 43 | 44
BCV131 | DX09 | DIO1 | 132 | 2 | 9 | 0 | 1 | 26 |  |  | DI | [9 empty] | 2.9\0.1:26 |  |  |  | S | [6 empty] | F1 | 45 | 46
BCV131 | DX09 | DIO1 | 132 | 2 | 9 | 0 | 1 | 27 |  |  | DI | [9 empty] | 2.9\0.1:27 |  |  |  | S | [6 empty] | F1 | 47 | 48
BCV131 | DX09 | DIO1 | 132 | 2 | 9 | 0 | 1 | 28 |  |  | DI | [9 empty] | 2.9\0.1:28 |  |  |  | S | [6 empty] | F1 | 49 | 50
BCV131 | DX09 | DIO1 | 132 | 2 | 9 | 0 | 1 | 29 |  |  | DI | [9 empty] | 2.9\0.1:29 |  |  |  | S | [6 empty] | F1 | 51 | 52
BCV131 | DX09 | DIO1 | 132 | 2 | 9 | 0 | 1 | 30 |  |  | DI | [9 empty] | 2.9\0.1:30 |  |  |  | S | [6 empty] | F1 | 53 | 54
BCV131 | DX09 | DIO1 | 132 | 2 | 9 | 0 | 1 | 31 |  |  | DI | [9 empty] | 2.9\0.1:31 |  |  |  | S | [6 empty] | F1 | 55 | 56
BCV131 | DX09 | DIO1 | 132 | 2 | 9 | 0 | 2 |  |  | BMXXEM010 |  | 0 | [8 empty] | 2.9\0.2:
BCV131 | DX09 | DIO1 | 132 | 2 | 9 | 0 | 2 |  |  |  |  | 0 | [8 empty] | 2.9\0.2:
BCV131 | DX09 | DIO1 | 132 | 2 | 9 | 0 | 2 |  |  |  |  | 0 | [8 empty] | 2.9\0.2:
BCV131 | DX09 | DIO1 | 132 | 2 | 9 | 0 | 2 |  |  |  |  | 0 | [8 empty] | 2.9\0.2:
BCV131 | DX09 | DIO1 | 132 | 2 | 9 | 0 | 3 |  |  | BMXXEM010 |  | 0 | [8 empty] | 2.9\0.3:
BCV131 | DX09 | DIO1 | 132 | 2 | 9 | 0 | 3 |  |  |  |  | 0 | [8 empty] | 2.9\0.3:
BCV131 | DX09 | DIO1 | 132 | 2 | 9 | 0 | 3 |  |  |  |  | 0 | [8 empty] | 2.9\0.3:
BCV131 | DX09 | DIO1 | 132 | 2 | 9 | 0 | 3 |  |  |  |  | 0 | [8 empty] | 2.9\0.3: | [15 empty] | Earth
Earth
BCV131AX24 - BCV131 - 2551m
BCV131 | AX24 | SIO1 | SLC02 | 2 | 12 | 0 | 0 | CPU |  | 1059305 | Type 4 | 3 | [9 empty] | BR4-2150-E-00190 | 0
BCV131 | AX24 | SIO1 | SLC02 | 2 | 12 | 0 | 1 | 1 | I1 | 1044125 | SDI | 3 | BCV131PWS51 | PWS51A |  | Pullwire Switch 51 ChA | Healthy |  | BCV131 |  | 2.12\0.1:1 | BR4-2150-E-00190 | 0
BCV131 | AX24 | SIO1 | SLC02 | 2 | 12 | 0 | 1 | 2 | I2 | 1047162 | SDI | 3 | BCV131PWS51 | PWS51B |  | Pullwire Switch 51 ChB | Healthy |  | BCV131 |  | 2.12\0.1:2 | BR4-2150-E-00190 | 0
BCV131 | AX24 | SIO1 | SLC02 | 2 | 12 | 0 | 1 | 3 | I3 |  | SDI | 3 | BCV131PWS52 | PWS52A |  | Pullwire Switch 52 ChA | Healthy |  | BCV131 |  | 2.12\0.1:3 | BR4-2150-E-00190 | 0
BCV131 | AX24 | SIO1 | SLC02 | 2 | 12 | 0 | 1 | 4 | I4 |  | SDI | 3 | BCV131PWS52 | PWS52B |  | Pullwire Switch 52 ChB | Healthy |  | BCV131 |  | 2.12\0.1:4 | BR4-2150-E-00190 | 0
BCV131 | AX24 | SIO1 | SLC02 | 2 | 12 | 0 | 1 | 5 | I5 |  | SDI | 3 | [8 empty] | 2.12\0.1:5 | BR4-2150-E-00190 | 0
BCV131 | AX24 | SIO1 | SLC02 | 2 | 12 | 0 | 1 | 6 | I6 |  | SDI | 3 | [8 empty] | 2.12\0.1:6 | BR4-2150-E-00190 | 0
BCV131 | AX24 | SIO1 | SLC02 | 2 | 12 | 0 | 1 | 7 | I7 |  | SDI | 3 | [8 empty] | 2.12\0.1:7 | BR4-2150-E-00190 | 0
BCV131 | AX24 | SIO1 | SLC02 | 2 | 12 | 0 | 1 | 8 | I8 |  | SDI | 3 | [8 empty] | 2.12\0.1:8 | BR4-2150-E-00190 | 0
BCV131 | AX24 | SIO1 | SLC02 | 2 | 12 | 0 | 1 | 1 | Q1 | XTIO-Q | SDO | 3 | BCV131YA47 | YL47 |  | Start Up Warning (Beacon) | Active |  | BCV131 |  | 2.12\0.1:1 | BR4-2150-E-00190 | 0
BCV131 | AX24 | SIO1 | SLC02 | 2 | 12 | 0 | 1 | 2 | Q2 |  | SDO | 3 | BCV131YA47 | YA47 |  | Start Up Warning (Siren) | Active |  | BCV131 |  | 2.12\0.1:2 | BR4-2150-E-00190 | 0
BCV131 | AX24 | SIO1 | SLC02 | 2 | 12 | 0 | 1 | 3 | Q3 |  | SDO | 3 | BCV131YA48 | YA48 |  | Start Up Warning (Siren) | Active |  | BCV131 |  | 2.12\0.1:3 | BR4-2150-E-00190 | 0
BCV131 | AX24 | SIO1 | SLC02 | 2 | 12 | 0 | 1 | 4 | Q4 |  | SDO | 3 | [8 empty] | 2.12\0.1:4 | BR4-2150-E-00190 | 0
BCV131AX25 - BCV131 - 2308m
BCV131 | AX25 | SIO1 | SLC01 | 1 | 13 | 0 | 0 | CPU |  | 1059305 | Type 4 | 3 | [9 empty] | BR4-2150-E-00191 | 0
BCV131 | AX25 | SIO1 | SLC01 | 1 | 13 | 0 | 1 | 1 | I1 | 1044125 | SDI | 3 | BCV131PWS53 | PWS53A |  | Pullwire Switch 53 ChA | Healthy |  | BCV131 |  | 1.13\0.1:1 | BR4-2150-E-00191 | 0
BCV131 | AX25 | SIO1 | SLC01 | 1 | 13 | 0 | 1 | 2 | I2 | 1047162 | SDI | 3 | BCV131PWS53 | PWS53B |  | Pullwire Switch 53 ChB | Healthy |  | BCV131 |  | 1.13\0.1:2 | BR4-2150-E-00191 | 0
BCV131 | AX25 | SIO1 | SLC01 | 1 | 13 | 0 | 1 | 3 | I3 |  | SDI | 3 | BCV131PWS54 | PWS54A |  | Pullwire Switch 54 ChA | Healthy |  | BCV131 |  | 1.13\0.1:3 | BR4-2150-E-00191 | 0
BCV131 | AX25 | SIO1 | SLC01 | 1 | 13 | 0 | 1 | 4 | I4 |  | SDI | 3 | BCV131PWS54 | PWS54B |  | Pullwire Switch 54 ChB | Healthy |  | BCV131 |  | 1.13\0.1:4 | BR4-2150-E-00191 | 0
BCV131 | AX25 | SIO1 | SLC01 | 1 | 13 | 0 | 1 | 5 | I5 |  | SDI | 3 | [8 empty] | 1.13\0.1:5 | BR4-2150-E-00191 | 0
BCV131 | AX25 | SIO1 | SLC01 | 1 | 13 | 0 | 1 | 6 | I6 |  | SDI | 3 | [8 empty] | 1.13\0.1:6 | BR4-2150-E-00191 | 0
BCV131 | AX25 | SIO1 | SLC01 | 1 | 13 | 0 | 1 | 7 | I7 |  | SDI | 3 | [8 empty] | 1.13\0.1:7 | BR4-2150-E-00191 | 0
BCV131 | AX25 | SIO1 | SLC01 | 1 | 13 | 0 | 1 | 8 | I8 |  | SDI | 3 | [8 empty] | 1.13\0.1:8 | BR4-2150-E-00191 | 0
BCV131 | AX25 | SIO1 | SLC01 | 1 | 13 | 0 | 1 | 1 | Q1 | XTIO-Q | SDO | 3 | BCV131YA49 | YL49 |  | Start Up Warning (Beacon) | Active |  | BCV131 |  | 1.13\0.1:1 | BR4-2150-E-00191 | 0
BCV131 | AX25 | SIO1 | SLC01 | 1 | 13 | 0 | 1 | 2 | Q2 |  | SDO | 3 | BCV131YA49 | YA49 |  | Start Up Warning (Siren) | Active |  | BCV131 |  | 1.13\0.1:2 | BR4-2150-E-00191 | 0
BCV131 | AX25 | SIO1 | SLC01 | 1 | 13 | 0 | 1 | 3 | Q3 |  | SDO | 3 | BCV131YA50 | YA50 |  | Start Up Warning (Siren) | Active |  | BCV131 |  | 1.13\0.1:3 | BR4-2150-E-00191 | 0
BCV131 | AX25 | SIO1 | SLC01 | 1 | 13 | 0 | 1 | 4 | Q4 |  | SDO | 3 | [8 empty] | 1.13\0.1:4 | BR4-2150-E-00191 | 0
BCV131AX26 - BCV131 - 2065m
BCV131 | AX26 | SIO1 | SLC02 | 2 | 13 | 0 | 0 | CPU |  | 1059305 | Type 4 | 3 | [9 empty] | BR4-2150-E-00192 | 0
BCV131 | AX26 | SIO1 | SLC02 | 2 | 13 | 0 | 1 | 1 | I1 | 1044125 | SDI | 3 | BCV131PWS55 | PWS55A |  | Pullwire Switch 55 ChA | Healthy |  | BCV131 |  | 2.13\0.1:1 | BR4-2150-E-00192 | 0
BCV131 | AX26 | SIO1 | SLC02 | 2 | 13 | 0 | 1 | 2 | I2 | 1047162 | SDI | 3 | BCV131PWS55 | PWS55B |  | Pullwire Switch 55 ChB | Healthy |  | BCV131 |  | 2.13\0.1:2 | BR4-2150-E-00192 | 0
BCV131 | AX26 | SIO1 | SLC02 | 2 | 13 | 0 | 1 | 3 | I3 |  | SDI | 3 | BCV131PWS56 | PWS56A |  | Pullwire Switch 56 ChA | Healthy |  | BCV131 |  | 2.13\0.1:3 | BR4-2150-E-00192 | 0
BCV131 | AX26 | SIO1 | SLC02 | 2 | 13 | 0 | 1 | 4 | I4 |  | SDI | 3 | BCV131PWS56 | PWS56B |  | Pullwire Switch 56 ChB | Healthy |  | BCV131 |  | 2.13\0.1:4 | BR4-2150-E-00192 | 0
BCV131 | AX26 | SIO1 | SLC02 | 2 | 13 | 0 | 1 | 5 | I5 |  | SDI | 3 | [8 empty] | 2.13\0.1:5 | BR4-2150-E-00192 | 0
BCV131 | AX26 | SIO1 | SLC02 | 2 | 13 | 0 | 1 | 6 | I6 |  | SDI | 3 | [8 empty] | 2.13\0.1:6 | BR4-2150-E-00192 | 0
BCV131 | AX26 | SIO1 | SLC02 | 2 | 13 | 0 | 1 | 7 | I7 |  | SDI | 3 | [8 empty] | 2.13\0.1:7 | BR4-2150-E-00192 | 0
BCV131 | AX26 | SIO1 | SLC02 | 2 | 13 | 0 | 1 | 8 | I8 |  | SDI | 3 | [8 empty] | 2.13\0.1:8 | BR4-2150-E-00192 | 0
BCV131 | AX26 | SIO1 | SLC02 | 2 | 13 | 0 | 1 | 1 | Q1 | XTIO-Q | SDO | 3 | BCV131YA51 | YL51 |  | Start Up Warning (Beacon) | Active |  | BCV131 |  | 2.13\0.1:1 | BR4-2150-E-00192 | 0
BCV131 | AX26 | SIO1 | SLC02 | 2 | 13 | 0 | 1 | 2 | Q2 |  | SDO | 3 | BCV131YA51 | YA51 |  | Start Up Warning (Siren) | Active |  | BCV131 |  | 2.13\0.1:2 | BR4-2150-E-00192 | 0
BCV131 | AX26 | SIO1 | SLC02 | 2 | 13 | 0 | 1 | 3 | Q3 |  | SDO | 3 | BCV131YA52 | YA52 |  | Start Up Warning (Siren) | Active |  | BCV131 |  | 2.13\0.1:3 | BR4-2150-E-00192 | 0
BCV131 | AX26 | SIO1 | SLC02 | 2 | 13 | 0 | 1 | 4 | Q4 |  | SDO | 3 | [8 empty] | 2.13\0.1:4 | BR4-2150-E-00192 | 0
BCV131DX10 - BCV131 - Along Horizontal Curve
EIO node #10 | DX10 | DIO1 | 132 | 2 | 10 | 0
BCV131 | DX10 | DIO1 | 132 | 2 | 10 | 0 |  | Chassis |  | BMEXBP0400
BCV131 | DX10 | DIO1 | 132 | 2 | 10 | 0 |  | Power |  | BMXCPS2010 |  | total |  | spare |  | % spare
BCV131 | DX10 | DIO1 | 132 | 2 | 10 | 0 | 0 | Comms |  | BMECRA31210 | I/O1 | 32 |  | 35 |  | 109.4%
BCV131 | DX10 | DIO1 | 132 | 2 | 10 | 0 | 1 | 0 | BMXFCW303 | BMXDDI3202K | DI | 3 |  | VDC01 |  | 24VDC BCV131DX10 PLC Control Supply | Healthy |  | BCV131DX10 |  | 2.10\0.1:0 | BR4-2150-E-00157 | 0 |  | D | [6 empty] | F1 | 1
BCV131 | DX10 | DIO1 | 132 | 2 | 10 | 0 | 1 | 1 |  |  | DI | [9 empty] | 2.10\0.1:1 |  |  |  | S | [6 empty] | F1 | 2
BCV131 | DX10 | DIO1 | 132 | 2 | 10 | 0 | 1 | 2 |  |  | DI | [9 empty] | 2.10\0.1:2 |  |  |  | S | [6 empty] | F1 | 3
BCV131 | DX10 | DIO1 | 132 | 2 | 10 | 0 | 1 | 3 |  |  | DI | [9 empty] | 2.10\0.1:3 |  |  |  | S | [6 empty] | F1 | 4
BCV131 | DX10 | DIO1 | 132 | 2 | 10 | 0 | 1 | 4 |  |  | DI | [9 empty] | 2.10\0.1:4 |  |  |  | S | [6 empty] | F1 | 5
BCV131 | DX10 | DIO1 | 132 | 2 | 10 | 0 | 1 | 5 |  |  | DI | [9 empty] | 2.10\0.1:5 |  |  |  | S | [6 empty] | F1 | 6
BCV131 | DX10 | DIO1 | 132 | 2 | 10 | 0 | 1 | 6 |  |  | DI | [9 empty] | 2.10\0.1:6 |  |  |  | S | [6 empty] | F1 | 7
BCV131 | DX10 | DIO1 | 132 | 2 | 10 | 0 | 1 | 7 |  |  | DI | [9 empty] | 2.10\0.1:7 |  |  |  | S | [6 empty] | F1 | 8
BCV131 | DX10 | DIO1 | 132 | 2 | 10 | 0 | 1 | 8 |  |  | DI | 4 | BCV131BDS11 | BDS11 |  | Belt Drift Switch 11 | Healthy |  | BCV131 |  | 2.10\0.1:8 | BR4-2150-E-00158 | 0 |  | S | [6 empty] | F1 | 9 | 10
BCV131 | DX10 | DIO1 | 132 | 2 | 10 | 0 | 1 | 9 |  |  | DI | 4 | BCV131BDS12 | BDS12 |  | Belt Drift Switch 12 | Healthy |  | BCV131 |  | 2.10\0.1:9 | BR4-2150-E-00158 | 0 |  | S | [6 empty] | F1 | 11 | 12
BCV131 | DX10 | DIO1 | 132 | 2 | 10 | 0 | 1 | 10 |  |  | DI | 4 | BCV131BDS13 | BDS13 |  | Belt Drift Switch 13 | Healthy |  | BCV131 |  | 2.10\0.1:10 | BR4-2150-E-00158 | 0 |  | S | [6 empty] | F1 | 13 | 14
BCV131 | DX10 | DIO1 | 132 | 2 | 10 | 0 | 1 | 11 |  |  | DI | 4 | BCV131BDS14 | BDS14 |  | Belt Drift Switch 14 | Healthy |  | BCV131 |  | 2.10\0.1:11 | BR4-2150-E-00158 | 0 |  | S | [6 empty] | F1 | 15 | 16
BCV131 | DX10 | DIO1 | 132 | 2 | 10 | 0 | 1 | 12 |  |  | DI | [9 empty] | 2.10\0.1:12 |  |  |  | S | [6 empty] | F1 | 17 | 18
BCV131 | DX10 | DIO1 | 132 | 2 | 10 | 0 | 1 | 13 |  |  | DI | [9 empty] | 2.10\0.1:13 |  |  |  | S | [6 empty] | F1 | 19 | 20
BCV131 | DX10 | DIO1 | 132 | 2 | 10 | 0 | 1 | 14 |  |  | DI | [9 empty] | 2.10\0.1:14 |  |  |  | S | [6 empty] | F1 | 21 | 22
BCV131 | DX10 | DIO1 | 132 | 2 | 10 | 0 | 1 | 15 |  |  | DI | [9 empty] | 2.10\0.1:15 |  |  |  | S | [6 empty] | F1 | 23 | 24
BCV131 | DX10 | DIO1 | 132 | 2 | 10 | 0 | 1 | 16 |  |  | DI | [9 empty] | 2.10\0.1:16 |  |  |  | S | [6 empty] | F1 | 25 | 26
BCV131 | DX10 | DIO1 | 132 | 2 | 10 | 0 | 1 | 17 |  |  | DI | [9 empty] | 2.10\0.1:17 |  |  |  | S | [6 empty] | F1 | 27 | 28
BCV131 | DX10 | DIO1 | 132 | 2 | 10 | 0 | 1 | 18 |  |  | DI | [9 empty] | 2.10\0.1:18 |  |  |  | S | [6 empty] | F1 | 29 | 30
BCV131 | DX10 | DIO1 | 132 | 2 | 10 | 0 | 1 | 19 |  |  | DI | [9 empty] | 2.10\0.1:19 |  |  |  | S | [6 empty] | F1 | 31 | 32
BCV131 | DX10 | DIO1 | 132 | 2 | 10 | 0 | 1 | 20 |  |  | DI | [9 empty] | 2.10\0.1:20 |  |  |  | S | [6 empty] | F1 | 33 | 34
BCV131 | DX10 | DIO1 | 132 | 2 | 10 | 0 | 1 | 21 |  |  | DI | [9 empty] | 2.10\0.1:21 |  |  |  | S | [6 empty] | F1 | 35 | 36
BCV131 | DX10 | DIO1 | 132 | 2 | 10 | 0 | 1 | 22 |  |  | DI | [9 empty] | 2.10\0.1:22 |  |  |  | S | [6 empty] | F1 | 37 | 38
BCV131 | DX10 | DIO1 | 132 | 2 | 10 | 0 | 1 | 23 |  |  | DI | [9 empty] | 2.10\0.1:23 |  |  |  | S | [6 empty] | F1 | 39 | 40
BCV131 | DX10 | DIO1 | 132 | 2 | 10 | 0 | 1 | 24 |  |  | DI | [9 empty] | 2.10\0.1:24 |  |  |  | S | [6 empty] | F1 | 41 | 42
BCV131 | DX10 | DIO1 | 132 | 2 | 10 | 0 | 1 | 25 |  |  | DI | [9 empty] | 2.10\0.1:25 |  |  |  | S | [6 empty] | F1 | 43 | 44
BCV131 | DX10 | DIO1 | 132 | 2 | 10 | 0 | 1 | 26 |  |  | DI | [9 empty] | 2.10\0.1:26 |  |  |  | S | [6 empty] | F1 | 45 | 46
BCV131 | DX10 | DIO1 | 132 | 2 | 10 | 0 | 1 | 27 |  |  | DI | [9 empty] | 2.10\0.1:27 |  |  |  | S | [6 empty] | F1 | 47 | 48
BCV131 | DX10 | DIO1 | 132 | 2 | 10 | 0 | 1 | 28 |  |  | DI | [9 empty] | 2.10\0.1:28 |  |  |  | S | [6 empty] | F1 | 49 | 50
BCV131 | DX10 | DIO1 | 132 | 2 | 10 | 0 | 1 | 29 |  |  | DI | [9 empty] | 2.10\0.1:29 |  |  |  | S | [6 empty] | F1 | 51 | 52
BCV131 | DX10 | DIO1 | 132 | 2 | 10 | 0 | 1 | 30 |  |  | DI | [9 empty] | 2.10\0.1:30 |  |  |  | S | [6 empty] | F1 | 53 | 54
BCV131 | DX10 | DIO1 | 132 | 2 | 10 | 0 | 1 | 31 |  |  | DI | [9 empty] | 2.10\0.1:31 |  |  |  | S | [6 empty] | F1 | 55 | 56
BCV131 | DX10 | DIO1 | 132 | 2 | 10 | 0 | 2 |  |  | BMXXEM010 |  | 0 | [8 empty] | 2.10\0.2:
BCV131 | DX10 | DIO1 | 132 | 2 | 10 | 0 | 2 |  |  |  |  | 0 | [8 empty] | 2.10\0.2:
BCV131 | DX10 | DIO1 | 132 | 2 | 10 | 0 | 2 |  |  |  |  | 0 | [8 empty] | 2.10\0.2:
BCV131 | DX10 | DIO1 | 132 | 2 | 10 | 0 | 2 |  |  |  |  | 0 | [8 empty] | 2.10\0.2:
BCV131 | DX10 | DIO1 | 132 | 2 | 10 | 0 | 3 |  |  | BMXXEM010 |  | 0 | [8 empty] | 2.10\0.3:
BCV131 | DX10 | DIO1 | 132 | 2 | 10 | 0 | 3 |  |  |  |  | 0 | [8 empty] | 2.10\0.3:
BCV131 | DX10 | DIO1 | 132 | 2 | 10 | 0 | 3 |  |  |  |  | 0 | [8 empty] | 2.10\0.3:
BCV131 | DX10 | DIO1 | 132 | 2 | 10 | 0 | 3 |  |  |  |  | 0 | [8 empty] | 2.10\0.3: | [15 empty] | Earth
Earth
BCV131AX27 - BCV131 - 1822m
BCV131 | AX27 | SIO1 | SLC01 | 1 | 14 | 0 | 0 | CPU |  | 1059305 | Type 4 | 3 | [9 empty] | BR4-2150-E-00193 | 0
BCV131 | AX27 | SIO1 | SLC01 | 1 | 14 | 0 | 1 | 1 | I1 | 1044125 | SDI | 3 | BCV131PWS57 | PWS57A |  | Pullwire Switch 57 ChA | Healthy |  | BCV131 |  | 1.14\0.1:1 | BR4-2150-E-00193 | 0
BCV131 | AX27 | SIO1 | SLC01 | 1 | 14 | 0 | 1 | 2 | I2 | 1047162 | SDI | 3 | BCV131PWS57 | PWS57B |  | Pullwire Switch 57 ChB | Healthy |  | BCV131 |  | 1.14\0.1:2 | BR4-2150-E-00193 | 0
BCV131 | AX27 | SIO1 | SLC01 | 1 | 14 | 0 | 1 | 3 | I3 |  | SDI | 3 | BCV131PWS58 | PWS58A |  | Pullwire Switch 58 ChA | Healthy |  | BCV131 |  | 1.14\0.1:3 | BR4-2150-E-00193 | 0
BCV131 | AX27 | SIO1 | SLC01 | 1 | 14 | 0 | 1 | 4 | I4 |  | SDI | 3 | BCV131PWS58 | PWS58B |  | Pullwire Switch 58 ChB | Healthy |  | BCV131 |  | 1.14\0.1:4 | BR4-2150-E-00193 | 0
BCV131 | AX27 | SIO1 | SLC01 | 1 | 14 | 0 | 1 | 5 | I5 |  | SDI | 3 | [8 empty] | 1.14\0.1:5 | BR4-2150-E-00193 | 0
BCV131 | AX27 | SIO1 | SLC01 | 1 | 14 | 0 | 1 | 6 | I6 |  | SDI | 3 | [8 empty] | 1.14\0.1:6 | BR4-2150-E-00193 | 0
BCV131 | AX27 | SIO1 | SLC01 | 1 | 14 | 0 | 1 | 7 | I7 |  | SDI | 3 | [8 empty] | 1.14\0.1:7 | BR4-2150-E-00193 | 0
BCV131 | AX27 | SIO1 | SLC01 | 1 | 14 | 0 | 1 | 8 | I8 |  | SDI | 3 | [8 empty] | 1.14\0.1:8 | BR4-2150-E-00193 | 0
BCV131 | AX27 | SIO1 | SLC01 | 1 | 14 | 0 | 1 | 1 | Q1 | XTIO-Q | SDO | 3 | BCV131YA53 | YL53 |  | Start Up Warning (Beacon) | Active |  | BCV131 |  | 1.14\0.1:1 | BR4-2150-E-00193 | 0
BCV131 | AX27 | SIO1 | SLC01 | 1 | 14 | 0 | 1 | 2 | Q2 |  | SDO | 3 | BCV131YA53 | YA53 |  | Start Up Warning (Siren) | Active |  | BCV131 |  | 1.14\0.1:2 | BR4-2150-E-00193 | 0
BCV131 | AX27 | SIO1 | SLC01 | 1 | 14 | 0 | 1 | 3 | Q3 |  | SDO | 3 | BCV131YA54 | YA54 |  | Start Up Warning (Siren) | Active |  | BCV131 |  | 1.14\0.1:3 | BR4-2150-E-00193 | 0
BCV131 | AX27 | SIO1 | SLC01 | 1 | 14 | 0 | 1 | 4 | Q4 |  | SDO | 3 | [8 empty] | 1.14\0.1:4 | BR4-2150-E-00193 | 0
BCV131AX28 - BCV131 - 1579m
BCV131 | AX28 | SIO1 | SLC02 | 2 | 14 | 0 | 0 | CPU |  | 1059305 | Type 4 | 3 | [9 empty] | BR4-2150-E-00194 | 0
BCV131 | AX28 | SIO1 | SLC02 | 2 | 14 | 0 | 1 | 1 | I1 | 1044125 | SDI | 3 | BCV131PWS59 | PWS59A |  | Pullwire Switch 59 ChA | Healthy |  | BCV131 |  | 2.14\0.1:1 | BR4-2150-E-00194 | 0
BCV131 | AX28 | SIO1 | SLC02 | 2 | 14 | 0 | 1 | 2 | I2 | 1047162 | SDI | 3 | BCV131PWS59 | PWS59B |  | Pullwire Switch 59 ChB | Healthy |  | BCV131 |  | 2.14\0.1:2 | BR4-2150-E-00194 | 0
BCV131 | AX28 | SIO1 | SLC02 | 2 | 14 | 0 | 1 | 3 | I3 |  | SDI | 3 | BCV131PWS60 | PWS60A |  | Pullwire Switch 60 ChA | Healthy |  | BCV131 |  | 2.14\0.1:3 | BR4-2150-E-00194 | 0
BCV131 | AX28 | SIO1 | SLC02 | 2 | 14 | 0 | 1 | 4 | I4 |  | SDI | 3 | BCV131PWS60 | PWS60B |  | Pullwire Switch 60 ChB | Healthy |  | BCV131 |  | 2.14\0.1:4 | BR4-2150-E-00194 | 0
BCV131 | AX28 | SIO1 | SLC02 | 2 | 14 | 0 | 1 | 5 | I5 |  | SDI | 3 | [8 empty] | 2.14\0.1:5 | BR4-2150-E-00194 | 0
BCV131 | AX28 | SIO1 | SLC02 | 2 | 14 | 0 | 1 | 6 | I6 |  | SDI | 3 | [8 empty] | 2.14\0.1:6 | BR4-2150-E-00194 | 0
BCV131 | AX28 | SIO1 | SLC02 | 2 | 14 | 0 | 1 | 7 | I7 |  | SDI | 3 | [8 empty] | 2.14\0.1:7 | BR4-2150-E-00194 | 0
BCV131 | AX28 | SIO1 | SLC02 | 2 | 14 | 0 | 1 | 8 | I8 |  | SDI | 3 | [8 empty] | 2.14\0.1:8 | BR4-2150-E-00194 | 0
BCV131 | AX28 | SIO1 | SLC02 | 2 | 14 | 0 | 1 | 1 | Q1 | XTIO-Q | SDO | 3 | BCV131YA55 | YL55 |  | Start Up Warning (Beacon) | Active |  | BCV131 |  | 2.14\0.1:1 | BR4-2150-E-00194 | 0
BCV131 | AX28 | SIO1 | SLC02 | 2 | 14 | 0 | 1 | 2 | Q2 |  | SDO | 3 | BCV131YA55 | YA55 |  | Start Up Warning (Siren) | Active |  | BCV131 |  | 2.14\0.1:2 | BR4-2150-E-00194 | 0
BCV131 | AX28 | SIO1 | SLC02 | 2 | 14 | 0 | 1 | 3 | Q3 |  | SDO | 3 | BCV131YA56 | YA56 |  | Start Up Warning (Siren) | Active |  | BCV131 |  | 2.14\0.1:3 | BR4-2150-E-00194 | 0
BCV131 | AX28 | SIO1 | SLC02 | 2 | 14 | 0 | 1 | 4 | Q4 |  | SDO | 3 | [8 empty] | 2.14\0.1:4 | BR4-2150-E-00194 | 0
BCV131DX11 - BCV131 - Prior to Horizontal Curve
EIO node #11 | DX11 | DIO1 | 132 | 2 | 11 | 0
BCV131 | DX11 | DIO1 | 132 | 2 | 11 | 0 |  | Chassis |  | BMEXBP0400
BCV131 | DX11 | DIO1 | 132 | 2 | 11 | 0 |  | Power |  | BMXCPS2010 |  | total |  | spare |  | % spare
BCV131 | DX11 | DIO1 | 132 | 2 | 11 | 0 | 0 | Comms |  | BMECRA31210 | I/O1 | 32 |  | 35 |  | 109.4%
BCV131 | DX11 | DIO1 | 132 | 2 | 11 | 0 | 1 | 0 | BMXFCW303 | BMXDDI3202K | DI | 3 | BCV131DX11 | VDC01 |  | 24VDC BCV131DX11 PLC Control Supply | Healthy |  | BCV131DX11 |  | 2.11\0.1:0 | BR4-2150-E-00159 | 0 |  | D | [6 empty] | F1 | 1
BCV131 | DX11 | DIO1 | 132 | 2 | 11 | 0 | 1 | 1 |  |  | DI | [9 empty] | 2.11\0.1:1 |  |  |  | S | [6 empty] | F1 | 2
BCV131 | DX11 | DIO1 | 132 | 2 | 11 | 0 | 1 | 2 |  |  | DI | [9 empty] | 2.11\0.1:2 |  |  |  | S | [6 empty] | F1 | 3
BCV131 | DX11 | DIO1 | 132 | 2 | 11 | 0 | 1 | 3 |  |  | DI | [9 empty] | 2.11\0.1:3 |  |  |  | S | [6 empty] | F1 | 4
BCV131 | DX11 | DIO1 | 132 | 2 | 11 | 0 | 1 | 4 |  |  | DI | [9 empty] | 2.11\0.1:4 |  |  |  | S | [6 empty] | F1 | 5
BCV131 | DX11 | DIO1 | 132 | 2 | 11 | 0 | 1 | 5 |  |  | DI | [9 empty] | 2.11\0.1:5 |  |  |  | S | [6 empty] | F1 | 6
BCV131 | DX11 | DIO1 | 132 | 2 | 11 | 0 | 1 | 6 |  |  | DI | [9 empty] | 2.11\0.1:6 |  |  |  | S | [6 empty] | F1 | 7
BCV131 | DX11 | DIO1 | 132 | 2 | 11 | 0 | 1 | 7 |  |  | DI | [9 empty] | 2.11\0.1:7 |  |  |  | S | [6 empty] | F1 | 8
BCV131 | DX11 | DIO1 | 132 | 2 | 11 | 0 | 1 | 8 |  |  | DI | 4 | BCV131BDS15 | BDS15 |  | Belt Drift Switch 15 | Healthy |  | BCV131 |  | 2.11\0.1:8 | BR4-2150-E-00160 | 0 |  | S | [6 empty] | F1 | 9 | 10
BCV131 | DX11 | DIO1 | 132 | 2 | 11 | 0 | 1 | 9 |  |  | DI | 4 | BCV131BDS16 | BDS16 |  | Belt Drift Switch 16 | Healthy |  | BCV131 |  | 2.11\0.1:9 | BR4-2150-E-00160 | 0 |  | S | [6 empty] | F1 | 11 | 12
BCV131 | DX11 | DIO1 | 132 | 2 | 11 | 0 | 1 | 10 |  |  | DI | 4 | BCV131BDS17 | BDS17 |  | Belt Drift Switch 17 | Healthy |  | BCV131 |  | 2.11\0.1:10 | BR4-2150-E-00160 | 0 |  | S | [6 empty] | F1 | 13 | 14
BCV131 | DX11 | DIO1 | 132 | 2 | 11 | 0 | 1 | 11 |  |  | DI | 4 | BCV131BDS18 | BDS18 |  | Belt Drift Switch 18 | Healthy |  | BCV131 |  | 2.11\0.1:11 | BR4-2150-E-00160 | 0 |  | S | [6 empty] | F1 | 15 | 16
BCV131 | DX11 | DIO1 | 132 | 2 | 11 | 0 | 1 | 12 |  |  | DI | [9 empty] | 2.11\0.1:12 |  |  |  | S | [6 empty] | F1 | 17 | 18
BCV131 | DX11 | DIO1 | 132 | 2 | 11 | 0 | 1 | 13 |  |  | DI | [9 empty] | 2.11\0.1:13 |  |  |  | S | [6 empty] | F1 | 19 | 20
BCV131 | DX11 | DIO1 | 132 | 2 | 11 | 0 | 1 | 14 |  |  | DI | [9 empty] | 2.11\0.1:14 |  |  |  | S | [6 empty] | F1 | 21 | 22
BCV131 | DX11 | DIO1 | 132 | 2 | 11 | 0 | 1 | 15 |  |  | DI | [9 empty] | 2.11\0.1:15 |  |  |  | S | [6 empty] | F1 | 23 | 24
BCV131 | DX11 | DIO1 | 132 | 2 | 11 | 0 | 1 | 16 |  |  | DI | [9 empty] | 2.11\0.1:16 |  |  |  | S | [6 empty] | F1 | 25 | 26
BCV131 | DX11 | DIO1 | 132 | 2 | 11 | 0 | 1 | 17 |  |  | DI | [9 empty] | 2.11\0.1:17 |  |  |  | S | [6 empty] | F1 | 27 | 28
BCV131 | DX11 | DIO1 | 132 | 2 | 11 | 0 | 1 | 18 |  |  | DI | [9 empty] | 2.11\0.1:18 |  |  |  | S | [6 empty] | F1 | 29 | 30
BCV131 | DX11 | DIO1 | 132 | 2 | 11 | 0 | 1 | 19 |  |  | DI | [9 empty] | 2.11\0.1:19 |  |  |  | S | [6 empty] | F1 | 31 | 32
BCV131 | DX11 | DIO1 | 132 | 2 | 11 | 0 | 1 | 20 |  |  | DI | [9 empty] | 2.11\0.1:20 |  |  |  | S | [6 empty] | F1 | 33 | 34
BCV131 | DX11 | DIO1 | 132 | 2 | 11 | 0 | 1 | 21 |  |  | DI | [9 empty] | 2.11\0.1:21 |  |  |  | S | [6 empty] | F1 | 35 | 36
BCV131 | DX11 | DIO1 | 132 | 2 | 11 | 0 | 1 | 22 |  |  | DI | [9 empty] | 2.11\0.1:22 |  |  |  | S | [6 empty] | F1 | 37 | 38
BCV131 | DX11 | DIO1 | 132 | 2 | 11 | 0 | 1 | 23 |  |  | DI | [9 empty] | 2.11\0.1:23 |  |  |  | S | [6 empty] | F1 | 39 | 40
BCV131 | DX11 | DIO1 | 132 | 2 | 11 | 0 | 1 | 24 |  |  | DI | [9 empty] | 2.11\0.1:24 |  |  |  | S | [6 empty] | F1 | 41 | 42
BCV131 | DX11 | DIO1 | 132 | 2 | 11 | 0 | 1 | 25 |  |  | DI | [9 empty] | 2.11\0.1:25 |  |  |  | S | [6 empty] | F1 | 43 | 44
BCV131 | DX11 | DIO1 | 132 | 2 | 11 | 0 | 1 | 26 |  |  | DI | [9 empty] | 2.11\0.1:26 |  |  |  | S | [6 empty] | F1 | 45 | 46
BCV131 | DX11 | DIO1 | 132 | 2 | 11 | 0 | 1 | 27 |  |  | DI | [9 empty] | 2.11\0.1:27 |  |  |  | S | [6 empty] | F1 | 47 | 48
BCV131 | DX11 | DIO1 | 132 | 2 | 11 | 0 | 1 | 28 |  |  | DI | [9 empty] | 2.11\0.1:28 |  |  |  | S | [6 empty] | F1 | 49 | 50
BCV131 | DX11 | DIO1 | 132 | 2 | 11 | 0 | 1 | 29 |  |  | DI | [9 empty] | 2.11\0.1:29 |  |  |  | S | [6 empty] | F1 | 51 | 52
BCV131 | DX11 | DIO1 | 132 | 2 | 11 | 0 | 1 | 30 |  |  | DI | [9 empty] | 2.11\0.1:30 |  |  |  | S | [6 empty] | F1 | 53 | 54
BCV131 | DX11 | DIO1 | 132 | 2 | 11 | 0 | 1 | 31 |  |  | DI | [9 empty] | 2.11\0.1:31 |  |  |  | S | [6 empty] | F1 | 55 | 56
BCV131 | DX11 | DIO1 | 132 | 2 | 11 | 0 | 2 |  |  | BMXXEM010 |  | 0 | [8 empty] | 2.11\0.2:
BCV131 | DX11 | DIO1 | 132 | 2 | 11 | 0 | 2 |  |  |  |  | 0 | [8 empty] | 2.11\0.2:
BCV131 | DX11 | DIO1 | 132 | 2 | 11 | 0 | 2 |  |  |  |  | 0 | [8 empty] | 2.11\0.2:
BCV131 | DX11 | DIO1 | 132 | 2 | 11 | 0 | 2 |  |  |  |  | 0 | [8 empty] | 2.11\0.2:
BCV131 | DX11 | DIO1 | 132 | 2 | 11 | 0 | 3 |  |  | BMXXEM010 |  | 0 | [8 empty] | 2.11\0.3:
BCV131 | DX11 | DIO1 | 132 | 2 | 11 | 0 | 3 |  |  |  |  | 0 | [8 empty] | 2.11\0.3:
BCV131 | DX11 | DIO1 | 132 | 2 | 11 | 0 | 3 |  |  |  |  | 0 | [8 empty] | 2.11\0.3:
BCV131 | DX11 | DIO1 | 132 | 2 | 11 | 0 | 3 |  |  |  |  | 0 | [8 empty] | 2.11\0.3: | [15 empty] | Earth
Earth
BCV131AX29 - BCV131 - 1336m
BCV131 | AX29 | SIO1 | SLC01 | 1 | 15 | 0 | 0 | CPU |  | 1059305 | Type 4 | 3 | [9 empty] | BR4-2150-E-00195 | 0
BCV131 | AX29 | SIO1 | SLC01 | 1 | 15 | 0 | 1 | 1 | I1 | 1044125 | SDI | 3 | BCV131PWS61 | PWS61A |  | Pullwire Switch 61 ChA | Healthy |  | BCV131 |  | 1.15\0.1:1 | BR4-2150-E-00195 | 0
BCV131 | AX29 | SIO1 | SLC01 | 1 | 15 | 0 | 1 | 2 | I2 | 1047162 | SDI | 3 | BCV131PWS61 | PWS61B |  | Pullwire Switch 61 ChB | Healthy |  | BCV131 |  | 1.15\0.1:2 | BR4-2150-E-00195 | 0
BCV131 | AX29 | SIO1 | SLC01 | 1 | 15 | 0 | 1 | 3 | I3 |  | SDI | 3 | BCV131PWS62 | PWS62A |  | Pullwire Switch 62 ChA | Healthy |  | BCV131 |  | 1.15\0.1:3 | BR4-2150-E-00195 | 0
BCV131 | AX29 | SIO1 | SLC01 | 1 | 15 | 0 | 1 | 4 | I4 |  | SDI | 3 | BCV131PWS62 | PWS62B |  | Pullwire Switch 62 ChB | Healthy |  | BCV131 |  | 1.15\0.1:4 | BR4-2150-E-00195 | 0
BCV131 | AX29 | SIO1 | SLC01 | 1 | 15 | 0 | 1 | 5 | I5 |  | SDI | 3 | [8 empty] | 1.15\0.1:5 | BR4-2150-E-00195 | 0
BCV131 | AX29 | SIO1 | SLC01 | 1 | 15 | 0 | 1 | 6 | I6 |  | SDI | 3 | [8 empty] | 1.15\0.1:6 | BR4-2150-E-00195 | 0
BCV131 | AX29 | SIO1 | SLC01 | 1 | 15 | 0 | 1 | 7 | I7 |  | SDI | 3 | [8 empty] | 1.15\0.1:7 | BR4-2150-E-00195 | 0
BCV131 | AX29 | SIO1 | SLC01 | 1 | 15 | 0 | 1 | 8 | I8 |  | SDI | 3 | [8 empty] | 1.15\0.1:8 | BR4-2150-E-00195 | 0
BCV131 | AX29 | SIO1 | SLC01 | 1 | 15 | 0 | 1 | 1 | Q1 | XTIO-Q | SDO | 3 | BCV131YA57 | YL57 |  | Start Up Warning (Beacon) | Active |  | BCV131 |  | 1.15\0.1:1 | BR4-2150-E-00195 | 0
BCV131 | AX29 | SIO1 | SLC01 | 1 | 15 | 0 | 1 | 2 | Q2 |  | SDO | 3 | BCV131YA57 | YA57 |  | Start Up Warning (Siren) | Active |  | BCV131 |  | 1.15\0.1:2 | BR4-2150-E-00195 | 0
BCV131 | AX29 | SIO1 | SLC01 | 1 | 15 | 0 | 1 | 3 | Q3 |  | SDO | 3 | BCV131YA58 | YA58 |  | Start Up Warning (Siren) | Active |  | BCV131 |  | 1.15\0.1:3 | BR4-2150-E-00195 | 0
BCV131 | AX29 | SIO1 | SLC01 | 1 | 15 | 0 | 1 | 4 | Q4 |  | SDO | 3 | [8 empty] | 1.15\0.1:4 | BR4-2150-E-00195 | 0
BCV131AX30 - BCV131 - 1093m
BCV131 | AX30 | SIO1 | SLC02 | 2 | 15 | 0 | 0 | CPU |  | 1059305 | Type 4 | 3 | [9 empty] | BR4-2150-E-00196 | 0
BCV131 | AX30 | SIO1 | SLC02 | 2 | 15 | 0 | 1 | 1 | I1 | 1044125 | SDI | 3 | BCV131PWS63 | PWS63A |  | Pullwire Switch 63 ChA | Healthy |  | BCV131 |  | 2.15\0.1:1 | BR4-2150-E-00196 | 0
BCV131 | AX30 | SIO1 | SLC02 | 2 | 15 | 0 | 1 | 2 | I2 | 1047162 | SDI | 3 | BCV131PWS63 | PWS63B |  | Pullwire Switch 63 ChB | Healthy |  | BCV131 |  | 2.15\0.1:2 | BR4-2150-E-00196 | 0
BCV131 | AX30 | SIO1 | SLC02 | 2 | 15 | 0 | 1 | 3 | I3 |  | SDI | 3 | BCV131PWS64 | PWS64A |  | Pullwire Switch 64 ChA | Healthy |  | BCV131 |  | 2.15\0.1:3 | BR4-2150-E-00196 | 0
BCV131 | AX30 | SIO1 | SLC02 | 2 | 15 | 0 | 1 | 4 | I4 |  | SDI | 3 | BCV131PWS64 | PWS64B |  | Pullwire Switch 64 ChB | Healthy |  | BCV131 |  | 2.15\0.1:4 | BR4-2150-E-00196 | 0
BCV131 | AX30 | SIO1 | SLC02 | 2 | 15 | 0 | 1 | 5 | I5 |  | SDI | 3 | [8 empty] | 2.15\0.1:5 | BR4-2150-E-00196 | 0
BCV131 | AX30 | SIO1 | SLC02 | 2 | 15 | 0 | 1 | 6 | I6 |  | SDI | 3 | [8 empty] | 2.15\0.1:6 | BR4-2150-E-00196 | 0
BCV131 | AX30 | SIO1 | SLC02 | 2 | 15 | 0 | 1 | 7 | I7 |  | SDI | 3 | [8 empty] | 2.15\0.1:7 | BR4-2150-E-00196 | 0
BCV131 | AX30 | SIO1 | SLC02 | 2 | 15 | 0 | 1 | 8 | I8 |  | SDI | 3 | [8 empty] | 2.15\0.1:8 | BR4-2150-E-00196 | 0
BCV131 | AX30 | SIO1 | SLC02 | 2 | 15 | 0 | 1 | 1 | Q1 | XTIO-Q | SDO | 3 | BCV131YA59 | YL59 |  | Start Up Warning (Beacon) | Active |  | BCV131 |  | 2.15\0.1:1 | BR4-2150-E-00196 | 0
BCV131 | AX30 | SIO1 | SLC02 | 2 | 15 | 0 | 1 | 2 | Q2 |  | SDO | 3 | BCV131YA59 | YA59 |  | Start Up Warning (Siren) | Active |  | BCV131 |  | 2.15\0.1:2 | BR4-2150-E-00196 | 0
BCV131 | AX30 | SIO1 | SLC02 | 2 | 15 | 0 | 1 | 3 | Q3 |  | SDO | 3 | BCV131YA60 | YA60 |  | Start Up Warning (Siren) | Active |  | BCV131 |  | 2.15\0.1:3 | BR4-2150-E-00196 | 0
BCV131 | AX30 | SIO1 | SLC02 | 2 | 15 | 0 | 1 | 4 | Q4 |  | SDO | 3 | [8 empty] | 2.15\0.1:4 | BR4-2150-E-00196 | 0
BCV131AX31 - BCV131 - 850m
BCV131 | AX31 | SIO1 | SLC01 | 1 | 16 | 0 | 0 | CPU |  | 1059305 | Type 4 | 3 | [9 empty] | BR4-2150-E-00197 | 0
BCV131 | AX31 | SIO1 | SLC01 | 1 | 16 | 0 | 1 | 1 | I1 | 1044125 | SDI | 3 | BCV131PWS65 | PWS65A |  | Pullwire Switch 65 ChA | Healthy |  | BCV131 |  | 1.16\0.1:1 | BR4-2150-E-00197 | 0
BCV131 | AX31 | SIO1 | SLC01 | 1 | 16 | 0 | 1 | 2 | I2 | 1047162 | SDI | 3 | BCV131PWS65 | PWS65B |  | Pullwire Switch 65 ChB | Healthy |  | BCV131 |  | 1.16\0.1:2 | BR4-2150-E-00197 | 0
BCV131 | AX31 | SIO1 | SLC01 | 1 | 16 | 0 | 1 | 3 | I3 |  | SDI | 3 | BCV131PWS66 | PWS66A |  | Pullwire Switch 66 ChA | Healthy |  | BCV131 |  | 1.16\0.1:3 | BR4-2150-E-00197 | 0
BCV131 | AX31 | SIO1 | SLC01 | 1 | 16 | 0 | 1 | 4 | I4 |  | SDI | 3 | BCV131PWS66 | PWS66B |  | Pullwire Switch 66 ChB | Healthy |  | BCV131 |  | 1.16\0.1:4 | BR4-2150-E-00197 | 0
BCV131 | AX31 | SIO1 | SLC01 | 1 | 16 | 0 | 1 | 5 | I5 |  | SDI | 3 | [8 empty] | 1.16\0.1:5 | BR4-2150-E-00197 | 0
BCV131 | AX31 | SIO1 | SLC01 | 1 | 16 | 0 | 1 | 6 | I6 |  | SDI | 3 | [8 empty] | 1.16\0.1:6 | BR4-2150-E-00197 | 0
BCV131 | AX31 | SIO1 | SLC01 | 1 | 16 | 0 | 1 | 7 | I7 |  | SDI | 3 | [8 empty] | 1.16\0.1:7 | BR4-2150-E-00197 | 0
BCV131 | AX31 | SIO1 | SLC01 | 1 | 16 | 0 | 1 | 8 | I8 |  | SDI | 3 | [8 empty] | 1.16\0.1:8 | BR4-2150-E-00197 | 0
BCV131 | AX31 | SIO1 | SLC01 | 1 | 16 | 0 | 1 | 1 | Q1 | XTIO-Q | SDO | 3 | BCV131YA61 | YL61 |  | Start Up Warning (Beacon) | Active |  | BCV131 |  | 1.16\0.1:1 | BR4-2150-E-00197 | 0
BCV131 | AX31 | SIO1 | SLC01 | 1 | 16 | 0 | 1 | 2 | Q2 |  | SDO | 3 | BCV131YA61 | YA61 |  | Start Up Warning (Siren) | Active |  | BCV131 |  | 1.16\0.1:2 | BR4-2150-E-00197 | 0
BCV131 | AX31 | SIO1 | SLC01 | 1 | 16 | 0 | 1 | 3 | Q3 |  | SDO | 3 | BCV131YA62 | YA62 |  | Start Up Warning (Siren) | Active |  | BCV131 |  | 1.16\0.1:3 | BR4-2150-E-00197 | 0
BCV131 | AX31 | SIO1 | SLC01 | 1 | 16 | 0 | 1 | 4 | Q4 |  | SDO | 3 | [8 empty] | 1.16\0.1:4 | BR4-2150-E-00197 | 0
BCV131AX32 - BCV131 - 607m
BCV131 | AX32 | SIO1 | SLC02 | 2 | 16 | 0 | 0 | CPU |  | 1059305 | Type 4 | 3 | [9 empty] | BR4-2150-E-00198 | 0
BCV131 | AX32 | SIO1 | SLC02 | 2 | 16 | 0 | 1 | 1 | I1 | 1044125 | SDI | 3 | BCV131PWS67 | PWS67A |  | Pullwire Switch 67 ChA | Healthy |  | BCV131 |  | 2.16\0.1:1 | BR4-2150-E-00198 | 0
BCV131 | AX32 | SIO1 | SLC02 | 2 | 16 | 0 | 1 | 2 | I2 | 1047162 | SDI | 3 | BCV131PWS67 | PWS67B |  | Pullwire Switch 67 ChB | Healthy |  | BCV131 |  | 2.16\0.1:2 | BR4-2150-E-00198 | 0
BCV131 | AX32 | SIO1 | SLC02 | 2 | 16 | 0 | 1 | 3 | I3 |  | SDI | 3 | BCV131PWS68 | PWS68A |  | Pullwire Switch 68 ChA | Healthy |  | BCV131 |  | 2.16\0.1:3 | BR4-2150-E-00198 | 0
BCV131 | AX32 | SIO1 | SLC02 | 2 | 16 | 0 | 1 | 4 | I4 |  | SDI | 3 | BCV131PWS68 | PWS68B |  | Pullwire Switch 68 ChB | Healthy |  | BCV131 |  | 2.16\0.1:4 | BR4-2150-E-00198 | 0
BCV131 | AX32 | SIO1 | SLC02 | 2 | 16 | 0 | 1 | 5 | I5 |  | SDI | 3 | [8 empty] | 2.16\0.1:5 | BR4-2150-E-00198 | 0
BCV131 | AX32 | SIO1 | SLC02 | 2 | 16 | 0 | 1 | 6 | I6 |  | SDI | 3 | [8 empty] | 2.16\0.1:6 | BR4-2150-E-00198 | 0
BCV131 | AX32 | SIO1 | SLC02 | 2 | 16 | 0 | 1 | 7 | I7 |  | SDI | 3 | [8 empty] | 2.16\0.1:7 | BR4-2150-E-00198 | 0
BCV131 | AX32 | SIO1 | SLC02 | 2 | 16 | 0 | 1 | 8 | I8 |  | SDI | 3 | [8 empty] | 2.16\0.1:8 | BR4-2150-E-00198 | 0
BCV131 | AX32 | SIO1 | SLC02 | 2 | 16 | 0 | 1 | 1 | Q1 | XTIO-Q | SDO | 3 | BCV131YA63 | YL63 |  | Start Up Warning (Beacon) | Active |  | BCV131 |  | 2.16\0.1:1 | BR4-2150-E-00198 | 0
BCV131 | AX32 | SIO1 | SLC02 | 2 | 16 | 0 | 1 | 2 | Q2 |  | SDO | 3 | BCV131YA63 | YA63 |  | Start Up Warning (Siren) | Active |  | BCV131 |  | 2.16\0.1:2 | BR4-2150-E-00198 | 0
BCV131 | AX32 | SIO1 | SLC02 | 2 | 16 | 0 | 1 | 3 | Q3 |  | SDO | 3 | BCV131YA64 | YA64 |  | Start Up Warning (Siren) | Active |  | BCV131 |  | 2.16\0.1:3 | BR4-2150-E-00198 | 0
BCV131 | AX32 | SIO1 | SLC02 | 2 | 16 | 0 | 1 | 4 | Q4 |  | SDO | 3 | [8 empty] | 2.16\0.1:4 | BR4-2150-E-00198 | 0
BCV131AX33 - BCV131 - 364m
BCV131 | AX33 | SIO1 | SLC01 | 1 | 17 | 0 | 0 | CPU |  | 1059305 | Type 4 | 3 | [9 empty] | BR4-2150-E-00199 | 0
BCV131 | AX33 | SIO1 | SLC01 | 1 | 17 | 0 | 1 | 1 | I1 | 1044125 | SDI | 3 | BCV131PWS69 | PWS69A |  | Pullwire Switch 69 ChA | Healthy |  | BCV131 |  | 1.17\0.1:1 | BR4-2150-E-00199 | 0
BCV131 | AX33 | SIO1 | SLC01 | 1 | 17 | 0 | 1 | 2 | I2 | 1047162 | SDI | 3 | BCV131PWS69 | PWS69B |  | Pullwire Switch 69 ChB | Healthy |  | BCV131 |  | 1.17\0.1:2 | BR4-2150-E-00199 | 0
BCV131 | AX33 | SIO1 | SLC01 | 1 | 17 | 0 | 1 | 3 | I3 |  | SDI | 3 | BCV131PWS70 | PWS70A |  | Pullwire Switch 70 ChA | Healthy |  | BCV131 |  | 1.17\0.1:3 | BR4-2150-E-00199 | 0
BCV131 | AX33 | SIO1 | SLC01 | 1 | 17 | 0 | 1 | 4 | I4 |  | SDI | 3 | BCV131PWS70 | PWS70B |  | Pullwire Switch 70 ChB | Healthy |  | BCV131 |  | 1.17\0.1:4 | BR4-2150-E-00199 | 0
BCV131 | AX33 | SIO1 | SLC01 | 1 | 17 | 0 | 1 | 5 | I5 |  | SDI | 3 | [8 empty] | 1.17\0.1:5 | BR4-2150-E-00199 | 0
BCV131 | AX33 | SIO1 | SLC01 | 1 | 17 | 0 | 1 | 6 | I6 |  | SDI | 3 | [8 empty] | 1.17\0.1:6 | BR4-2150-E-00199 | 0
BCV131 | AX33 | SIO1 | SLC01 | 1 | 17 | 0 | 1 | 7 | I7 |  | SDI | 3 | [8 empty] | 1.17\0.1:7 | BR4-2150-E-00199 | 0
BCV131 | AX33 | SIO1 | SLC01 | 1 | 17 | 0 | 1 | 8 | I8 |  | SDI | 3 | [8 empty] | 1.17\0.1:8 | BR4-2150-E-00199 | 0
BCV131 | AX33 | SIO1 | SLC01 | 1 | 17 | 0 | 1 | 1 | Q1 | XTIO-Q | SDO | 3 | BCV131YA65 | YL65 |  | Start Up Warning (Beacon) | Active |  | BCV131 |  | 1.17\0.1:1 | BR4-2150-E-00199 | 0
BCV131 | AX33 | SIO1 | SLC01 | 1 | 17 | 0 | 1 | 2 | Q2 |  | SDO | 3 | BCV131YA65 | YA65 |  | Start Up Warning (Siren) | Active |  | BCV131 |  | 1.17\0.1:2 | BR4-2150-E-00199 | 0
BCV131 | AX33 | SIO1 | SLC01 | 1 | 17 | 0 | 1 | 3 | Q3 |  | SDO | 3 | BCV131YA66 | YA66 |  | Start Up Warning (Siren) | Active |  | BCV131 |  | 1.17\0.1:3 | BR4-2150-E-00199 | 0
BCV131 | AX33 | SIO1 | SLC01 | 1 | 17 | 0 | 1 | 4 | Q4 |  | SDO | 3 | [8 empty] | 1.17\0.1:4 | BR4-2150-E-00199 | 0
BCV131AX34 - BCV131 - 121m
BCV131 | AX34 | SIO1 | SLC02 | 2 | 17 | 0 | 0 | CPU |  | 1059305 | Type 7
BCV131 | AX34 | SIO1 | SLC02 | 2 | 17 | 0 | 1 | 1 | I1 | 1044125 | SDI | 3 | BCV131PWS71 | PWS71A |  | Pullwire Switch 71 ChA | Healthy |  | BCV131 |  | 2.17\0.1:1 | BR4-2150-E-00200 | 0
BCV131 | AX34 | SIO1 | SLC02 | 2 | 17 | 0 | 1 | 2 | I2 | 1047162 | SDI | 3 | BCV131PWS71 | PWS71B |  | Pullwire Switch 71 ChB | Healthy |  | BCV131 |  | 2.17\0.1:2 | BR4-2150-E-00200 | 0
BCV131 | AX34 | SIO1 | SLC02 | 2 | 17 | 0 | 1 | 3 | I3 |  | SDI | 3 | BCV131PWS72 | PWS72A |  | Pullwire Switch 72 ChA | Healthy |  | BCV131 |  | 2.17\0.1:3 | BR4-2150-E-00200 | 0
BCV131 | AX34 | SIO1 | SLC02 | 2 | 17 | 0 | 1 | 4 | I4 |  | SDI | 3 | BCV131PWS72 | PWS72B |  | Pullwire Switch 72 ChB | Healthy |  | BCV131 |  | 2.17\0.1:4 | BR4-2150-E-00200 | 0
BCV131 | AX34 | SIO1 | SLC02 | 2 | 17 | 0 | 1 | 5 | I5 |  | SDI | 3 | BCV131PWS73 | PWS73A |  | Pullwire Switch 73 ChA | Healthy |  | BCV131 |  | 2.17\0.1:5 | BR4-2150-E-00200 | 0
BCV131 | AX34 | SIO1 | SLC02 | 2 | 17 | 0 | 1 | 6 | I6 |  | SDI | 3 | BCV131PWS73 | PWS73B |  | Pullwire Switch 73 ChB | Healthy |  | BCV131 |  | 2.17\0.1:6 | BR4-2150-E-00200 | 0
BCV131 | AX34 | SIO1 | SLC02 | 2 | 17 | 0 | 1 | 7 | I7 |  | SDI | 3 | BCV131PWS74 | PWS74A |  | Pullwire Switch 74 ChA | Healthy |  | BCV131 |  | 2.17\0.1:7 | BR4-2150-E-00200 | 0
BCV131 | AX34 | SIO1 | SLC02 | 2 | 17 | 0 | 1 | 8 | I8 |  | SDI | 3 | BCV131PWS74 | PWS74B |  | Pullwire Switch 74 ChB | Healthy |  | BCV131 |  | 2.17\0.1:8 | BR4-2150-E-00200 | 0
BCV131 | AX34 | SIO1 | SLC02 | 2 | 17 | 0 | 1 | 1 | Q1 |  | SDO | 3 | BCV131YA67 | YL67 |  | Start Up Warning (Beacon) | Active |  | BCV131 |  | 2.17\0.1:1 | BR4-2150-E-00200 | 0
BCV131 | AX34 | SIO1 | SLC02 | 2 | 17 | 0 | 1 | 2 | Q2 |  | SDO | 3 | BCV131YA67 | YA67 |  | Start Up Warning (Siren) | Active |  | BCV131 |  | 2.17\0.1:2 | BR4-2150-E-00200 | 0
BCV131 | AX34 | SIO1 | SLC02 | 2 | 17 | 0 | 1 | 3 | Q3 |  | SDO | 3 | BCV131YA68 | YA68 |  | Start Up Warning (Siren) | Active |  | BCV131 |  | 2.17\0.1:3 | BR4-2150-E-00200 | 0
BCV131 | AX34 | SIO1 | SLC02 | 2 | 17 | 0 | 1 | 4 | Q4 |  | SDO | 3 | [8 empty] | 2.17\0.1:4 | BR4-2150-E-00200 | 0
BCV131 | AX34 | SIO1 | SLC02 | 2 | 17 | 0 | 2 | 1 | I1 | 1044125 | SDI | 3 | BCV131LCS04 | LOS04A |  | Lock Off Stop 4 ChA | Healthy |  | BCV131 |  | 2.17\0.2:1 | BR4-2150-E-00200 | 0
BCV131 | AX34 | SIO1 | SLC02 | 2 | 17 | 0 | 2 | 2 | I2 |  | SDI | 3 | BCV131LCS04 | LOS04B |  | Lock Off Stop 4 ChB | Healthy |  | BCV131 |  | 2.17\0.2:2 | BR4-2150-E-00200 | 0
BCV131 | AX34 | SIO1 | SLC02 | 2 | 17 | 0 | 2 | 3 | I3 |  | SDI | 3 | BCV131BK01LCS01 | LOS01A |  | Lock Off Stop 1 ChA | Healthy |  | BCV131BK01 |  | 2.17\0.2:3 | BR4-2150-E-00200 | 0
BCV131 | AX34 | SIO1 | SLC02 | 2 | 17 | 0 | 2 | 4 | I4 |  | SDI | 3 | BCV131BK01LCS01 | LOS01B |  | Lock Off Stop 1 ChB | Healthy |  | BCV131BK01 |  | 2.17\0.2:4 | BR4-2150-E-00200 | 0
BCV131 | AX34 | SIO1 | SLC02 | 2 | 17 | 0 | 2 | 5 | I5 |  | SDI | 3 | BCV131BK02LCS01 | LOS01A |  | Lock Off Stop 2 ChA | Healthy |  | BCV131BK02 |  | 2.17\0.2:5 | BR4-2150-E-00200 | 0
BCV131 | AX34 | SIO1 | SLC02 | 2 | 17 | 0 | 2 | 6 | I6 |  | SDI | 3 | BCV131BK02LCS01 | LOS01B |  | Lock Off Stop 2 ChB | Healthy |  | BCV131BK02 |  | 2.17\0.2:6 | BR4-2150-E-00200 | 0
BCV131 | AX34 | SIO1 | SLC02 | 2 | 17 | 0 | 2 | 7 | I7 |  | SDI | 3 | [8 empty] | 2.17\0.2:7 | BR4-2150-E-00200 | 0
BCV131 | AX34 | SIO1 | SLC02 | 2 | 17 | 0 | 2 | 8 | I8 |  | SDI | 3 | [8 empty] | 2.17\0.2:8 | BR4-2150-E-00200 | 0
BCV131 | AX34 | SIO1 | SLC02 | 2 | 17 | 0 | 2 | 1 | Q1 |  | SDO | 3 | [8 empty] | 2.17\0.2:1 | BR4-2150-E-00200 | 0
BCV131 | AX34 | SIO1 | SLC02 | 2 | 17 | 0 | 2 | 2 | Q2 |  | SDO | 3 | [8 empty] | 2.17\0.2:2 | BR4-2150-E-00200 | 0
BCV131 | AX34 | SIO1 | SLC02 | 2 | 17 | 0 | 2 | 3 | Q3 |  | SDO | 3 | [8 empty] | 2.17\0.2:3 | BR4-2150-E-00200 | 0
BCV131 | AX34 | SIO1 | SLC02 | 2 | 17 | 0 | 2 | 4 | Q4 |  | SDO | 3 | [8 empty] | 2.17\0.2:4 | BR4-2150-E-00200 | 0
BCV131DX12 - BCV131 - Tail End
EIO node #12 | DX12 | DIO1 | 132 | 2 | 12 | 0
BCV131 | DX12 | DIO1 | 132 | 2 | 12 | 0 |  | Chassis |  | BMEXBP1200
BCV131 | DX12 | DIO1 | 132 | 2 | 12 | 0 |  | Power |  | BMXCPS4022 |  | total |  | spare |  | % spare
BCV131 | DX12 | DIO1 | 132 | 2 | 12 | 0 | 0 | Comms |  | BMECRA31210 | I/O1 | 96 |  | 60 |  | 62.5%
BCV131 | DX12 | DIO1 | 132 | 2 | 12 | 0 | 1 | 0 | BMXFCW303 | BMXDDI3202K | DI | 3 |  | CB01 |  | 240VAC Circuit Breaker - Spare | Closed | Q106 | BCV131DX12 |  | 2.12\0.1:0 | BR4-2150-E-00161 | 0 |  | D | [6 empty] | F1 |  | 1
BCV131 | DX12 | DIO1 | 132 | 2 | 12 | 0 | 1 | 1 |  |  | DI | 3 |  | VDC01 |  | 24VDC DIO1 Output Control Supply | Healthy | Q143 | BCV131DX12 |  | 2.12\0.1:1 | BR4-2150-E-00161 | 0 |  | D | [6 empty] | F1 |  | 2
BCV131 | DX12 | DIO1 | 132 | 2 | 12 | 0 | 1 | 2 |  |  | DI | 3 |  | VDC02 |  | 24VDC GW1 Control Supply | Healthy | Q157 | BCV131DX12 |  | 2.12\0.1:2 | BR4-2150-E-00161 | 0 |  | D | [6 empty] | F1 |  | 3
BCV131 | DX12 | DIO1 | 132 | 2 | 12 | 0 | 1 | 3 |  |  | DI | 3 |  | VDC03 |  | 24VDC Instrument Supply | Healthy | Q164 | BCV131DX12 |  | 2.12\0.1:3 | BR4-2150-E-00161 | 0 |  | D | [6 empty] | F1 |  | 4
BCV131 | DX12 | DIO1 | 132 | 2 | 12 | 0 | 1 | 4 |  |  | DI | 3 |  | VDC04 |  | 24VDC Transmitter Supply | Healthy | Q168 | BCV131DX12 |  | 2.12\0.1:4 | BR4-2150-E-00161 | 0 |  | D | [6 empty] | F1 |  | 5
BCV131 | DX12 | DIO1 | 132 | 2 | 12 | 0 | 1 | 5 |  |  | DI | 3 |  | VDC05 |  | 24VDC BCV131DX12 Control Supply | Healthy | Q172 | BCV131DX12 |  | 2.12\0.1:5 | BR4-2150-E-00161 | 0 |  | D | [6 empty] | F1 |  | 6
BCV131 | DX12 | DIO1 | 132 | 2 | 12 | 0 | 1 | 6 |  |  | DI | 3 |  | VDC06 |  | 24VDC BCV131BK01 Control Supply | Healthy | Q176 | BCV131DX12 |  | 2.12\0.1:6 | BR4-2150-E-00161 | 0 |  | D | [6 empty] | F1 |  | 7
BCV131 | DX12 | DIO1 | 132 | 2 | 12 | 0 | 1 | 7 |  |  | DI | 3 |  | VDC07 |  | 24VDC BCV131BK02 Control Supply | Healthy | Q180 | BCV131DX12 |  | 2.12\0.1:7 | BR4-2150-E-00161 | 0 |  | D | [6 empty] | F1 |  | 8
BCV131 | DX12 | DIO1 | 132 | 2 | 12 | 0 | 1 | 8 |  |  | DI | 3 |  | VDC08 |  | 24VDC Spare Control Supply | Healthy | Q184 | BCV131DX12 |  | 2.12\0.1:8 | BR4-2150-E-00161 | 0 |  | D | [6 empty] | F1 |  | 9
BCV131 | DX12 | DIO1 | 132 | 2 | 12 | 0 | 1 | 9 |  |  | DI | 3 |  | VDC09 |  | 24VDC Spare Control Supply | Healthy | Q188 | BCV131DX12 |  | 2.12\0.1:9 | BR4-2150-E-00161 | 0 |  | D | [6 empty] | F1 |  | 10
BCV131 | DX12 | DIO1 | 132 | 2 | 12 | 0 | 1 | 10 |  |  | DI | 3 |  | VDC10 |  | 24VDC Spare Control Supply | Healthy | Q192 | BCV131DX12 |  | 2.12\0.1:10 | BR4-2150-E-00161 | 0 |  | D | [6 empty] | F1 |  | 11
BCV131 | DX12 | DIO1 | 132 | 2 | 12 | 0 | 1 | 11 |  |  | DI | 3 |  | VDC11 |  | 24VDC Spare Control Supply | Healthy | Q196 | BCV131DX12 |  | 2.12\0.1:11 | BR4-2150-E-00161 | 0 |  | D | [6 empty] | F1 |  | 12
BCV131 | DX12 | DIO1 | 132 | 2 | 12 | 0 | 1 | 12 |  |  | DI | [9 empty] | 2.12\0.1:12 |  |  |  | S | [6 empty] | F1 |  | 13
BCV131 | DX12 | DIO1 | 132 | 2 | 12 | 0 | 1 | 13 |  |  | DI | [9 empty] | 2.12\0.1:13 |  |  |  | S | [6 empty] | F1 |  | 14
BCV131 | DX12 | DIO1 | 132 | 2 | 12 | 0 | 1 | 14 |  |  | DI | [9 empty] | 2.12\0.1:14 |  |  |  | S | [6 empty] | F1 |  | 15
BCV131 | DX12 | DIO1 | 132 | 2 | 12 | 0 | 1 | 15 |  |  | DI | [9 empty] | 2.12\0.1:15 |  |  |  | S | [6 empty] | F1 |  | 16
BCV131 | DX12 | DIO1 | 132 | 2 | 12 | 0 | 1 | 16 |  |  | DI | 4 | BCV131BDS19 | BDS19 |  | Belt Drift Switch 19 | Healthy |  | BCV131 |  | 2.12\0.1:16 | BR4-2150-E-00162 | 0 |  | S | [6 empty] | F1 | 17 | 18
BCV131 | DX12 | DIO1 | 132 | 2 | 12 | 0 | 1 | 17 |  |  | DI | 4 | BCV131BDS20 | BDS20 |  | Belt Drift Switch 20 | Healthy |  | BCV131 |  | 2.12\0.1:17 | BR4-2150-E-00162 | 0 |  | S | [6 empty] | F1 | 19 | 20
BCV131 | DX12 | DIO1 | 132 | 2 | 12 | 0 | 1 | 18 |  |  | DI | 4 | BCV131BDS21 | BDS21 |  | Belt Drift Switch 21 | Healthy |  | BCV131 |  | 2.12\0.1:18 | BR4-2150-E-00162 | 0 |  | S | [6 empty] | F1 | 21 | 22
BCV131 | DX12 | DIO1 | 132 | 2 | 12 | 0 | 1 | 19 |  |  | DI | 4 | BCV131BDS22 | BDS22 |  | Belt Drift Switch 22 | Healthy |  | BCV131 |  | 2.12\0.1:19 | BR4-2150-E-00162 | 0 |  | S | [6 empty] | F1 | 23 | 24
BCV131 | DX12 | DIO1 | 132 | 2 | 12 | 0 | 1 | 20 |  |  | DI | 4 | BCV131BRS01 | BRS01 | String | Rip Detector Switch 1 | Healthy |  | BCV131 |  | 2.12\0.1:20 | BR4-2150-E-00162 | 0 |  | S | [6 empty] | F1 | 25 | 26
BCV131 | DX12 | DIO1 | 132 | 2 | 12 | 0 | 1 | 21 |  |  | DI | 4 | BCV131BRS02 | BRS02 | Pan | Rip Detector Switch 2 | Healthy |  | BCV131 |  | 2.12\0.1:21 | BR4-2150-E-00162 | 0 |  | S | [6 empty] | F1 | 27 | 28
BCV131 | DX12 | DIO1 | 132 | 2 | 12 | 0 | 1 | 22 |  |  | DI | 4 | BCV131BRS03 | BRS03 | String | Rip Detector Switch 3 | Healthy |  | BCV131 |  | 2.12\0.1:22 | BR4-2150-E-00162 | 0 |  | S | [6 empty] | F1 | 29 | 30
BCV131 | DX12 | DIO1 | 132 | 2 | 12 | 0 | 1 | 23 |  |  | DI | 4 | BCV131LCS04 | STT01 |  | Local Start Pushbutton - Overland Conveyor | Activated |  | BCV131 |  | 2.12\0.1:23 | BR4-2150-E-00162 | 0 |  | S | [6 empty] | F1 | 31 | 32
BCV131 | DX12 | DIO1 | 132 | 2 | 12 | 0 | 1 | 24 |  |  | DI | 4 | BCV131LCS04 | STP01 |  | Local Stop Pushbutton - Overland Conveyor | Activated |  | BCV131 |  | 2.12\0.1:24 | BR4-2150-E-00162 | 0 |  | S | [6 empty] | F1 | 33 | 34
BCV131 | DX12 | DIO1 | 132 | 2 | 12 | 0 | 1 | 25 |  |  | DI | [9 empty] | 2.12\0.1:25 |  |  |  | S | [6 empty] | F1 | 35 | 36
BCV131 | DX12 | DIO1 | 132 | 2 | 12 | 0 | 1 | 26 |  |  | DI | [9 empty] | 2.12\0.1:26 |  |  |  | S | [6 empty] | F1 | 37 | 38
BCV131 | DX12 | DIO1 | 132 | 2 | 12 | 0 | 1 | 27 |  |  | DI | [9 empty] | 2.12\0.1:27 |  |  |  | S | [6 empty] | F1 | 39 | 40
BCV131 | DX12 | DIO1 | 132 | 2 | 12 | 0 | 1 | 28 |  |  | DI | [9 empty] | 2.12\0.1:28 |  |  |  | S | [6 empty] | F1 | 41 | 42
BCV131 | DX12 | DIO1 | 132 | 2 | 12 | 0 | 1 | 29 |  |  | DI | [9 empty] | 2.12\0.1:29 |  |  |  | S | [6 empty] | F1 | 43 | 44
BCV131 | DX12 | DIO1 | 132 | 2 | 12 | 0 | 1 | 30 |  |  | DI | [9 empty] | 2.12\0.1:30 |  |  |  | S | [6 empty] | F1 | 45 | 46
BCV131 | DX12 | DIO1 | 132 | 2 | 12 | 0 | 1 | 31 |  |  | DI | [9 empty] | 2.12\0.1:31 |  |  |  | S | [6 empty] | F1 | 47 | 48
BCV131 | DX12 | DIO1 | 132 | 2 | 12 | 0 | 2 | 0 | BMXFCW303 | BMXDDI3202K | DI | 6 | BCV131BK01ZS01A | ZS01A | BCV131 TAIL BRAKE 1 CALIPER 1 | RHS Position Switch | Lifted |  | BCV131BK01 |  | 2.12\0.2:0 | BR4-2150-E-00163 | 0 |  | S | [6 empty] | F2 | 1 | 2
BCV131 | DX12 | DIO1 | 132 | 2 | 12 | 0 | 2 | 1 |  |  | DI | 6 | BCV131BK01ZS01B | ZS01B | BCV131 TAIL BRAKE 1 CALIPER 1 | RHS Position Switch | Worn |  | BCV131BK01 |  | 2.12\0.2:1 | BR4-2150-E-00163 | 0 |  | S | [6 empty] | F2 | 3 | 4
BCV131 | DX12 | DIO1 | 132 | 2 | 12 | 0 | 2 | 2 |  |  | DI | 4 | BCV131BK01PS01 | PS01 | BCV131 TAIL BRAKE | BCV131 Tail Brake Pressure Switch 1 | Lifted |  | BCV131BK01 |  | 2.12\0.2:2 | BR4-2150-E-00162 | 0 |  | S | [6 empty] | F2 | 5 | 6
BCV131 | DX12 | DIO1 | 132 | 2 | 12 | 0 | 2 | 3 |  |  | DI | 4 | BCV131BK01PS02 | PS02 | BCV131 TAIL BRAKE | BCV131 Tail Brake Pressure Switch 2 | Low |  | BCV131BK01 |  | 2.12\0.2:3 | BR4-2150-E-00162 | 0 |  | S | [6 empty] | F2 | 7 | 8
BCV131 | DX12 | DIO1 | 132 | 2 | 12 | 0 | 2 | 4 |  |  | DI | 4 | BCV131BK01UI01 | LS01 | BCV131 TAIL BRAKE | BCV131 Tail Brake 1 Oil Level | Low |  | BCV131BK01UI01 |  | 2.12\0.2:4 | BR4-2150-E-00163 | 0 |  | S | [6 empty] | F2 | 9 | 10
BCV131 | DX12 | DIO1 | 132 | 2 | 12 | 0 | 2 | 5 |  |  | DI | 4 | BCV131BK01UI01 | TS01 | BCV131 TAIL BRAKE | BCV131 Tail Brake 1 Temperature Switch | High |  | BCV131BK01UI01 |  | 2.12\0.2:5 | BR4-2150-E-00163 | 0 |  | S | [6 empty] | F2 | 11 | 12
BCV131 | DX12 | DIO1 | 132 | 2 | 12 | 0 | 2 | 6 |  |  | DI | 4 | BCV131BK01LCS01 | STT01 | BCV131 TAIL BRAKE | BCV131 Tail Brake Start Pushbutton | Activated |  | BCV131BK01 |  | 2.12\0.2:6 | BR4-2110-E-00218 | A |  | S | [6 empty] | F2 | 13 | 14
BCV131 | DX12 | DIO1 | 132 | 2 | 12 | 0 | 2 | 7 |  |  | DI | 4 | BCV131BK01LCS01 | STP01 | BCV131 TAIL BRAKE | BCV131 Tail Brake Stop Pushbutton | Activated |  | BCV131BK01 |  | 2.12\0.2:7 | BR4-2110-E-00218 | A |  | S | [6 empty] | F2 | 15 | 16
BCV131 | DX12 | DIO1 | 132 | 2 | 12 | 0 | 2 | 8 |  |  | DI | 6 | BCV131BK02ZS01 | ZS01A | BCV131 TAIL BRAKE 2 CALIPER 1 | RHS Position Switch | Lifted |  | BCV131BK02 |  | 2.12\0.2:8 | BR4-2150-E-00163 | 0 |  | S | [6 empty] | F2 | 17 | 18
BCV131 | DX12 | DIO1 | 132 | 2 | 12 | 0 | 2 | 9 |  |  | DI | 6 | BCV131BK02ZS02 | ZS01B | BCV131 TAIL BRAKE 2 CALIPER 1 | RHS Position Switch | Worn |  | BCV131BK02 |  | 2.12\0.2:9 | BR4-2150-E-00163 | 0 |  | S | [6 empty] | F2 | 19 | 20
BCV131 | DX12 | DIO1 | 132 | 2 | 12 | 0 | 2 | 10 |  |  | DI | 4 | BCV131BK02PS01 | PS01 | BCV131 TAIL BRAKE | BCV131 Tail Brake Pressure Switch | Lifted |  | BCV131BK02 |  | 2.12\0.2:10 | BR4-2150-E-00162 | 0 |  | S | [6 empty] | F2 | 21 | 22
BCV131 | DX12 | DIO1 | 132 | 2 | 12 | 0 | 2 | 11 |  |  | DI | 4 | BCV131BK02PS02 | PS02 | BCV131 TAIL BRAKE | BCV131 Tail Brake Pressure Switch | Low |  | BCV131BK02 |  | 2.12\0.2:11 | BR4-2150-E-00162 | 0 |  | S | [6 empty] | F2 | 23 | 24
BCV131 | DX12 | DIO1 | 132 | 2 | 12 | 0 | 2 | 12 |  |  | DI | 4 | BCV131BK02UI01 | LS01 | BCV131 TAIL BRAKE | BCV131 Tail Brake 2 Oil Level | Low |  | BCV131BK02UI01 |  | 2.12\0.2:12 | BR4-2150-E-00163 | 0 |  | S | [6 empty] | F2 | 25 | 26
BCV131 | DX12 | DIO1 | 132 | 2 | 12 | 0 | 2 | 13 |  |  | DI | 4 | BCV131BK02UI01 | TS01 | BCV131 TAIL BRAKE | BCV131 Tail Brake 2 Temperature Switch | High |  | BCV131BK02UI01 |  | 2.12\0.2:13 | BR4-2150-E-00163 | 0 |  | S | [6 empty] | F2 | 27 | 28
BCV131 | DX12 | DIO1 | 132 | 2 | 12 | 0 | 2 | 14 |  |  | DI | 4 | BCV131BK02LCS01 | STT01 | BCV131 TAIL BRAKE | BCV131 Tail Brake Start Pushbutton | Activated |  | BCV131BK02 |  | 2.12\0.2:14 | BR4-2110-E-00219 | A |  | S | [6 empty] | F2 | 29 | 30
BCV131 | DX12 | DIO1 | 132 | 2 | 12 | 0 | 2 | 15 |  |  | DI | 4 | BCV131BK02LCS01 | STP01 | BCV131 TAIL BRAKE | BCV131 Tail Brake Stop Pushbutton | Activated |  | BCV131BK02 |  | 2.12\0.2:15 | BR4-2110-E-00219 | A |  | S | [6 empty] | F2 | 31 | 32
BCV131 | DX12 | DIO1 | 132 | 2 | 12 | 0 | 2 | 16 |  |  | DI | 6 | BCV131BK01ZS02A | ZS02A | BCV131 TAIL BRAKE 1 CALIPER 1 | LHS Position Switch | Lifted |  | BCV131BK01 |  | 2.12\0.2:16 | BR4-2150-E-00163 | 0 |  | S | [6 empty] | F3 | 1 | 2
BCV131 | DX12 | DIO1 | 132 | 2 | 12 | 0 | 2 | 17 |  |  | DI | 6 | BCV131BK01ZS02B | ZS02B | BCV131 TAIL BRAKE 1 CALIPER 1 | LHS Position Switch | Worn |  | BCV131BK01 |  | 2.12\0.2:17 | BR4-2150-E-00163 | 0 |  | S | [6 empty] | F3 | 3 | 4
BCV131 | DX12 | DIO1 | 132 | 2 | 12 | 0 | 2 | 18 |  |  | DI | 6 | BCV131BK01ZS03A | ZS03A | BCV131 TAIL BRAKE 1 CALIPER 2 | RHS Position Switch | Lifted |  | BCV131BK01 |  | 2.12\0.2:18 | BR4-2150-E-00163 | 0 |  | S | [6 empty] | F3 | 5 | 6
BCV131 | DX12 | DIO1 | 132 | 2 | 12 | 0 | 2 | 19 |  |  | DI | 6 | BCV131BK01ZS03B | ZS03B | BCV131 TAIL BRAKE 1 CALIPER 2 | RHS Position Switch | Worn |  | BCV131BK01 |  | 2.12\0.2:19 | BR4-2150-E-00163 | 0 |  | S | [6 empty] | F3 | 7 | 8
BCV131 | DX12 | DIO1 | 132 | 2 | 12 | 0 | 2 | 20 |  |  | DI | 6 | BCV131BK01ZS04A | ZS04A | BCV131 TAIL BRAKE 1 CALIPER 2 | LHS Position Switch | Lifted |  | BCV131BK01 |  | 2.12\0.2:20 | BR4-2150-E-00163 | 0 |  | S | [6 empty] | F3 | 9 | 10
BCV131 | DX12 | DIO1 | 132 | 2 | 12 | 0 | 2 | 21 |  |  | DI | 6 | BCV131BK01ZS04B | ZS04B | BCV131 TAIL BRAKE 1 CALIPER 2 | LHS Position Switch | Worn |  | BCV131BK01 |  | 2.12\0.2:21 | BR4-2150-E-00163 | 0 |  | S | [6 empty] | F3 | 11 | 12
BCV131 | DX12 | DIO1 | 132 | 2 | 12 | 0 | 2 | 22 |  |  | DI | 6 | BCV131BK02ZS02A | ZS02A | BCV131 TAIL BRAKE 2 CALIPER 1 | LHS Position Switch | Lifted |  | BCV131BK02 |  | 2.12\0.2:22 | BR4-2150-E-00163 | 0 |  | S | [6 empty] | F3 | 13 | 14
BCV131 | DX12 | DIO1 | 132 | 2 | 12 | 0 | 2 | 23 |  |  | DI | 6 | BCV131BK02ZS02B | ZS02B | BCV131 TAIL BRAKE 2 CALIPER 1 | LHS Position Switch | Worn |  | BCV131BK02 |  | 2.12\0.2:23 | BR4-2150-E-00163 | 0 |  | S | [6 empty] | F3 | 15 | 16
BCV131 | DX12 | DIO1 | 132 | 2 | 12 | 0 | 2 | 24 |  |  | DI | 6 | BCV131BK02ZS03A | ZS03A | BCV131 TAIL BRAKE 2 CALIPER 2 | RHS Position Switch | Lifted |  | BCV131BK02 |  | 2.12\0.2:24 | BR4-2150-E-00163 | 0 |  | S | [6 empty] | F3 | 17 | 18
BCV131 | DX12 | DIO1 | 132 | 2 | 12 | 0 | 2 | 25 |  |  | DI | 6 | BCV131BK02ZS03B | ZS03B | BCV131 TAIL BRAKE 2 CALIPER 2 | RHS Position Switch | Worn |  | BCV131BK02 |  | 2.12\0.2:25 | BR4-2150-E-00163 | 0 |  | S | [6 empty] | F3 | 19 | 20
BCV131 | DX12 | DIO1 | 132 | 2 | 12 | 0 | 2 | 26 |  |  | DI | 6 | BCV131BK02ZS04A | ZS04A | BCV131 TAIL BRAKE 2 CALIPER 2 | LHS Position Switch | Lifted |  | BCV131BK02 |  | 2.12\0.2:26 | BR4-2150-E-00163 | 0 |  | S | [6 empty] | F3 | 21 | 22
BCV131 | DX12 | DIO1 | 132 | 2 | 12 | 0 | 2 | 27 |  |  | DI | 6 | BCV131BK02ZS04B | ZS04B | BCV131 TAIL BRAKE 2 CALIPER 2 | LHS Position Switch | Worn |  | BCV131BK02 |  | 2.12\0.2:27 | BR4-2150-E-00163 | 0 |  | S | [6 empty] | F3 | 23 | 24
BCV131 | DX12 | DIO1 | 132 | 2 | 12 | 0 | 2 | 28 |  |  | DI | [9 empty] | 2.12\0.2:28 |  |  |  | S | [6 empty] | F3 | 25 | 26
BCV131 | DX12 | DIO1 | 132 | 2 | 12 | 0 | 2 | 29 |  |  | DI | 4 | BTN130FIT01 | FQ01 | TRANSFER TOWER | Transfer Tower Flow Totaliser Pulse | Active |  | BTN130 |  | 2.12\0.2:29 | BR4-2150-E-00163 | 0 |  | S | [6 empty] | F3 | 27 | 28
BCV131 | DX12 | DIO1 | 132 | 2 | 12 | 0 | 2 | 30 |  |  | DI | 4 | BCV131FIT02 | FQ02 | BCV131 DUST SUPPRESSION | BCV131 Dust Suppression Flow Totaliser Pulse | Active |  | BCV131 |  | 2.12\0.2:30 | BR4-2150-E-00163 | 0 |  | S | [6 empty] | F3 | 29 | 30
BCV131 | DX12 | DIO1 | 132 | 2 | 12 | 0 | 2 | 31 |  |  | DI | [9 empty] | 2.12\0.2:31 |  |  |  | S | [6 empty] | F3 | 31 | 32
BCV131 | DX12 | DIO1 | 132 | 2 | 12 | 0 | 3 | 0 | BMXFTB2010 | BMXDDO1602 | DO | 4 | BCV131BK01SV01 | SV01 | BCV131 TAIL BRAKE 1 | BCV131 Tail Brake 1 | Release |  | BCV131BK01 |  | 2.12\0.3:0 | BR4-2150-E-00163 | 0 |  | S | [6 empty] | F5 | 1 | 2
BCV131 | DX12 | DIO1 | 132 | 2 | 12 | 0 | 3 | 1 |  |  | DO | 6 | BCV131BK01SV03 | SV03 | BCV131 TAIL BRAKE 1 | BCV131 Tail Brake 1 | Dump |  | BCV131BK01 |  | 2.12\0.3:1 | BR4-2150-E-00163 | 0 |  | S | [6 empty] | F5 | 3 | 4
BCV131 | DX12 | DIO1 | 132 | 2 | 12 | 0 | 3 | 2 |  |  | DO | 5 | [8 empty] | 2.12\0.3:2 | BR4-2110-F-00005 | D | Removed - as per discussion with Steve, Remsafe wired directly so not required on IO list. | S | [6 empty] | F5 | 5 | 6
BCV131 | DX12 | DIO1 | 132 | 2 | 12 | 0 | 3 | 3 |  |  | DO | 4 | BCV131BK02SV01 | SV01 | BCV131 TAIL BRAKE 2 | BCV131 Tail Brake 2 | Release |  | BCV131BK02 |  | 2.12\0.3:3 | BR4-2150-E-00163 | 0 |  | S | [6 empty] | F5 | 7 | 8
BCV131 | DX12 | DIO1 | 132 | 2 | 12 | 0 | 3 | 4 |  |  | DO | 6 | BCV131BK02SV03 | SV03 | BCV131 TAIL BRAKE 2 | BCV131 Tail Brake 2 | Dump |  | BCV131BK02 |  | 2.12\0.3:4 | BR4-2150-E-00163 | 0 |  | S | [6 empty] | F5 | 9 | 10
BCV131 | DX12 | DIO1 | 132 | 2 | 12 | 0 | 3 | 5 |  |  | DO | 5 | [8 empty] | 2.12\0.3:5 |  |  | Removed - as per discussion with Steve, Remsafe wired directly so not required on IO list. | S | [6 empty] | F5 | 11 | 12
BCV131 | DX12 | DIO1 | 132 | 2 | 12 | 0 | 3 | 6 |  |  | DO | 4 | BCV131SV07 | SV07 |  | BCV131 Dust Spray - Tail End | Open |  | BCV131 |  | 2.12\0.3:6 | BR4-2150-E-00162 | 0 |  | S | [6 empty] | F5 | 13 | 14
BCV131 | DX12 | DIO1 | 132 | 2 | 12 | 0 | 3 | 7 |  |  | DO | [9 empty] | 2.12\0.3:7 |  |  |  | S | [6 empty] | F5 | 15 | 16
BCV131 | DX12 | DIO1 | 132 | 2 | 12 | 0 | 3 | 8 |  |  | DO | [9 empty] | 2.12\0.3:8 |  |  |  | S | [6 empty] | F5 | 17 | 18
BCV131 | DX12 | DIO1 | 132 | 2 | 12 | 0 | 3 | 9 |  |  | DO |  |  |  | Release Solenoid | [5 empty] | 2.12\0.3:9 |  |  |  | S | [6 empty] | F5 | 19 | 20
BCV131 | DX12 | DIO1 | 132 | 2 | 12 | 0 | 3 | 10 |  |  | DO |  |  |  | Dump Solenoid | [5 empty] | 2.12\0.3:10 |  |  |  | S | [6 empty] | F5 | 21 | 22
BCV131 | DX12 | DIO1 | 132 | 2 | 12 | 0 | 3 | 11 |  |  | DO | [9 empty] | 2.12\0.3:11 |  |  |  | S | [6 empty] | F5 | 23 | 24
BCV131 | DX12 | DIO1 | 132 | 2 | 12 | 0 | 3 | 12 |  |  | DO | [9 empty] | 2.12\0.3:12 |  |  |  | S | [6 empty] | F5 | 25 | 26
BCV131 | DX12 | DIO1 | 132 | 2 | 12 | 0 | 3 | 13 |  |  | DO | [9 empty] | 2.12\0.3:13 |  |  |  | S | [6 empty] | F5 | 27 | 28
BCV131 | DX12 | DIO1 | 132 | 2 | 12 | 0 | 3 | 14 |  |  | DO | [9 empty] | 2.12\0.3:14 |  |  |  | S | [6 empty] | F5 | 29 | 30
BCV131 | DX12 | DIO1 | 132 | 2 | 12 | 0 | 3 | 15 |  |  | DO | [9 empty] | 2.12\0.3:15 |  |  |  | S | [6 empty] | F5 | 31 | 32
BCV131 | DX12 | DIO1 | 132 | 2 | 12 | 0 | 4 | 0 | BMXFTW301S | BMEAHI0812 | AI | 4 | BTN130FIT01 | FT01 | TRANSFER TOWER | Transfer Tower |  | L/s | BTN130 | REAL | 2.12\0.4:0 | BR4-2150-E-00163 | 0 |  | S | [5 empty] | #.# EU | F5 | 33 | 34
BCV131 | DX12 | DIO1 | 132 | 2 | 12 | 0 | 4 | 1 |  |  | AI | 4 | BCV131FIT02 | FT02 | BCV131 DUST SUPPRESSION | BCV131 Dust Suppression |  |  | BCV131 |  | 2.12\0.4:1 | BR4-2150-E-00163 | 0 |  | S | [6 empty] | F5 | 35 | 36
BCV131 | DX12 | DIO1 | 132 | 2 | 12 | 0 | 4 | 2 |  |  | AI | [9 empty] | 2.12\0.4:2 | [10 empty] | F5 | 37 | 38
BCV131 | DX12 | DIO1 | 132 | 2 | 12 | 0 | 4 | 3 |  |  | AI | [9 empty] | 2.12\0.4:3 | [10 empty] | F5 | 39 | 40
BCV131 | DX12 | DIO1 | 132 | 2 | 12 | 0 | 4 | 4 |  |  | AI | [9 empty] | 2.12\0.4:4 | [10 empty] | F5 | 41 | 42
BCV131 | DX12 | DIO1 | 132 | 2 | 12 | 0 | 4 | 5 |  |  | AI | [9 empty] | 2.12\0.4:5 | [10 empty] | F5 | 43 | 44
BCV131 | DX12 | DIO1 | 132 | 2 | 12 | 0 | 4 | 6 |  |  | AI | [9 empty] | 2.12\0.4:6 | [10 empty] | F5 | 45 | 46
BCV131 | DX12 | DIO1 | 132 | 2 | 12 | 0 | 4 | 7 |  |  | AI | [9 empty] | 2.12\0.4:7 | [10 empty] | F5 | 47 | 48
BCV131 | DX12 | DIO1 | 132 | 2 | 12 | 0 | 5 | 0 | BMXFTB2010 | BMXEHC0800 | HSCI | 4 | BCV131SS01 | SS01 | OVERLAND CONVEYOR | Underspeed Pulse | Active |  | BCV131 |  | 2.12\0.5:0 | BR4-2150-E-00162 | 0 |  | S | [6 empty] | F2 | 33 | 34
BCV131 | DX12 | DIO1 | 132 | 2 | 12 | 0 | 5 | 1 |  |  | HSCI | 3 | BCV131ZQ01 | ZQ01 | OVERLAND CONVEYOR | Distance Pulse |  |  | BCV131 |  | 2.12\0.5:1 | BR4-2150-E-00162 | 0 |  | S | [6 empty] | F2 | 35 | 36
BCV131 | DX12 | DIO1 | 132 | 2 | 12 | 0 | 5 | 2 |  |  | HSCI | [9 empty] | 2.12\0.5:2 |  |  |  | S | [6 empty] | F2 | 37 | 38
BCV131 | DX12 | DIO1 | 132 | 2 | 12 | 0 | 5 | 3 |  |  | HSCI | [9 empty] | 2.12\0.5:3 |  |  |  | S | [6 empty] | F2 | 39 | 40
BCV131 | DX12 | DIO1 | 132 | 2 | 12 | 0 | 5 | 4 |  |  | HSCI | [9 empty] | 2.12\0.5:4 |  |  |  | S | [6 empty] | F2 | 41 | 42
BCV131 | DX12 | DIO1 | 132 | 2 | 12 | 0 | 5 | 5 |  |  | HSCI | [9 empty] | 2.12\0.5:5 |  |  |  | S | [6 empty] | F2 | 43 | 44
BCV131 | DX12 | DIO1 | 132 | 2 | 12 | 0 | 5 | 6 |  |  | HSCI | [9 empty] | 2.12\0.5:6 |  |  |  | S | [6 empty] | F2 | 45 | 46
BCV131 | DX12 | DIO1 | 132 | 2 | 12 | 0 | 5 | 7 |  |  | HSCI | [9 empty] | 2.12\0.5:7 |  |  |  | S | [6 empty] | F2 | 47 | 48
BCV131 | DX12 | DIO1 | 132 | 2 | 12 | 0 | 6 |  |  | BMXXEM010 | [10 empty] | 2.12\0.6:
BCV131 | DX12 | DIO1 | 132 | 2 | 12 | 0 | 6 | [13 empty] | 2.12\0.6:
BCV131 | DX12 | DIO1 | 132 | 2 | 12 | 0 | 6 | [13 empty] | 2.12\0.6:
BCV131 | DX12 | DIO1 | 132 | 2 | 12 | 0 | 6 | [13 empty] | 2.12\0.6:
BCV131 | DX12 | DIO1 | 132 | 2 | 12 | 0 | 7 |  |  | BMXXEM010 | [10 empty] | 2.12\0.7:
BCV131 | DX12 | DIO1 | 132 | 2 | 12 | 0 | 7 | [13 empty] | 2.12\0.7:
BCV131 | DX12 | DIO1 | 132 | 2 | 12 | 0 | 7 | [13 empty] | 2.12\0.7:
BCV131 | DX12 | DIO1 | 132 | 2 | 12 | 0 | 7 | [13 empty] | 2.12\0.7:
BCV131 | DX12 | DIO1 | 132 | 2 | 12 | 0 | 8 |  |  | BMXXEM010 | [10 empty] | 2.12\0.8:
BCV131 | DX12 | DIO1 | 132 | 2 | 12 | 0 | 8 | [13 empty] | 2.12\0.8:
BCV131 | DX12 | DIO1 | 132 | 2 | 12 | 0 | 8 | [13 empty] | 2.12\0.8:
BCV131 | DX12 | DIO1 | 132 | 2 | 12 | 0 | 8 | [13 empty] | 2.12\0.8:
BCV131 | DX12 | DIO1 | 132 | 2 | 12 | 0 | 9 |  |  | BMXXEM010 | [10 empty] | 2.12\0.9:
BCV131 | DX12 | DIO1 | 132 | 2 | 12 | 0 | 9 | [13 empty] | 2.12\0.9:
BCV131 | DX12 | DIO1 | 132 | 2 | 12 | 0 | 9 | [13 empty] | 2.12\0.9:
BCV131 | DX12 | DIO1 | 132 | 2 | 12 | 0 | 9 | [13 empty] | 2.12\0.9:
BCV131 | DX12 | DIO1 | 132 | 2 | 12 | 0 | 10 |  |  | BMXXEM010 | [10 empty] | 2.12\0.10:
BCV131 | DX12 | DIO1 | 132 | 2 | 12 | 0 | 10 | [13 empty] | 2.12\0.10:
BCV131 | DX12 | DIO1 | 132 | 2 | 12 | 0 | 10 | [13 empty] | 2.12\0.10:
BCV131 | DX12 | DIO1 | 132 | 2 | 12 | 0 | 10 | [13 empty] | 2.12\0.10:
BCV131 | DX12 | DIO1 | 132 | 2 | 12 | 0 | 11 |  |  | BMXXEM010 | [10 empty] | 2.12\0.11:
BCV131 | DX12 | DIO1 | 132 | 2 | 12 | 0 | 11 | [13 empty] | 2.12\0.11:
BCV131 | DX12 | DIO1 | 132 | 2 | 12 | 0 | 11 | [13 empty] | 2.12\0.11:
BCV131 | DX12 | DIO1 | 132 | 2 | 12 | 0 | 11 | [13 empty] | 2.12\0.11:
Note on P277: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: SHOULD THESE GO TO THE FIRE PANEL
Note on P278: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: SHOULD THESE GO TO THE FIRE PANEL